| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Design Criteria | Vendor To confirm That All supplied material all in full compliance with Project site condition : - Min/Max air temperature = -5°C / 52°C - Relative humidity = 100% max at 52°C - Altitude = 12 m a.s.l. - Climate = Class 4 (Very High) Vendor shall submitted temperature de‐rating factors of equipment such as CB, etc. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated rated current be equal or higher than rate current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. Please confirm. | CONFIRM | Closed . |  |  |  |
|  | Documents Priority | All The equipment’s shall be engineered, designed, manufactured, tested and installed in accordance with one of the following standards: LOCAL CODES AND STANDARDS Iranian Petroleum Standard (IPS) INTERNATIONAL CODES AND STANDARDS IEC (International Electrotechnical Commission) BS (British Standard) IEEE (Institute of Electrical and Electronics Engineers) API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards and codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes and Standards. 4-Vendor technical offer Please confirm. | CONFIRM | Closed . |  |  |  |
|  | Scope of Supply | Minimum Scope of work and supply are in full compliance with Project Requirements. for Electrical has been Listed but not Limited to the following Items: - Full Engineering Services. - One Set Diesel Engine Generator Pkg. Base on attached data sheet (BK-GCS-PEDCO-120-EL-DT-0003 ). - Power Panel without ATS. - Control Panel . - Other items acc to Spec for DEG All Requirements’ should be considered. Please confirm and Complete the List. | CONFIRM | Closed. |  |  |  |
|  | Deviation List | Technical requirements shall be according to project specification in as minimum except those clearly specified in “deviation-exception form”. Basic Design Documents : BK-GNRAL-PEDCO-000-EL-DC-0001 - Electrical Design Criteria BK-GCS-PEDCO-120-EL-CN-0007 - Diesel Generator Sizing BK-GCS-PEDCO-120-EL-SL-0002 - LV Switchgear/MCC Single Line Diagram BK-GNRAL-PEDCO-000-EL-SP-0001 – Spec for LV SWG & MCC Panel BK-GNRAL-PEDCO-000-EL-SP-0007 – Spec for Package Equipment’s BK-GNRAL-PEDCO-000-EL-SP-0014 – Spec for Power and Control Cable BK-GNRAL-PEDCO-000-EL-SP-0008 – Spec for Bulk Material BK-GNRAL-PEDCO-000-EL-SP-0009 – Specification for Diesel Engine BK-GCS-PEDCO-120-EL-DT-0003 – Datasheet for Diesel Generator BK-GCS-PEDCO-120-EL-LI-0005- I/O List BK-GCS-PEDCO-120-EL-MR-0004- MR for DEG. BK-GCS-PEDCO-120-EL-LD-0001- Control Logic Diagram BK-GCS-PEDCO-120-EL-SL-0001- Overall Single Line Diagram (Will be Submitted Later) Shall be fill full and submitted in Next Proposal. Please confirm. | PLEASE SEND US THE DEVIATION FORM TO BE FULFILED | Deviation form is in attached to the MR. ( project format attachment 3 page 14 ) |  |  |  |
|  | General | Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to Inquiry package and codes & standards referred in the Reference documents by issuing a Deviation/Exception List for purchaser's review and approval. Otherwise, the vendor must declare full compliance between all documents attached to the Inquiry package and its proposal. Please send Deviations/Exceptions List or declare "No Deviation". | PLEASE SEND US THE DEVIATION FORM TO BE FULFILED | Deviation form is in attached to the MR. ( project format attachment 3 page 14 ) |  |  |  |
|  | General | Diesel Engine Generator Package shall be Design for continues Operating Duty. Please confirm. | STANDBY AS DATA SHEET | As per project specification diesel engine generator package shall be design for continues operating duty. Pls follow it. |  |  |  |
|  | General | Attached TBE Table should be fill full and reply by vendor in native word sheet in next proposal. All required data and reference Documents shall be submitted in next proposal. Please confirm. | CONFIRM | Closed. |  |  |  |
|  | General | All Required Cable Glands & Plugs are in Vendor Scope of work and shall be ISO metric threaded in accordance with IEC60423. It should be considered by Vendor. Please confirm | LATER | DUE TO THE FACT THAT THE VENDOR HAS POSTPHONED SOME ITEMS UNTIL AFTER PO. IT is assumed that the provided equipment is fully compatible by the technical document of the project please confirmed it. |  |  |  |
|  | Part List , Spare Part | Part List, Spare Part for Commissioning and 2 Years Operation should be Submitted acc to Project Specification. Please confirm and submit in next proposal. | PLEASE SEND THE DOCUMENT | It is not accepted and vendor shall be sending his proposal for approval based on previous experiences in similar projects. |  |  |  |
|  | Spare Part | Spare part list and interchangeability record (SPIR form) shall be filled by vendor after P.O stage, based on Attachment BK-GNRAL-PEDCO-000-EL-SP-0009 – Specification for Diesel Engine Please confirm. | PLEASE SEND THE DOCUMENT | It is not accepted and vendor shall be sending his proposal for approval based on previous experiences in similar projects. |  |  |  |
|  | Special Tools | Any Special Tools for erection and for regular maintenance shall be included in technical offer. Please confirm. | CONFIRM | Closed. |  |  |  |
|  | Guarantee | Guarantee term (for engineering, materials and work ship) shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/package at site . Under this Guarantee, all material, parts, and assemblies found to be defect during the guarantee period shall be replaced by bidder without any charge. Please confirm. | OR 1000 HR OPERATION AND EACH COMES FIRST | It is not acceptable. Project document shall be followed by vendor. |  |  |  |
|  | Specification | Electrical Cable Type are as follow : Power : Cu/XLPE/SWA/PVC OR : Cu/XLPE/AWA/PVC Control : Cu/PVC/SWA/PVC RTD or PTC : Cu/PVC/ISCR/OSCR/SWA/PVC All Cable & Cabling inside the package Battery Limit are in Vendor SOW. Please confirm and change in next proposal. | CONFIRM | Closed. |  |  |  |
|  | Vendor List | Electrical Sub-Vendor List shall be submitted for all Equipment’s of Package Scope of Supply. Please confirm and Change in next proposal. | AFTER FINAL ROUND | It is not acceptable. Project document shall be followed by vendor. |  |  |  |
|  | Catalogue | Catalogue for all proposed equipment shall be Submitted. Please confirm and Complete Proposal. | CONFIRM | Closed. |  |  |  |
|  | Software | Original setting configuration software (on CD) shall be submitted in three original copies, Please correct your special tools list. Also Special cables between relay and computer for setting, configuration, uploading, downloading and testing of relays (3 meters) with special connectors at both ends shall be supplied. Please confirm. | OK | Closed. |  |  |  |
|  | Specification | Vendor of Main Items in the Low Voltage Switchgears shall be selected as follows: - Vendor of Protection Relays will be one of the companies SIEMENS, ABB, ALSTOM/AREVA or SHNEIDER ELECTRIC. - Vendor of Circuit Breakers and Contactors will be one of the companies SIEMENS, ABB, ALSTOM/AREVA, SHNEIDER ELECTRIC, HITACHI, MITSUBISHI, MOELLER or LEGRAND. - Vendor of Aux. Relays will be one of the companies SIEMENS, ABB, ALSTOM/AREVA, MOELLER, SHNEIDER ELECTRIC, HAGER, FINDER, LEGRAND or OMRON. - Vendor of CT and PT will be one of the companies SIEMENS, ABB, ALSTOM/AREVA, SHNEIDER ELECTRIC, ZELISKO, RITZ or MAG ELECTRIC. - Vendor of Terminal will be one of the companies SIEMENS, PHONIX CONTACT, ALSTOM/AREVA, ABB, LEGRAND, SHNEIDER ELECTRIC or ENTERELEC. - Vendor of Fuse will be one of the companies SIEMENS, ALSTOM/AREVA, ABB, LEGRAND, SIBA, SHNEIDER ELECTRIC or FERRAZ. - Vendor of Electric Meters will be one of the companies SIEMENS, ALSTOM/AREVA, ABB, LEGRAND, IME, SHNEIDER ELECTRIC, ISKRA or UNIDATA. Please Confirm and revise your Proposal. | OK | Closed. |  |  |  |
|  | Specification | Main LV Switchgear is not in Vendor scope of supply but Item-17 shall be confirmed for Generator Power Panel. Please Confirm. | OK | Closed. |  |  |  |
|  | Specification | Electrical Load List for Auxiliaries Loads’ has not been submitted. - As Minimum Below items shall be Specified : Type of Load = Motor / Feeder Load Factor = Absorb Power/Install Power Load Efficiency and Power Factor @ Load Factor. - Load List for UPS Shall be submitted separately. - Load List for DC Shall be submitted separately. - Refer to Clause 7.4.3.4 in IPS-E-EL-100(1), Motors Larger than 0.4kW be shall be 3ph. Please confirm and submit in next proposal. | WE NEED JUST 1 FEEDER 230 VOLTS 50HZ 60 AMP FOR AUX FEEDING | Closed. |  |  |  |
|  | Specification | General Arrangement Layout shall be submitted with minimum dimensional drawings for below items : 1- Diesel Engine + Generator. 2- Power & Control Panels and Access Doors. 3- Battery Stand. 4-Other Main Equipment’s. Please confirm and submit in next proposal. | AFTER PO | It is not acceptable. Project document shall be followed by vendor. |  |  |  |
|  | Tests | Preliminary QCP/ITP for package shall be Submitted by vendor in the Technical Proposal. Please Submit in next proposal. | SAMPLE TEST SUBMITTED | Closed. |  |  |  |
|  | General | For other Comment refer to TCL Attachments for further action. Please Consider relevant Changes in Next Proposal. | OK | Closed. |  |  |  |
|  | Specification | All interconnecting control wiring inside the Package shall be furnished and installed by the vendor | OK | Closed. |  |  |  |
|  | Specification | Minimum Insulation Class and maximum Temp. rise at Continuous mode on operation shall be F and B | H-H | Pls. mention in deviation list (project format attachment 3 page 14 ) |  |  |  |
|  | General | There is deviation which should be review and approved by Client. | PLEASE SEND US THE DEVIATION FORM TO BE FULFILED | Deviation form is in attached to the MR. ( project format attachment 3 page 14 ) |  |  |  |
|  | Specification | Rating of generator set together with Temp rise shall be specified for the following operation modes at site and ISO conditions: Continuous mode Intermittent mode Standby mode | OK | Closed. |  |  |  |
|  | Data Sheet | As per project data sheet 9 RTD is required but vender proposed NO if vendor cannot provide project required, pls. Mention in deviation list (project format attachment 3 page 14 ) |  |  |  |  |  |
|  | Data Sheet | For changeover panel MCB isn’t accepted and vendor shall be followed project document. |  |  |  |  |  |
|  | Data Sheet | Some Of The Column Of Data Sheet Refer To Catalog Or No Answer So It Isn’t Accepted. Pls Specified Exactly. |  |  |  |  |  |
| Civil & Structure |  |  |  |  |  |  |  |
|  | Specification | All of data which is needed for foundation design such as (layout, anchor bolt size and arrangement, foundation loads including: dynamic and static loads&…..)Shall be submitted by vendor. Structure required information shall be submitted in foundation layout after P.O. 1: grout type and thickness shall be submitted. 2: wind and earthquake loads and cal. shall be submitted. 3: C.O.G shall be added. 4: empty and operation weight shall be submitted. Please Confirm. | NON OF THE REQUESTED DATA IS NOT AVAILABLE , WE JUST NEED A FLAT FOUNDATION TO ROLL BOLT THE DG TO THE FOUNDATION AND WE WILL GIVE YOU FOUNDATION DETAIL AND DWG BUT THERE IS NO LOAD STUDY IN IT . | It is not acceptable. Project document shall be followed by vendor. |  |  |  |
| Instrument |  |  |  |  |  |  |  |
|  | Specification | The control panel shall be self-supporting made of steel sheets of at least 2.5 mm thickness. The panel shall be suitable for floor mounting against the wall and shall be supplied with all necessary accessories for fixing. The panel shall be accessible from the front and shall be provided with hinged doors fitted with locking devices. | INSIDE CANOPY | Not Acceptable Project Specification Must Be Followed. |  |  |  |
|  | Specification | In the Control Panel minimum conductor sizes shall be 2.5 mm2 for control and protection, and 1.5 mm2 for signal wiring. | LATER | Due to the fact that the vendor has postponed some items until after po. It is assumed that the provided equipment is fully compatible by the technical document of the project please confirmed it. |  |  |  |
|  | Specification | The minimum degree of Control Panel protection shall be IP55. | XX | Not Acceptable Project Specification Must Be Followed. |  |  |  |
|  | Specification | Interconnecting wiring and cabling between the diesel engine generator and panel shall be supplied by Vendor including cable glands, conduits, etc. | OK | Closed. |  |  |  |
|  | Specification | The control panel shall be designed and constructed to withstand the effects of internal and external faults in accordance with IEC-61439. | OK | Closed. |  |  |  |
|  | Specification | This device shall have serial port for Modbus RTU serial link to the PMS (RS 485). Serial link signals shall be based on the section 9.5 of SPECIFICATION FOR DIESEL ENGINE GENERATOR (286-100-EL-SP-026). | OK | Closed. |  |  |  |
|  | Specification | Signals such as status signals, circuit breaker control commands, etc shall transmitted to PMS and LV switchboard by hard wire as per section 9.6 of SPECIFICATION FOR DIESEL ENGINE GENERATOR (286-100-EL-SP-026). | OK | Closed. |  |  |  |
|  | Specification | Control functions shall be based on the section 9.5 of SPECIFICATION FOR DIESEL ENGINE GENERATOR (286-100-EL-SP-026). | OK | Closed. |  |  |  |