| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| TBE FOR EMERGENCY DIESEL GENERATOR نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |
| D00 | Oct. 2024 | IFI | M.Pourdasht | M.Fakharian | M.Sadeghian |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | Client Approval |
| Class:3 |  | Client Doc. Number: F0Z-709334 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for Client Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  |  |  |  | 51 |  |  |  |  |  |
| 2 | X |  |  |  |  |  | 52 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 53 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 54 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 55 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 56 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 57 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 58 |  |  |  |  |  |
| 9 | X |  |  |  |  |  | 59 |  |  |  |  |  |
| 10 | X |  |  |  |  |  | 60 |  |  |  |  |  |
| 11 | X |  |  |  |  |  | 61 |  |  |  |  |  |
| 12 | X |  |  |  |  |  | 62 |  |  |  |  |  |
| 13 | X |  |  |  |  |  | 63 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 64 |  |  |  |  |  |
| 15 | X |  |  |  |  |  | 65 |  |  |  |  |  |
| 16 | X |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 | X |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 | X |  |  |  |  |  | 68 |  |  |  |  |  |
| 19 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 20 | X |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 | X |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 | X |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 | X |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 | X |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 | X |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 | X |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 | X |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 | X |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

| # TBE For Emergency Diesel Generator |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MR | PMR For Emergency Diesel Generator ( BK-GCS-PEDCO-120-EL-MR-0004 ) | Purchaser Requirement | Vendor | Status |  |  |  |  |
| Item | Description |  |  |  |  |  |  |  |
| - Environmental Data (Process Basis Design, BK-GNRAL-PEDCO-000-PR-DB-0001) |  |  |  |  |  |  |  |  |
|  | Location | Binak Oilfield in Bushehr Province | ok |  |  |  |  |  |
|  | Installation | Outdoor Under Shelter, Safe Area | confirm |  |  |  |  |  |
|  | Installation Elevation | 12.5m (Above Sea Level) | confirm |  |  |  |  |  |
|  | Seismic Loads | Zone 3 UBC | confirm |  |  |  |  |  |
|  | Relative Humidity | 100% | confirm |  |  |  |  |  |
|  | Ambient Temperature Range | 5 ~ 52°C | confirm |  |  |  |  |  |
|  | Atmosphere | Corrosive & Hot | confirm |  |  |  |  |  |
| - General |  |  |  |  |  |  |  |  |
|  | Manufacturer's Name | By Vendor | volvo |  |  |  |  |  |
|  | Model | By Vendor | TAD1641GE |  |  |  |  |  |
|  | Quantity/Tag Number | 1 /GCS-DG-001 | confirm |  |  |  |  |  |
|  | Electrical Standard | IPS-E-EL-100(1) IPS-M-EL-138 (1) BK-GNRAL-PEDCO-000-EL-SP-0009 | confirm |  |  |  |  |  |
|  | Mechanical Standard | IPS-M-PM-290 (2) BK-GCS-PEDCO-120-ME-SP-0012 | confirm |  |  |  |  |  |
|  | References | Calculation Note for Diesel Generator Sizing (BK-GCS-PEDCO-120-EL-CN-0007) | confirm |  |  |  |  |  |
|  | Description of Equipment | Gen Set with Diesel Engine Prime Mover (Diesel Generator) | confirm |  |  |  |  |  |
| - Engine Specifications |  |  |  |  |  |  |  |  |
|  | Genset Operation Mode (Single or Parallel) | Single | confirm |  |  |  |  |  |
|  | Duty | Emergency Standby (Calculated for continuous operation) | STANDBY DUTY |  |  |  |  |  |
|  | Aspiration | Turbo Charged, Intercooler | confirm |  |  |  |  |  |
|  | Cylinder configuration | By Vendor | LINE |  |  |  |  |  |
|  | Number of Cylinders | By Vendor | 6 |  |  |  |  |  |
|  | Type | Industrial, 4 strokes, Direct Injection | confirm |  |  |  |  |  |
|  | Displacement (liter) | By Vendor | 16120 |  |  |  |  |  |
|  | Bore/Stroke (mm) | By Vendor | LATER |  |  |  |  |  |
|  | Compression Ratio | By Vendor | LATER |  |  |  |  |  |
|  | Governor Type | Electronic | CONFIRM |  |  |  |  |  |
|  | Air Cleaner Type | Heavy Duty | STANDARD |  |  |  |  |  |
|  | Engine speed (rpm) | 1500 | CONFIRM |  |  |  |  |  |
|  | Derating Factor for Working at Site Conditions (55°C) | 0.97 (Vendor Shall Advise This Value) | LATER |  |  |  |  |  |
|  | ISO Gross Shaft Power at (kw) Continuous Prime Maximum Standby | By Vendor >494 >506 | 658HP |  |  |  |  |  |
|  | Cooling Fan Power Requirement (kw) | 10 | LATER |  |  |  |  |  |
|  | ISO Net Shaft Power at (kw) Continuous Prime Maximum Standby | By Vendor >496 >510 | 440 KW |  |  |  |  |  |
|  | Piston Speed (m/s) | By Vendor | LATER |  |  |  |  |  |
|  | Starting System | Electrical | OK |  |  |  |  |  |
|  | Type of Batteries | Vented Ni-Cd | LEAD ACID |  |  |  |  |  |
|  | Number of Batteries (Cell) | 20 Number Cells | NO |  |  |  |  |  |
|  | Size of Batteries (Ah) | Not Less than 200 Ah | 200 AH |  |  |  |  |  |
|  | Max Startup & Loading Time up to Full Load (Sec) | 10 Sec | OK |  |  |  |  |  |
| - Lubricating System |  |  |  |  |  |  |  |  |
|  | Type | Forced Feed by Gear Oil Pump | OK |  |  |  |  |  |
|  | Total Oil Capacity Min/Max (liter) | By Vendor | LATER |  |  |  |  |  |
|  | Oil Filter | By Vendor | OK |  |  |  |  |  |
|  | Oil Cooler | Water Cooled | NO |  |  |  |  |  |
|  | Oil Type Required | By Vendor | 15W40 |  |  |  |  |  |
|  | Lube Oil Consumption at: (gr/h) Continuous Power Prime Power Standby POWER | By Vendor | LATER |  |  |  |  |  |
| - Fuel System |  |  |  |  |  |  |  |  |
|  | Type of Fuel | Gas oil | OK |  |  |  |  |  |
|  | Fuel Filter Type | By Vendor | LATER |  |  |  |  |  |
|  | Permissible Suction Head | By Vendor | LATER |  |  |  |  |  |
|  | Permissible Return Head | By Vendor | LATER |  |  |  |  |  |
|  | Specified Fuel Consumption at: (gr/kwh) 100% Maximum Standby Power Prime Power 100% Continuous Power | By Vendor | 90 L/H @ 75% |  |  |  |  |  |
|  | Daily Tank | For 8 Hours Operation | 193 L |  |  |  |  |  |
| - Cooling System |  |  |  |  |  |  |  |  |
|  | Total Coolant Capacity (liter) | By Vendor | LATER |  |  |  |  |  |
|  | Water Pump Type | Centrifugal | LATER |  |  |  |  |  |
|  | Temp. Rise Across Engine at: ºC Continuous Power Prime Power Standby Power | By Vendor | LATER |  |  |  |  |  |
|  | Heat Rejection to Exhaust (Prime Power) (kw) | By Vendor | LATER |  |  |  |  |  |
|  | Heat Rejection to Coolant (Prime Power) (kw) | By Vendor | LATER |  |  |  |  |  |
|  | Heat Rejection to Intercooler (Prime Power) (kw) | By Vendor | LATER |  |  |  |  |  |
|  | Heat Rejection by Radiation From Engine Surface (Prime Power) (kw) | By Vendor | LATER |  |  |  |  |  |
|  | Cooling Air Required for Radiator (Prime Power) (kw) | By Vendor | LATER |  |  |  |  |  |
| - Air Intake |  |  |  |  |  |  |  |  |
|  | Combustion Air Flow at: (m3/h) Standby Power Prime Power Continuous Power | By Vendor | LATER |  |  |  |  |  |
|  | Max. Air Intake Restriction of Engine : hPa With New Filter With Used Filter | By Vendor | LATER |  |  |  |  |  |
|  | Alternator Cooling Air (m3/h) | By Vendor | LATER |  |  |  |  |  |
| - Exhaust System |  |  |  |  |  |  |  |  |
|  | Max. Allowable Back Pressure for Exhaust Line (pa) | By Vendor | LATER |  |  |  |  |  |
|  | Exhaust Flow (at Standby Power) (m3/h) | By Vendor | LATER |  |  |  |  |  |
|  | Exhaust Gas Temp. After Turbine (at Standby Power) (ºC) | By Vendor | LATER |  |  |  |  |  |
|  | Silencer Type | Residential | CONFIRM |  |  |  |  |  |
|  | Spark Arrester | Required | NO |  |  |  |  |  |
| - Engine Auxiliaries |  |  |  |  |  |  |  |  |
|  | Alternator Manufacturer | By Vendor | STAMFORD / MEC ALTE |  |  |  |  |  |
|  | Alternator Voltage (v) | By Vendor | 400 |  |  |  |  |  |
|  | Alternator Current (A) | By Vendor | 800 |  |  |  |  |  |
|  | Starter Manufacturer | By Vendor | LATER |  |  |  |  |  |
|  | Starter Motor Voltage (v) | By Vendor | 24 |  |  |  |  |  |
|  | Starter Motor Power (kw) | By Vendor | LATER |  |  |  |  |  |
| - Generator Specifications |  |  |  |  |  |  |  |  |
|  | Quantity / Duty | 1 X 100% / Continuous | STANDBY |  |  |  |  |  |
|  | Manufacturer / Type | By Vendor | LATER |  |  |  |  |  |
|  | Continuous Rating (MCR) at Standard Condition for Class F Temperature Rise (kva) | > 512kVA to meet continuous operation > 539kVA to meet starting conditions | 550 KVA STANDBY |  |  |  |  |  |
|  | De-Rating Factor for Ambient Temperature Kt | 0.9 (MFR shall advise his value) | LATER |  |  |  |  |  |
|  | De-Rating Factor for Altitude Ka | 1.0 | LATER |  |  |  |  |  |
|  | Total Generator De-Rating Factor Kd=Ka*Kt | 0.9 (MFR Shall Advise His Value) | LATER |  |  |  |  |  |
|  | Continuous Rating (MCR) at Site Conditions for Class F Temp. Rise (kva) | 394 | CLASS H |  |  |  |  |  |
|  | Permissible Overload (Class H Temp. Rise & Standby Duty) (kva) | 10% of Rated Current for a Period of One Hour (in Each 12 Hours Function) | NOT ALLOWED |  |  |  |  |  |
|  | Starting Capability (12% Voltage Dip at gen. Terminal) | Starting of the biggest motor while having the other loads in operation PF=0.80 | LATER |  |  |  |  |  |
|  | Unbalance Loading Capacity (%) | 15% | NOT SPECIFIED |  |  |  |  |  |
|  | Power Factor | 0.80 | OK |  |  |  |  |  |
|  | Terminal Voltage (v) | 400 | OK |  |  |  |  |  |
|  | Stator Winding Connection | Series Star | OK |  |  |  |  |  |
|  | Frequency (Hz) | 50 | OK |  |  |  |  |  |
|  | Grounding | Solidly Grounded | OK |  |  |  |  |  |
|  | Neutral Point | Brought out | OK |  |  |  |  |  |
|  | Insulation Class | F | H |  |  |  |  |  |
|  | Temp. Rise for Continuous Duty | B | H |  |  |  |  |  |
|  | Ingress Protection of Terminal Box | IP55W | OK |  |  |  |  |  |
|  | Ingress Protection for Generator | IP23 | OK |  |  |  |  |  |
|  | Short Circuit Ratio at Rated Volts & Current | By Vendor | LATER |  |  |  |  |  |
|  | Synchronous Reactance Xd (Base 600kVA, 400V, Saturated) (pu) | By Vendor | LATER |  |  |  |  |  |
|  | Direct Axis Transient Reactance X’d1(pu) | By Vendor | LATER |  |  |  |  |  |
|  | Direct Axis sub-Trans. Reactance X”d (pu) | By Vendor | LATER |  |  |  |  |  |
|  | Quadrature Axis Reactance Xq (pu) | By Vendor | LATER |  |  |  |  |  |
|  | Quadrature Axis Sub-Trans. Reactance X”q (pu) | By Vendor | LATER |  |  |  |  |  |
|  | Zero Sequence Reactance X0 (pu) | By Vendor | LATER |  |  |  |  |  |
|  | Negative Sequence Reactance X2 (pu) | By Vendor | LATER |  |  |  |  |  |
|  | Leakage Reactance XL (pu) | By Vendor | LATER |  |  |  |  |  |
|  | Time Constants (sec) Td’ Td” Ta | By Vendor | LATER |  |  |  |  |  |
|  | Generator Efficiency at: 1/2 Full Load (%) 3/4 Full Load (%) 4/4 Full Load (%) | By Vendor | LATER |  |  |  |  |  |
|  | Number of Bearings | 1 (2 is preferred) | 1 |  |  |  |  |  |
|  | Type of Bearings / Lubrication | Anti-friction / Grease | OK |  |  |  |  |  |
|  | Generator Space Heater - Voltage (v) - Power (w) | Required 230 By Vendor | OK |  |  |  |  |  |
|  | Exciter Type | Self-Excited (PMG is preferred) Brushless, 3 phase sensing | OK |  |  |  |  |  |
|  | Exciter Voltage | By Vendor | LATER |  |  |  |  |  |
|  | Exciter Manufacturer | By Vendor | LATER |  |  |  |  |  |
|  | AVR Model | By Vendor | LATER |  |  |  |  |  |
|  | Voltage Regulation | ±5% | LATER |  |  |  |  |  |
|  | Exciter Current at: (A) Continuous Operation Short time Overload | By Vendor | LATER |  |  |  |  |  |
| - Control Panel |  |  |  |  |  |  |  |  |
|  | Manufacturer | By Vendor | DEEP SEA |  |  |  |  |  |
|  | Standard | IEC, IPS-M-EL-143(3) | IEC |  |  |  |  |  |
|  | Type | Fixed | OK |  |  |  |  |  |
|  | Construction | Self-Standing | SKID MOUNTED |  |  |  |  |  |
|  | Sheet Steel Thickness | 2mm Wall / 2.5 mm Frame | LATER |  |  |  |  |  |
|  | Access | Front Via Hinged Door | SKID MOUNTED |  |  |  |  |  |
|  | Location | Outdoor (Under Shelter) | INSIDE CANOPY |  |  |  |  |  |
|  | Ingress Protection | IP54 | XX |  |  |  |  |  |
|  | Busbar System | 3Ph+N+PE | OK |  |  |  |  |  |
|  | Rated Busbar Current (A) | 800 | OK |  |  |  |  |  |
|  | Busbar Material | Copper (Insulated With Heat Shrink) | OK |  |  |  |  |  |
|  | Protection Functions (Embedded in ACB Protection Unit) | - Overload 49 - Phase over current 50/51 Earth fault 50N/51N | OK |  |  |  |  |  |
|  | Protection Functions (Other Than ACB Protection Unit) | According to “BK-GCS-PEDCO-120-EL-SL-0002” | PLEASE SEND FOR REVIEW |  |  |  |  |  |
|  | Controller Manufacturer / Model no. | By Vendor | DEEP SEA |  |  |  |  |  |
|  | Indicators on Panel | - Gen. Voltages (Analogue) - Gen. Currents - Gen. Frequency (Analogue) - Battery charging ammeter - Power factor meter - Jacket water temperature - Lubricating oil temp. - Lubricating oil press. - Hours run meter - Watt meter - Watt-hour meter - VAR-hour meter VAR meter | ALL IN CONTROLLER DEEP SEA |  |  |  |  |  |
|  | Transducers (4~20mA Output) | - Generator Voltage Frequency | NO |  |  |  |  |  |
|  | Generator Neutral CT Manufacturer Rating & Class | Required for 51G protection Required for 64R protection By Vendor 51G: 800/5A, Cl. 5P10 | NO |  |  |  |  |  |
|  | Earth Fault Protections Manufacturer Type Setting Range | Required BY Vendor Solid state By Vendor | LATER |  |  |  |  |  |
|  | Panel Accessories | Anti-Condensation Heater Panel Lighting Removable Gland Plate | OK |  |  |  |  |  |
|  | Finish Color | RAL 7032 | LATER |  |  |  |  |  |
|  | Cable entry | Bottom via Cable Gland | OK |  |  |  |  |  |
|  | Cable Specification & Size From Generator to Local Panel: From Local Panel to LV switchgear: | CU/XLPE/AWA/PVC By Vendor 2x(1x300mm²) Phase 1 2x(1x300mm²) Phase 2 2x(1x300mm²) Phase 3 1x(1x3300mm²) Neutral | LATER |  |  |  |  |  |
| - Switching Device |  |  |  |  |  |  |  |  |
|  | Type of Switching Device | ACB | MCB |  |  |  |  |  |
|  | Manufacturer | By Vendor | LATER |  |  |  |  |  |
|  | Type Designation | By Vendor | XX |  |  |  |  |  |
|  | Operating Mechanism | Motor Operated, Spring Charged, Stored Energy, Trip Free Mechanism | OK |  |  |  |  |  |
|  | Number of Poles | 4 | OK |  |  |  |  |  |
|  | Rated Current (A) | 800 | OK |  |  |  |  |  |
|  | Rated Voltage (V) | 690 | OK |  |  |  |  |  |
|  | Standard | IEC | OK |  |  |  |  |  |
|  | Rated Breaking Current | Not Less Than 35kA | OK |  |  |  |  |  |
|  | Charging Motor Operating Voltage (V) | 24 (Fed from diesel batteries) | OK |  |  |  |  |  |
|  | Trip Unit | Electronic type | OK |  |  |  |  |  |
|  | Trip Unit Functions | 49, 50, 51, 50N, 51N | OK |  |  |  |  |  |
|  | Trip Unit Model | By Vendor | XX |  |  |  |  |  |
| - Generator Accessories |  |  |  |  |  |  |  |  |
|  | RTD (Pt100) | Yes (9 RTD’s for S > 500kVA) | NO |  |  |  |  |  |
|  | Lifting Bolts | Yes | OK |  |  |  |  |  |
|  | Earthing Bolt | Yes | OK |  |  |  |  |  |
|  | Drain Plug | Yes | OK |  |  |  |  |  |
| - General |  |  |  |  |  |  |  |  |
|  | Noise Level | Not More than 81dB @ No Load | 85 DB |  |  |  |  |  |
|  | Weight of Diesel Engine Without Oil and Water (Kg) | By Vendor | LATER |  |  |  |  |  |
|  | Weight of Generator (Kg) | By Vendor | LATER |  |  |  |  |  |
|  | Weight of Diesel Generator Skid (Kg) | By Vendor | LATER |  |  |  |  |  |
|  | Overall Dimension of Diesel Generator Skid (W x D x H) (mm) | By Vendor | LATER |  |  |  |  |  |
|  | Dimension of Control Panel (W x D x H) (mm) | By Vendor | LATER |  |  |  |  |  |

STATUS LEGENDS:

A=Acceptable

N=Not Acceptable

N/A=Not Applicable

INA=Information Not Available

C=Clarification is Required

CA= Conditionally Acceptable

M = Requirement is Mandatory

Conclusion Table:

| Item | Equipment | Vendor 1 | Vendor 2 | Vendor 3 |
| --- | --- | --- | --- | --- |
| 1 | Diesel Generator | X | X | X |

Conclusion Note:

Vendor 1

Vendor 2

Vendor3