## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
TBE FOR FIRE WATER PUMP
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 8
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | TB | 0011 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
TBE FOR FIRE WATER PUMP نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | NOV.2024 |  | FI |  |  |  | V.Amjadi |  |  | M.Fakharian |  | M.Sadeghian
D00 |  | DEC.2022 |  | IFI |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 3 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-709236
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Record Sheet
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
TBE For Fire Water Pump
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 8
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | TB | 0011 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 59
2 | X | X | [6 empty] | 60
3 | X | [7 empty] | 61
4 | X | [7 empty] | 62
5 | X | [7 empty] | 63
6 | X | [7 empty] | 64
7 | X | [7 empty] | 65
8 | X | [7 empty] | 66
9 | [8 empty] | 67
10 | [8 empty] | 68
11 | [8 empty] | 69
12 | [8 empty] | 70
13 | [8 empty] | 71
14 | [8 empty] | 72
15 | [8 empty] | 73
16 | [8 empty] | 74
17 | [8 empty] | 75
18 | [8 empty] | 76
19 | [8 empty] | 77
20 | [8 empty] | 78
21 | [8 empty] | 79
22 | [8 empty] | 80
23 | [8 empty] | 81
24 | [8 empty] | 82
25 | [8 empty] | 83
26 | [8 empty] | 84
27 | [8 empty] | 85
28 | [8 empty] | 86
29 | [8 empty] | 87
30 | [8 empty] | 88
31 | [8 empty] | 89
32 | [8 empty] | 90
33 | [8 empty] | 91
34 | [8 empty] | 92
35 | [8 empty] | 93
36 | [8 empty] | 94
37 | [8 empty] | 95
38 | [8 empty] | 96
39 | [8 empty] | 97
40 | [8 empty] | 98
41 | [8 empty] | 99
42 | [8 empty] | 100
43 | [8 empty] | 101
44 | [8 empty] | 102
45 | [8 empty] | 103
46 | [8 empty] | 104
47 | [8 empty] | 105
48 | [8 empty] | 106
49 | [8 empty] | 107
50 | [8 empty] | 108
51 | [8 empty] | 109
52 | [8 empty] | 110
53 | [8 empty] | 111
54 | [8 empty] | 112
55 | [8 empty] | 113
56 | [8 empty] | 114
57 | [8 empty] | 115
58 | [8 empty] | 116

## TBE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
TBE For Fire Water Pump
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  |  | شماره صفحه: 3 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME |  | TB | 0011 |  | D01
REQ. NO. |  | BK-GCS-PEDCO-120-ME-MR-0011 |  | BIDDER NAME: |  |  |  | Arya Sepehr Kayhan |  |  | Petro Rahan Co. |  |  | PETCO |  |  | Kalay e Pump
QUOTATION NO.: | [7 empty] | ASK-HEN-TS-A0 |  |  | PJ01-112011 |  |  | 401-1244 |  |  | 7-5093
QUOTATION DATE: | [7 empty] | 1401-08-22 |  |  | 1401-08-24 |  |  | 1401-08-11 |  |  | 19.11.2022
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED |  |  |  | MEETS REQUISITION REQUIREMENTS
[10 empty] | Status |  |  | Status |  |  | Status |  | Status
1 | GENERAL
1 | Origine of Manufacturer |  |  | VTS |  |  |  | IRAN |  | Y | PETRO RAHAN PUMP |  | Y | PETCO IRAN |  | Y | IRAN | Y
2 | Delivery Time |  |  | VTS |  |  |  | 8 Month |  | Y | 150 WORKINGS DAYS |  | Y | 8 MONTHS |  | Y | 7-8 Mounths | Y
3 | Design Life |  |  | 25 years |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | 25 years | Y
2 | Scope Of Supply
1 | Complete Pump Units |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Motor Driver |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Diesel Engine |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | Pump Controllers |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
5 | Common Skid Under Pump, Motor/Engine, Controller & Batteries |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Foundation Bolts and Nuts with Liners, Shims & Jack Screw |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | Local Control Panel, Cables & Glands |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8 | Piping, Valves & Fittings with its Support |  |  | Required |  |  |  | Confirmed |  | Y | Data is not available |  | N/A | At pump skid |  | Y | Confirmed | Y
9 | Mating Flanges with Bolts, Nuts and Gasket (If Required) |  |  | Required |  |  |  | Confirmed |  | Y | Data is not available |  | N/A | Confirmed |  | Y | Confirmed | Y
10 | Grounding Bosses & Wiring |  |  | Required |  |  |  | Confirmed |  | Y | Data is not available |  | N/A | Confirmed |  | Y | Confirmed | Y
11 | Touch-up Paint |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Data is not available |  | N/A | Confirmed | Y
12 | First Fill Lube Oil |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
13 | Name plates |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
14 | Commissioning Spare Parts |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
15 | Two Years Spare Parts |  |  | Required (As Option) |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
16 | Special Tools for erection, commissioning, test and maintenance |  |  | If Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
17 | Acoustic Enclosure (If Required) |  |  | Required |  |  |  | Confirmed |  | Y | Not required |  | Y | Not required |  | Y | Not required | Y
3 | Scope of Work
1 | Engineering & Documentation |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Manufacturing & Assembling |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Mounting and Alignment |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | PIM (pre-inspection meeting) |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
5 | Procurement |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Inspection & Testing at shop |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | Performance Guarantee |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8 | Mechanical Guarantee |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
9 | Wiring & Tubing to JB |  |  | Required |  |  |  | Confirmed |  | Y | Data is not available |  | N/A | Confirmed |  | Y | Confirmed | Y
10 | Interconnecting piping inside unit assembly, including lubrication and cooling circuits. |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | At pump skid |  | Y | Confirmed | Y
11 | Painting |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
12 | Packing & Preservation |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
13 | Shipping & Transportation |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
14 | Export customs clearance |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | If any |  | Y | Confirmed | Y
15 | Obtain any export license or other official authorization |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Not required |  | Y | Confirmed | Y
16 | Supervision for Installation |  |  | Required (As Option) |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed(As Option) | Y
17 | Supervision for Pre-commissioning, commissioning & Start up |  |  | Required (As Option) |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed(As Option) | Y
18 | Vendor Shop Training for Owner’s Personnel |  |  | Required (As Option) |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed(As Option) | Y
4 | Inspection & Test
1 | Quality Control Plan (QCP)/ Inspection and Test Plan |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Copy of Quality Management System Certificate (According to ISO 9001) |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Certification (Material, IP, EX, etc.) |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | Surface & Subsurface Examinations |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
5 | NDE (RT,UT, MT, PT) |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Hydrostatic Test (1.5 x MAWP) |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | Mechanical Runninig Test |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8 | Complete Unit Test |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
9 | Over speed test of diesel engine @ 110% of rated speed |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
10 | Performance Test |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
11 | NPSH Test |  |  | If Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y

## TBE (2)
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
TBE For Fire Water Pump
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  |  | شماره صفحه: 4 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME |  | TB | 0011 |  | D01
REQ. NO. |  | BK-GCS-PEDCO-120-ME-MR-0011 |  | BIDDER NAME: |  |  |  | Arya Sepehr Kayhan |  |  | Petro Rahan Co. |  |  | PETCO |  |  | Kalay e Pump
QUOTATION NO.: | [7 empty] | ASK-HEN-TS-A0 |  |  | PJ01-112011 |  |  | 401-1244 |  |  | 7-5093
QUOTATION DATE: | [7 empty] | 1401-08-22 |  |  | 1401-08-24 |  |  | 1401-08-11 |  |  | 19.11.2022
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED |  |  |  | MEETS REQUISITION REQUIREMENTS
[10 empty] | Status |  |  | Status |  |  | Status |  | Status
5 | Guarantees
1 | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site. |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Exhaust Emissions Less Than specified limits in “Specification For Environmental Job; BK-GNRAL-PEDCO-000-SA-SP-0004" |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Exeption & Deviation
1 | Submitted Deviation List |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | JOCKEY PUMPS (P-2302 A/B)
7-1 | Operating Conditions
1 | Item No. |  |  | P-2302 A/B |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Service Name |  |  | Jockey Fire Water Pump |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Number required |  |  | 1+1 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | 1+1 | Y
4 | Proposed Model No. |  |  | VTS |  |  |  | OH2 40-315 |  | Y | OH2 40-315 |  | Y | CP-25.315 |  | Y | KP2532 | Y
5 | Applicable of Code & Standards/ Edition |  |  | NFPA 20 -2019 & IPS-M-PM-125 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Pump Type |  |  | Vendor to specify |  |  |  | Centrifugal/OH2 |  | Y | Centrifugal/OH2 |  | Y | Centrifugal/OH2 |  | Y | Centrifugal/OH2 | Y
7 | Driver Type |  |  | Electrical Motor |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8 | Vapor Pressure (bara) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
9 | Viscosity (cP) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
10 | Density (kg/m3) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
11 | Pumping Temperature (°C) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
12 | Capacity (Rated) (m3/hr) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
13 | Discharge Pressure (barg) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
14 | Suction Pressure (Max./Min.) (barg) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
15 | Diff. Pressure (bar) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
16 | Diff. Head (m) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
17 | NPSH Available (m) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
18 | Hydraulic Power (kw) |  |  | As per Purchaser's Data Sheet |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7-2 | Site Condition
1 | Location |  |  | Outdoor/Under Shelter |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Area Classification. |  |  | Safe |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7-3 | Design (Performance Features)
1 | Pump Speed (rpm) |  |  | VTS |  |  |  | 2950 |  | Y | 2950 |  | Y | 3000 |  | Y | 2950 | Y
2 | NPSH Required (m) |  |  | VTS |  |  |  | 1.4 |  | Y | 2 |  | Y | 2 |  | Y | 1.5 | Y
3 | NPSH Margin (m) |  |  | More Than 1 Meter |  |  |  | 7.4 |  | Y | 6.8 |  | Y | 6.8 |  | Y | 7.3 | Y
4 | Efficiency (%) |  |  | VTS |  |  |  | 28 |  | Y | 31.5 |  | Y | 31 |  | Y | 29 | Y
5 | Rated Power (KW) |  |  | VTS |  |  |  | 15.28 |  | Y | 14 |  | Y | 13.79 |  | Y | 14.8 | Y
6 | BEP Capacity (m³/h) |  |  | VTS |  |  |  | 17.6 |  | Y | 22.5 |  | Y | 25 |  | Y | 19 | Y
7 | Min. Continuous Flow (m³/h) |  |  | VTS |  |  |  | 5.3 |  | Y | 6 |  | Y | 7.5 |  | Y | 5.7 | Y
8 | Max. Head @ Rated Impeller (m) |  |  | VTS |  |  |  | 115.5 |  | Y | 107 |  | Y | 118.1 |  | Y | 119 | Y
9 | Percentage of Head Rise (Rated to Shut-off) (%) |  |  | less than 115% |  |  |  | 110% |  | Y | 102% |  | Y | 112% |  | Y | 113% | Y
10 | Impeller Diameter (min / rated / max) (mm) |  |  | VTS |  |  |  | 260/278/320 |  | Y | 260/276/315 |  | Y | 250/277/314 |  | Y | 250/286/324 | Y
11 | Impeller Mounted |  |  | VTS |  |  |  | Overhoung |  | Y | Overhoung |  | Y | Overhoung |  | Y | Overhoung | Y

## TBE (3)
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
TBE For Fire Water Pump
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  |  | شماره صفحه: 5 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME |  | TB | 0011 |  | D01
REQ. NO. |  | BK-GCS-PEDCO-120-ME-MR-0011 |  | BIDDER NAME: |  |  |  | Arya Sepehr Kayhan |  |  | Petro Rahan Co. |  |  | PETCO |  |  | Kalay e Pump
QUOTATION NO.: | [7 empty] | ASK-HEN-TS-A0 |  |  | PJ01-112011 |  |  | 401-1244 |  |  | 7-5093
QUOTATION DATE: | [7 empty] | 1401-08-22 |  |  | 1401-08-24 |  |  | 1401-08-11 |  |  | 19.11.2022
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED |  |  |  | MEETS REQUISITION REQUIREMENTS
[10 empty] | Status |  |  | Status |  |  | Status |  | Status
7-4 | Design (Construction Features)
1 | MAWP / Design Temperature (Barg / ºc) |  |  | VTS/ 85 |  |  |  | 40 @ 38 ºc |  | Y | 40 @ 38 ºc |  | Y | 17.5 @ 50°c |  | Y | 17 @ 50°c | Y
2 | Hydrotest Pressure (Barg) |  |  | 1.5x MAWP |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Casing , Split / Type |  |  | Radially |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | Suc. / Disch. Nozzle Arrangement |  |  | VTS |  |  |  | End / Top |  | Y | End / Top |  | Y | End / Top |  | Y | End / Top | Y
5 | Suc. Nozzle Size / Rating / Facing |  |  | VTS / 300# / RF |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Disch. Nozzle Size / Rating / Facing |  |  | VTS / 300# / RF |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | First Stage Suction (Single / Double) |  |  | Single |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8 | Vent , Size / Type |  |  | VTS |  |  |  | Self Vent |  | Y | Self Vent |  | Y | Self Vent |  | Y | Self Vent | Y
9 | Drain, Size / Type |  |  | VTS |  |  |  | 1/2" / Flanged |  | Y | 1/2" / Flanged |  | Y | 1/2" / N/A |  | Y | 1/2" / Flanged | Y
10 | Seal Type |  |  | Mechanical Seal |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
11 | Interconnecting Piping |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Loose items will be supplied | Y
7-5 | MATERIAL
1 | API Class |  |  | I-2 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Casing / Barrel |  |  | VTS |  |  |  | ASTM A396 |  | Y | ASTM A396 |  | Y | ASTM A396 |  | Y | ASTM A536 60-40-16 | Y
3 | Impeller |  |  | VTS |  |  |  | C92200 |  | Y | C95500 |  | Y | C95200 |  | Y | C95200 | Y
4 | Shaft |  |  | VTS |  |  |  | AISI 416 |  | Y | A276 Type 420 |  | Y | AISI 416 (S.S Alloy) |  | Y | A276 Type 420 | Y
5 | Wear Rings: Casing , Impeller |  |  | VTS |  |  |  | C92200 |  | Y | C95500 |  | Y | C95200 |  | Y | C95200 | Y
6 | Sleeve |  |  | VTS |  |  |  | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available | N/A
7 | Baseplate |  |  | VTS |  |  |  | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available | N/A
7-6 | Design (Driver Features)
1 | Type / Model |  |  | Induction Motor/VTS |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Manufacturer |  |  | VTS |  |  |  | VEM/HYOSUNG |  | Y | WEG/SIEMENS |  | N/A | WEG/VEM/NANYANG |  | Y | OME | Y
3 | Nameplate HP (KW) |  |  | VTS |  |  |  | 30 |  | Y | 22 |  | Y | 22 |  | Y | 18.5 | Y
4 | Rated Speed (rpm) |  |  | VTS |  |  |  | 2950 |  | Y | 2950 |  | Y | 2950 |  | Y | 2950 | Y
5 | Constant Speed |  |  | Yes |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Voltage / Phase / Hertz |  |  | 400/3/50 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | Area Classification |  |  | Safe Area |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8 | IP Protection |  |  | IP55 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
9 | Insulation Class / Temp. Rise |  |  | F/B |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7-7 | Design (Control & Instrumentation)
1 | Local Control Panel |  |  | Required as per NFPA20 & project specification |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Type of Control System |  |  | As per project requirement |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7-8 | Design (Accessories Features)
1 | Bearing Type: Radial / Axial |  |  | VTS |  |  |  | ROLLER / BALL |  | Y | ROLLER / BALL |  | Y | ROLLER / BALL |  | Y | ROLLER / BALL | Y
2 | Bearing Manufacturer |  |  | VTS |  |  |  | SKF/FAG |  | Y | SKF/FAG |  | Y | SKF |  | Y | SKF/FAG | Y
3 | Seal Type |  |  | Single (Plane 11) |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | Seal Manufacturer |  |  | VTS |  |  |  | Burgmann Pars /turbo seal |  | Y | JOHN CRANE/BURGMAN PARS |  | Y | BURGMANN PARS |  | Y | Turbo Seal Tech | Y
5 | Coupling Type / Manufacturer |  |  | Metalic Disk Felexible Spacer Type Coupling |  |  |  | Metalic Disk Felexible Spacer Type/turbo seal |  | Y | Metalic Disk Felexible Spacer Type/PETRO RAHAN PUMP/ JOHN CRANE |  | Y | Metalic Disk Felexible Spacer Type/PETCO |  | Y | Metalic Disk Felexible Spacer Type/Turbo Seal Tech | Y
6 | Coupling Service Factor |  |  | min 1.5 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | Coupling Guard |  |  | Non-Sparking |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7-9 | WEIGHT/ DIMENSION
1 | Pump (Kg) |  |  | VTS |  |  |  | 190 |  | Y | 70 |  | Y | 128 |  | Y | 125 | Y
2 | Baseplate (Kg) |  |  | VTS |  |  |  | 320 |  | Y | 100 |  | Y | 275 |  | Y | Data is not available | N/A
3 | Motor (Kg) |  |  | VTS |  |  |  | 165 |  | Y | 100 |  | Y | 300 |  | Y | 115 | Y
4 | Total (Electric Motor pump) (Kg) |  |  | VTS |  |  |  | 675 |  | Y | 270 |  | Y | 720 |  | Y | 240 | Y
5 | Length / Width / Height (m) (m * m * m) |  |  | VTS |  |  |  | 1840*760*725 |  | Y | 1300*550*470 |  | Y | Data is not available |  | N/A | 0.3 x 0.3 x 1.5 | Y

## TBE (4)
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
TBE For Fire Water Pump
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  |  | شماره صفحه: 6 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME |  | TB | 0011 |  | D01
REQ. NO. |  | BK-GCS-PEDCO-120-ME-MR-0011 |  | BIDDER NAME: |  |  |  | Arya Sepehr Kayhan |  |  | Petro Rahan Co. |  |  | PETCO |  |  | Kalay e Pump
QUOTATION NO.: | [7 empty] | ASK-HEN-TS-A0 |  |  | PJ01-112011 |  |  | 401-1244 |  |  | 7-5093
QUOTATION DATE: | [7 empty] | 1401-08-22 |  |  | 1401-08-24 |  |  | 1401-08-11 |  |  | 19.11.2022
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED |  |  |  | MEETS REQUISITION REQUIREMENTS
[10 empty] | Status |  |  | Status |  |  | Status |  | Status
8 | MAIN PUMPS (P-2301 A/B)
8-1 | Operating Condition
1 | Item No. |  |  | P-2301 A/B |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Service Name |  |  | Main Fire Water Pump |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Number required |  |  | 1 (Electrical) +1 (Diesel) |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | Proposed Model No. |  |  | VTS |  |  |  | BB1 200-600 |  | Y | DSP200-500 |  | Y | HGT1-200.510 |  | Y | KPSPF 150-570 | Y
5 | Applicable of Code & Standards/ Edition |  |  | NFPA 20 -2019 & IPS-M-PM-125 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Pump Type |  |  | Axially Split (Between Bearing)-BB1 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | Driver Type |  |  | Electrical Motor & Diesel Engine |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8 | Vapor Pressure (bara) |  |  | As per Purchaser's Data Sheet |  |  |  | 0.1219 |  | Y | 0.1219 |  | Y | 0.1219 |  | Y | 0.1219 | Y
9 | Viscosity (Cp) |  |  | As per Purchaser's Data Sheet |  |  |  | 1 |  | Y | 1 |  | Y | 1 |  | Y | 1 | Y
10 | Density (kg/m3) |  |  | As per Purchaser's Data Sheet |  |  |  | 997 |  | Y | 997 |  | Y | 997 |  | Y | 997 | Y
11 | Pumping Temperature (°C) |  |  | As per Purchaser's Data Sheet |  |  |  | 50 |  | Y | 50 |  | Y | 50 |  | Y | 50 | Y
12 | Capacity (Rated) (m3/hr) |  |  | As per Purchaser's Data Sheet |  |  |  | 454.2 |  | Y | 454.2 |  | Y | 454.2 |  | Y | 454.2 | Y
13 | Discharge Pressure (barg) |  |  | As per Purchaser's Data Sheet |  |  |  | 10.4 |  | Y | 10.4 |  | Y | 10.4 |  | Y | 10.4 | Y
14 | Suction Pressure (Max./Min.) (barg) |  |  | As per Purchaser's Data Sheet |  |  |  | 0.83 |  | Y | 0.83 |  | Y | 0.83 |  | Y | 0.83 | Y
15 | Diff. Pressure (bar) |  |  | As per Purchaser's Data Sheet |  |  |  | 10.3 |  | Y | 10.3 |  | Y | 10.3 |  | Y | 10.3 | Y
16 | Diff. Head (m) |  |  | As per Purchaser's Data Sheet |  |  |  | 105 |  | Y | 105 |  | Y | 105 |  | Y | 105 | Y
17 | NPSH Available (m) |  |  | As per Purchaser's Data Sheet |  |  |  | 8.8 |  | Y | 8.8 |  | Y | 8.8 |  | Y | 8.8 | Y
18 | Hydraulic Power (kW) |  |  | As per Purchaser's Data Sheet |  |  |  | 129.5 |  | Y | 129.5 |  | Y | 129.5 |  | Y | 129.5 | Y
8-2 | Site Condition
1 | Location |  |  | Outdoor/Under Shelter |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Area Classification |  |  | Safe |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8-3 | Design (Performance Features)
1 | Pump Speed (rpm) |  |  | VTS |  |  |  | 1450 |  | Y | 1450 |  | Y | 1500 |  | Y | 1490 | Y
2 | NPSH Required (m) |  |  | VTS |  |  |  | 3.8 |  | Y | 2 |  | Y | 3 |  | Y | 3.5 | Y
3 | NPSH Margin (m) |  |  | More Than 1 Meter |  |  |  | 5 |  | Y | 6.8 |  | Y | 5.8 |  | Y | 5.3 | Y
4 | Efficiency (%) |  |  | VTS |  |  |  | 65% |  | Y | 73% |  | Y | 70% |  | Y | 72% | Y
5 | Rated Power (kW) |  |  | VTS |  |  |  | 199.34 |  | Y | 176.3 |  | Y | 183.7 |  | Y | 180.5 | Y
6 | BEP Capacity (m³/h) |  |  | VTS |  |  |  | 522.3 |  | Y | 560 |  | Y | 592.3 |  | Y | 489 | Y
7 | Min. Continuous Flow (m³/h) |  |  | VTS |  |  |  | 182.8 |  | Y | 150 |  | Y | 177.69 |  | Y | 146 | Y
8 | Max. Head @ Rated Impeller (m) |  |  | VTS |  |  |  | 117.6 |  | Y | 116 |  | Y | 115.9 |  | Y | 120 | Y
9 | Percentage of Head Rise (Rated to Shut-off) (%) |  |  | more than 110% and less than 115% |  |  |  | 112 |  | Y | 110 |  | Y | 110 |  | Y | 114 | Y
10 | Impeller Diameter (min / rated / max) (mm) |  |  | VTS |  |  |  | 490/579/605 |  | Y | 490/558/590 |  | Y | 450 / 565 / 580 |  | Y | 450 / 530 / 585 | Y
11 | Impeller Mounted |  |  | Between Bearing |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8-4 | Design (Construction Features)
1 | MAWP / Design Temperature (Barg / ºc) |  |  | VTS/ 85 |  |  |  | 20 @ 38ºc |  | Y | 20 @ 55ºc |  | Y | 25 @ 50ºc |  | Y | 17 @ 50ºc | Y
2 | Hydrotest Pressure (Barg) |  |  | 1.5x MAWP |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Casing , Split / Type |  |  | Axially |  |  |  | Confirmed |  | Y | Confirmed |  | A | Confirmed |  | Y | Confirmed | Y
4 | Suc. / Disch. Nozzle Arrangement |  |  | VTS/VTS |  |  |  | Side/Side |  | Y | Side/Side |  | A | Side/Side |  | Y | Side/Side | Y
5 | Suc. Nozzle Size / Rating / Facing |  |  | VTS / 300# / RF |  |  |  | 10"/300# / RF |  | Y | 10"/300# / RF |  | Y | 10"/150# / RF |  | N | 8"/150# / RF | N
6 | Disch. Nozzle Size / Rating / Facing |  |  | VTS / 300# / RF |  |  |  | 8"/300# / RF |  | Y | 8"/300# / RF |  | Y | 8"/150# / RF |  | N | 6"/150# / RF | N
7 | First Stage Suction (Single / Double) |  |  | VTS |  |  |  | Single |  | Y | Single |  | Y | Single |  | Y | Single | Y
8 | Vent , Size / Type |  |  | VTS |  |  |  | Data is not available |  | N/A | 3/4"/150#/RF |  | N | 3/4"/150#/RF |  | N | 1/2"/150#/RF | N
9 | Drain, Size / Type |  |  | VTS |  |  |  | Data is not available |  | N/A | 3/4"/150#/RF |  | Y | 3/4"/150#/RF |  | N | 1/2"/150#/RF | N
10 | Seal Type |  |  | Packing |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
11 | Interconnecting Piping |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Loose items will be supplied | Y
12 | PSV on discharge line (Diesel engine driven pump) |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y

## TBE (5)
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
TBE For Fire Water Pump
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  |  | شماره صفحه: 7 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME |  | TB | 0011 |  | D01
REQ. NO. |  | BK-GCS-PEDCO-120-ME-MR-0011 |  | BIDDER NAME: |  |  |  | Arya Sepehr Kayhan |  |  | Petro Rahan Co. |  |  | PETCO |  |  | Kalay e Pump
QUOTATION NO.: | [7 empty] | ASK-HEN-TS-A0 |  |  | PJ01-112011 |  |  | 401-1244 |  |  | 7-5093
QUOTATION DATE: | [7 empty] | 1401-08-22 |  |  | 1401-08-24 |  |  | 1401-08-11 |  |  | 19.11.2022
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED |  |  |  | MEETS REQUISITION REQUIREMENTS
[10 empty] | Status |  |  | Status |  |  | Status |  | Status
8-5 | MATERIAL
1 | API Class |  |  | I-2 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Casing / Barrel |  |  | Cast Iron |  |  |  | ASTM A396 |  | Y | ASTM A396 |  | Y | ASTM A396 |  | Y | ASTM A536 60-40-16 | Y
3 | Impeller |  |  | Bronze |  |  |  | C92200 |  | Y | C95500 |  | Y | C95200 |  | Y | C95200 | Y
4 | Shaft |  |  | VTS |  |  |  | AISI 416 |  | Y | A276 Type 420 |  | Y | AISI 416 (S.S Alloy) |  | Y | A276 Type 420 | Y
5 | Wear Rings: Casing , Impeller |  |  | VTS |  |  |  | C92200 |  | Y | C95500 |  | Y | C95200 |  | Y | C95200 | Y
6 | Sleeve |  |  | VTS |  |  |  | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available | N/A
7 | Baseplate |  |  | VTS |  |  |  | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available | N/A
8-6 | Design (Electrical Driver Features)
1 | Type / Model |  |  | Induction Motor/VTS |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Number Required |  |  | 1 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Manufacturer |  |  | VTS |  |  |  | VEM/HYOSUNG |  | Y | WEG/SIEMENS |  | N/A | WEG/VEM/NANYANG |  | Y | OME | Y
4 | Nameplate HP (KW) |  |  | VTS |  |  |  | 315 |  | Y | 300 |  | Y | 280 |  | Y | 250 after derating | Y
5 | Rated Speed (rpm) |  |  | VTS |  |  |  | 1450 |  | Y | 1450 |  | Y | 1500 |  | Y | 1490 | Y
6 | Constant Speed |  |  | Yes |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | Voltage / Phase / Hertz |  |  | 3300/3/50 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8 | Area Classification |  |  | Safe Area |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
9 | IP Protection |  |  | IP55 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
10 | Insulation Class / Temp. Rise |  |  | F/B |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8-7 | Design (Diesel Engine Features)
1 | Type / Model |  |  | 4 Stroke Turbocharger, Constant speed |  |  |  | VOLVO /TAD1342 GE |  | Y | VOLVO /TAD1341 GE |  | Y | VOLVO /TAD1342 GE |  | Y | VOLVO /TAD1341 GE | Y
2 | Applicable Codes & Standards |  |  | ISO 3046 & NFPA 20 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Number Required |  |  | 1 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | Manufacturer |  |  | VTS |  |  |  | VOLVO |  | Y | VOLVO |  | Y | VOLVO |  | Y | VOLVO | Y
5 | Site Condition |  |  | 5°C / 50°C |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
6 | Rated Speed/Max. Allowable Speed (rpm) |  |  | VTS / VTS |  |  |  | 1450 |  | Y | 1500 |  | Y | 1500 |  | Y | 1490 | Y
7 | Diesel Power ( Gross/ Net ) @ ISO condition (Kw) |  |  | VTS |  |  |  | 343 |  | Y | 308 |  | Y | 343 |  | Y | 308 | Y
8 | Engine Power @ site condition (Kw) |  |  | VTS |  |  |  | 315 |  | Y | 275 |  | Y | 303 |  | Y | 250 | Y
9 | Power Requirement @ 150% of Rated Flow (Kw) |  |  | VTS |  |  |  | 297.6 |  | Y | 210 |  | Y | 245.97 |  | Y | 241 | Y
10 | Power Transmission |  |  | Metalic Disk Felexible Spacer Type Coupling |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
11 | Derating Factors |  |  | VTS |  |  |  | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available |  | N/A | Data is not available | N/A
12 | Governor Type |  |  | Electronic |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8-8 | Diesel Engine (Fuel System)
1 | Fuel Filter |  |  | Duplex |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Fuel Tank Design |  |  | NFPA 20 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Daily Fuel Tank Capacity (separated for each set of diesel pump) |  |  | As Per NFPA 20 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | Specific Fuel consumption at prime power (g/kWh) |  |  | VTS |  |  |  | 191 |  | Y | 191 |  | Y | 191 |  | Y | 191 | Y
8-9 | Diesel Engine(Intake & Exhaust)
1 | Intake Filter |  |  | Single / Dry |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Intake Silencer / Exhaust Silencer |  |  | VTS / Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Not applicable / Included | Y
3 | Expansion Joint |  |  | Required |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8-10 | Diesel Engine(Starting System)
1 | Type |  |  | Remote/Local |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Primary /Secondary Starting |  |  | Electric Starting/Electric Starting |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
3 | Starting Capacity |  |  | As Per NFPA 20 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | No. of Battery |  |  | 2 Set (Ni-Cd) |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
5 | Battery Charger |  |  | VTS ( two recharging means is required) |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y

## TBE (6)
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
TBE For Fire Water Pump
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  |  | شماره صفحه: 8 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME |  | TB | 0011 |  | D01
REQ. NO. |  | BK-GCS-PEDCO-120-ME-MR-0011 |  | BIDDER NAME: |  |  |  | Arya Sepehr Kayhan |  |  | Petro Rahan Co. |  |  | PETCO |  |  | Kalay e Pump
QUOTATION NO.: | [7 empty] | ASK-HEN-TS-A0 |  |  | PJ01-112011 |  |  | 401-1244 |  |  | 7-5093
QUOTATION DATE: | [7 empty] | 1401-08-22 |  |  | 1401-08-24 |  |  | 1401-08-11 |  |  | 19.11.2022
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED |  |  |  | MEETS REQUISITION REQUIREMENTS
[10 empty] | Status |  |  | Status |  |  | Status |  | Status
8-11 | Diesel Engine (Lubrication System)
1 | Lube Oil Filter |  |  | Duplex with change-over valves |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Lube Oil Cooler Type |  |  | VTS |  |  |  | Water cooled, Shell & Tube |  | Y | Water cooled, Shell & Tube |  | Y | Water cooled, Shell & Tube |  | Y | Water cooled, Shell & Tube | Y
3 | Lube Oil Pump |  |  | VTS |  |  |  | Gear type |  | Y | Gear type |  | Y | Gear type |  | Y | Gear type | Y
4 | Lube Oil Capacity (l/h) |  |  | VTS |  |  |  | 0.04 |  | Y | 0.04 |  | Y | 0.04 |  | Y | 0.04 | Y
8-12 | Design (Control & Instrumentation)
1 | Local Control Panel |  |  | Required as per NFPA20 & project specification |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
2 | Type of Control System |  |  | As per project requirement |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8-13 | Design (Accessories Features)
1 | Bearing Type: Radial / Axial |  |  | VTS |  |  |  | Anti-Friction |  | Y | BALL/BALL |  | Y | Ball / Ball |  | Y | Roller / Ball | Y
2 | Bearing Manufacturer |  |  | VTS |  |  |  | SKF/FAG |  | Y | SKF/FAG |  | Y | SKF |  | Y | SKF/FAG | Y
3 | Seal Type |  |  | Packing |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
4 | Seal Manufacturer |  |  | VTS |  |  |  | Burgmann Pars /turbo seal |  | Y | JOHN CRANE/BURGMAN PARS |  | Y | BURGMANN PARS |  | Y | Turbo Seal Tech | Y
5 | Coupling Type / Manufacturer |  |  | Metalic Disk Felexible Spacer Type Coupling |  |  |  | Metalic Disk Felexible Spacer Type/turbo seal |  | Y | Metalic Disk Felexible Spacer Type/PETRO RAHAN PUMP/ JOHN CRANE |  | Y | Metalic Disk Felexible Spacer Type/PETCO |  | Y | Metalic Disk Felexible Spacer Type/Turbo Seal Tech | Y
6 | Coupling Service Factor |  |  | min 1.5 |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
7 | Coupling Guard |  |  | Non-Spark type |  |  |  | Confirmed |  | Y | Confirmed |  | Y | Confirmed |  | Y | Confirmed | Y
8-14 | Weight/Dimension
1 | Pump (Kg) |  |  | VTS |  |  |  | Data is not available |  | N/A | 700 |  | Y | as sample estimated 800 kg |  | Y | 1025 | Y
2 | Baseplate (Kg) |  |  | VTS |  |  |  | Data is not available |  | N/A | 550 |  | Y | as sample estimated 1100 kg |  | Y | 720 | Y
3 | Motor (Kg) |  |  | VTS |  |  |  | Data is not available |  | N/A | 1900 |  | Y | as sample estimated 1900 kg |  | Y | 2600 | Y
4 | Engine Weight (kg) |  |  | VTS |  |  |  | 1325 |  | Y | 1325 |  | Y | 1325 |  | Y | 1325 | Y
5 | Engine Dimension (mm) |  |  | VTS |  |  |  | 1114*2206*1391 |  | Y | 1106*2204*1391 |  | Y | 1114*2206*1391 |  | Y | 1114*2206*1391 | Y
6 | Total (Electric Motor pump) (Kg) |  |  | VTS |  |  |  | Data is not available |  | N/A | 2600 |  | Y | 3900 |  | Y | 5070 | Y
7 | Length / Width / Height (m) (m * m * m) |  |  | VTS |  |  |  | 3000*1800*1500 |  | Y | 3800*1800*1500 |  | Y | 3100*1305*1835 |  | Y | 3200x1400x1540 | Y
F | Manufacturer's Location |  |  | - |  |  |  | TABRIZ - IRAN |  |  | TEHRAN-IRAN |  |  | TABRIZ - IRAN |  |  | TEHRAN-IRAN
G | General Technical acceptance of Quotation |  |  | -
FINAL CONCLUSION | [7 empty] | ACCEPTED |  |  | ACCEPTED |  |  | ACCEPTED |  |  | ACCEPTED
Notes:
1) ABBREVIATIONS: Y: ACCEPTED By Bidder, N: NOT ACCEPTED By Bidder, N.A.: NOT APPLICABLE, VTF: Vendor to Follow, C:Clarification Required, C.A: Conditionally Accepted with Some Notes, N/A: Not Available

## Page18 (hidden)
[5 empty] | CCEC DOCUMENT NUMBER | [6 empty] | DOCUMENT NUMBER
[5 empty] | UNIT NO. | GROUP |  | SUB-UNIT | TYPE | DOC. NO. |  | JOB | TYPE |  | SIZE | GROUP |  | DOC. NO.
[12 empty] | 1248 | DS |  | 4 | EMR |  | 22022
[5 empty] | CCEC PROJECT NO.: | [6 empty] | SHEET | 18 |  | OF | 20 |  | REV. | C2
MECHANICAL DATA SHEET FOR HYDROGEN RECYCLE RECIPROCATING COMPRESSOR (API 618)
1 | NOTES
2
3 | 1. Hydrogen Recycle Compressor is foreseen to be a reciprocating compressor. Number of stages to be decided | [17 empty] | C2
4 | by vendor.
5 | Indicated capacities exclude kick-back. Actual capacities to be specified by vendor.
6 | The compressor shall be designed for the following intermittent operating cases:
7 | a) Normal: 100% load on Front End and Methanol loop is not in operation. Recycle hydrogen extracted from D-2005.
8 | b) Import H2: Hydrogen from BL
9 | c) Startup: Startup of reforming section with methanol. Recycle hydrogen extracted from D-2005.
10 | 2. Gas loss is foreseen to be negligible. Manufacturer to indicate expected gas loss if any.
11 | 3. Hydrogen Recycle Compressor is to be supplied as a package, comprising( but not limitied to) the following: | [17 empty] | C2
12 | a) Compressor complete with all ancillary equipment/piping/instrumentation
13 | b)Electric motor driver
14 | c) Pulsation dampers.
15 | d)Common baseplate as specified
16 | e) Capacity control in steps by valve unloaders and/or clearance pocket.
17 | f) Dedicated kick-back system for max capacity viz. cooler, KO drum and associated equipment.
18 | g) Instrumentation to UCP. The UCP shall communicate with DCS via redundant RS-485 modbus serial link for
19 |  | reporting and monitoring. For more detail refer to Spec. Doc. No. 1248-SP-4-EJJ-40009
20 | h) Full capacity safety valves on compressor discharge. Set pressure is 60 barg
21 | i) and as required for safe and efficient operation of the compressor.
22 | 4. Requirement for acoustic housing to be determined by Vendor. | [17 empty] | C2
23 | 5. Force cylinder cooling is foreseen. | [17 empty] | C2
24 | 6. Pressure relief valve with one spare at discharge of compressor shall be furnished by the compressor vendor. | [17 empty] | C2
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
OWNER DOCUMENT NUMBER |  |  | PROJECT NO. | ORIGINATOR |  |  | AREA |  | GROUP |  | TYPE |  |  | SIZE |  |  | SEQUENCE
|  |  | 133/17 | CCEC |  |  | PR |  | RE |  | DSH |  |  | 4 |  |  | 22022

## Page19 (hidden)
[14 empty] | DOCUMENT NUMBER | [13 empty] | DOCUMENT NUMBER
[14 empty] | JOB |  |  | TYPE |  | SIZE |  |  | GROUP |  |  | DOC. NO. |  |  | JOB |  |  | TYPE |  |  | SIZE |  |  | GROUP |  |  | DOC. NO.
[28 empty] | 1248 |  |  | DS |  |  | 4 |  |  | EMR |  |  | 22022
[14 empty] | CCEC PROJECT NO.: | [13 empty] | SHEET |  |  | 19 |  |  | OF |  |  | 20 |  |  | REV. |  | C2
MOTOR DATA SHEET
1 | APPLICABLE TO: | [5 empty] | PROPOSAL |  |  |  | PURCHASE |  |  |  | AS BUILT | [26 empty] | REV.
2 | FOR |  |  |  | Marjan Petrochemical Company | [12 empty] | UNIT | [23 empty] | C2
3 | SITE |  |  |  | Assaluyeh | [12 empty] | MODEL | [23 empty] | C2
4 | DRIVEN EQUIPMENT TYPE | [7 empty] | Hydrogen Recycle Compressor | [8 empty] | SERIAL NO。 | [23 empty] | C2
5 | DRIVEN EQUIPMENT ITEM NO.: | [7 empty] | MC 2002 | [8 empty] | QUANTITY | [23 empty] | C2
6 | MANUFACTURER | [16 empty] | NEMA FRAME | [23 empty] | C2
7 | NOTE: |  |  | INFORMATION TO BE COMPLETED BY | [8 empty] | m | PURCHASER |  |  |  |  | MANUFACTURER | [6 empty] | PURCHASER OR MACUFACTURER | [15 empty] | C2
6 | OPERATING CONDITIONS | [40 empty] | C2
7 | SITE DATE |  |  |  |  | m | INDOOR | [8 empty] | OUTDOOR | [5 empty] | TEMP RISE |  |  | B |  | ºC ABOVE |  |  |  | ºC BY |  |  |  |  | INSULATION CALSS |  |  |  | F |  | C2
8 | m | ALTITUDE |  |  |  |  | LESS THAN 1000 m | [8 empty] | OTHER |  |  |  | m | m | TEMP RISE CODE (IEC) | [19 empty] | C2
9 |  | AMBIENT TEMPERATURE | [7 empty] | MAX/MIN |  |  | 48 / 5 | [6 empty] | ºC |  | SPACE HEATER | [8 empty] | WATTS | [10 empty] | C2
10 | ELECTRICAL CHARACTERISTICS | [20 empty] | VOLTS |  |  | 230 | [5 empty] | PHASE |  |  | 3 |  |  |  | HERTZ |  | 50 |  | C2
11 |  | VOLTS |  | 6KV |  |  |  | PHASE |  |  | 3 |  |  | HERTZ |  |  | 50 |  |  |  | m | MAX. SHEATH TEMPERATURE | [18 empty] | ºC | C2
12 | ELECTRICAL AREA CLASSIFICATION | [12 empty] | NON-HAZARDOUS | [6 empty] | COOLING WATER (IF REQUIRED) | [20 empty] | C2
13 |  | ZONE |  |  | 2 |  |  | EXPLOSION GROUP |  |  |  |  | IIC |  |  | TEM. CLASS |  |  | T3 |  |  | m | SUPPLY, PRESS | [9 empty] | kg/cm²g, TEMP. | [7 empty] | ºC | C2
14 | m | ATMOSPHERIC MIXTURE | [19 empty] | m | RETURN, PRESS | [9 empty] | kg/cm²g, TEMP. | [7 empty] | ºC | C2
15 | m | IGNITION TEMP | [17 empty] | ºC | AIR / GAS COOLING(IF REQUIRED) | [20 empty] | C2
16 | STARTING METHOD | [8 empty] | DIRECTION ON-LINE | [5 empty] | m | [5 empty] | m | SUPPLY, PRESS | [11 empty] | kg/cm²g |  | FLOW |  |  |  | m³/hr | C2
17 | STARTING METHOD | [7 empty] | m | DIRECTION ON-LINE | [5 empty] | m |  |  |  |  | m | ADJUSTABLE FREQUENCY DRIVE | [19 empty] | C2
18 | STARTING | [7 empty] | m | OFF LOAD | [5 empty] | m | ON LOAD |  |  |  | m | SPEED RANGE FROM | [12 empty] | rpm; TO |  |  |  |  | rpm |  | C2
19 | STARTING VOLTAGE | [7 empty] | m | FULLl | [6 empty] | REDUCED |  | 80 | % | DRIVE METHOD | [20 empty] | C2
20 | [22 empty] | DIRECT |  |  | m | V-BELT |  |  | m | OTHER ,WITH GEAR BOX | [10 empty] | C2
21 | PERFORMANCE | [40 empty] | C2
22 |  | NAMEPLATE POWER | [9 empty] | kW |  | RATED POWER | [5 empty] | kW |  | STARTS PER HOUR | [11 empty] | HOT; | [6 empty] | COLD | C2
23 |  | SPEED, SYNCH | [9 empty] | rpm |  | FULL LOAD | [5 empty] | rpm |  | STALL TIME (Max) | [11 empty] | HOT; | [6 empty] | COLD | C2
24 | LOAD |  |  |  | CURRENT (Amps) | [5 empty] | EFFICIENCY |  |  |  |  | POWER FACTOR | [5 empty] | ACCEL TIME AT NO LOAD / FULL LOAD | [18 empty] | SECONDS | C2
25 | FULL | [20 empty] | STARTING POWER FACTOR | [19 empty] | C2
26 | 75% | [20 empty] | TIME INTERVAL TO REACH MAX. TEMP. @ LOCKED ROTOR, | [19 empty] | C2
27 | 50% | [20 empty] | HOT: | [10 empty] | SECONDS, | COLD | [6 empty] | SECONDS | C2
28 |  | LOCKED ROTOR AMPS: | [17 empty] | Amps |  | MOTOR ROTOR INERTIA (WR2): | [18 empty] | kg-m2 | C2
29 |  | NO LOAD CURRENT | [17 empty] | Amps |  | DRIVEN EQUIPMENT INERTIA (WR²): | [18 empty] | kg-m2 | C2
30 |  | FULL-LOAD TORQUE | [17 empty] | N-m |  | INERTIA CONSTANT (H): | [18 empty] | kW-sec/kVA | C2
31 |  | LOCKED ROTOR TORQUE | [17 empty] | %FLT |  | CRITICAL SPEEDS, 1st: | [19 empty] | C2
32 |  | PULL UP TORQUE | [17 empty] | %FLT |  | REACTANCES, | [19 empty] | C2
33 |  | BREAKDOWN TORQUE | [17 empty] | %FLT |  |  | SUB-TRANSIENT (X"d) | [12 empty] | X/R RATIO | [5 empty] | C2
34 |  | STATOR RESISTANCE | [11 empty] | ohms @ | [5 empty] | °C |  |  | TRANSIENT (X'd) | [18 empty] | C2
35 |  | STATOR RESISTANCE | [11 empty] | ohms @ | [5 empty] | °C |  |  | ZERO SEQUENCE (X0) | [18 empty] | C2
36 |  | ROTOR RESISTANCE AT FULL LOAD | [11 empty] | ohms @ | [5 empty] | °C |  |  | STEADY STATE (X) | [18 empty] | C2
37 |  | ROTOR RESISTANCE AT FULL LOAD | [11 empty] | ohms @ | [5 empty] | °C |  |  | MAGNETIZING (Xm) | [18 empty] | C2
38 |  | ROTOR RESISTANCE AT LOCKED ROTOR | [11 empty] | ohms @ | [5 empty] | °C |  | OPEN CIRCUIT TIME CONSTANT: | [18 empty] | SECONDS | C2
39 |  | ROTOR RESISTANCE AT LOCKED ROTOR | [11 empty] | ohms @ | [5 empty] | °C |  | COOL DOWN TIME: | [6 empty] | RUNNING: | [5 empty] | STOPPED: | [5 empty] | MINS | C2
40 | CONSTRUCTION FEATURES | [40 empty] | C2
41 | CONSTRUCTION (MOUNTING): | [19 empty] | PROTECTION: | [5 empty] | m | E, COMPLY WITH IEC STANDARDS | [13 empty] | C2
42 |  |  | HORZONTAL | [5 empty] | m | IM B3 |  | m | IM | [14 empty] | Ex, HAZARDOUS LOCATION | [13 empty] | C2
43 |  | m | VERTICAL | [5 empty] | m | IM V1 |  | m | IM |  |  | m | WITH CANOPY |  |  |  |  | MOTOR - |  |  |  |  | m | D |  |  | E |  | m | P |  | m | N |  |  |  |  | C2
44 | ENCLOSURE: | [20 empty] | JUNCT. BOX - |  |  |  |  | m | D |  |  | E |  | m | P |  | m | N |  |  |  |  | C2
45 |  |  | MOTOR: | [6 empty] | IP 55 |  | m | IP | [13 empty] | m | IIA |  | m | IIB |  |  | IIC | [7 empty] | C2
46 |  |  | JUNCT. BOX: | [6 empty] | IP 55 |  | m | NEMA 4/4X | [13 empty] | m | T1 |  | m | T2 |  |  | T3 |  | m | T4 |  |  |  |  | C2
47 | COOLING: | [7 empty] | m | IC 01 |  |  | IC 411 |  |  | m | IC 81W |  |  |  | TYPE: |  |  |  | SQUIRREL CAGE | [5 empty] | m | OTHER | [9 empty] | C2
48 | [8 empty] | m | IC616 |  | m | IC 611 |  |  | m | IC | [6 empty] | m | STANDARD | [5 empty] | m | HIGH EFFICIENCY | [5 empty] | m | LOW NOISE |  |  | C2
49 | REMARKS:
50
51
52
53
54
55
56
OWNER DOCUMENT NUMBER | [8 empty] | PROJECT NO. |  |  |  | ORIGINATOR |  |  |  |  | AREA |  |  | GROUP |  |  |  |  | TYPE | [5 empty] | SIZE |  |  |  |  | SEQUENCE
[9 empty] | 133/17 |  |  |  | CCEC |  |  |  |  | PR |  |  | RE |  |  |  |  | DSH | [5 empty] | 4 |  |  |  |  | 22022

## Page20 (hidden)
[12 empty] | DOCUMENT NUMBER | [12 empty] | DOCUMENT NUMBER
[12 empty] | JOB |  |  | TYPE |  | SIZE |  |  | GROUP |  | DOC. NO. |  |  | JOB |  | TYPE |  |  | SIZE |  |  | GROUP | DOC. NO.
[25 empty] | 1248 |  | DS |  |  | 4 |  |  | EMR | 22022
[12 empty] | CCEC PROJECT NO.: | [12 empty] | SHEET |  | 20 |  |  | OF |  |  | 20 | REV. |  | C2
MOTOR DATA SHEET
1 | CONSTRUCTION FEATURES (CONTINUED) | [34 empty] | REV.
2 |  | MATERIAL OF CONSTRUCTION | [17 empty] | MOTOR ROTATION: (FACING MOTOR SHAFT) | [15 empty] | C2
3 |  | FRAME | [7 empty] | BEARING HOUSING | [11 empty] | CW |  |  |  |  | CCW | [5 empty] | BI-DIRECTIONAL |  |  | C2
4 |  | JUNCTION BOX | [7 empty] | SHAST | [9 empty] | FAN: |  | REVERSIBLE |  |  |  |  | UNI-DIRECTIONAL | [5 empty] | NON-SPARKING |  |  | C2
5 |  | BEARING TYPE | [17 empty] | SHAFT EXTENSION/ O.D. mm): | [15 empty] | C2
6 |  | RADIAL |  |  | ANTI-FRICTION |  |  |  |  | TILT PAD | [5 empty] | SLEEVE |  |  |  | SOLID SHAFT | [6 empty] | HOLLOW SHAFT | [5 empty] | TAPERED SHAFT END |  |  | C2
7 |  | THRUST |  |  | ANTI-FRICTION |  |  |  |  | TILT PAD | [9 empty] | ALLOWABLE THRUST (VERTICAL): | [8 empty] | UP |  |  |  | DOWN |  |  | C2
8 |  | BEARING IDENTIFICATION NO | [17 empty] | ALLOWABLE SOUND PRESSURE LEVEL (dBA): | [12 empty] | 85 |  | @1m | C2
9 |  | RADIAL | [6 empty] | THRUST | [10 empty] | ACTUAL SOUND PRESSURE LEVEL (dBA): | [14 empty] | @1m | C2
10 |  | BEARING LUBRICATION | [17 empty] | WEIGHT (kg), NET: | [6 empty] | SHIPPING: | [5 empty] | ROTOR: |  |  | C2
11 |  |  | GREASE | [6 empty] | REGREASING DEVICE | [9 empty] | MAX. MAINT. WEIGHT (kg): | [10 empty] | IDENTIFY: |  |  |  |  | C2
12 |  |  | PRESSURE LUBE SYSTEM, PROVIDED BY | [16 empty] | DIMENSIONS (m),L: | [7 empty] | W: |  |  |  | H: |  |  |  | C2
13 |  |  | FLOW REQ'D | [6 empty] | m³/hr, PRESS | [7 empty] | kg/cm2g |  | BASEPLATE, |  |  |  | COMMMON WITH DRIVEN EQUIPMENT | [11 empty] | C2
14 |  |  | RING OIL | [6 empty] | OIL MIST | [13 empty] | SUPPLIED BY: | [11 empty] | C2
15 |  |  | PURGE | [6 empty] | PURE | [13 empty] | OTHER | [11 empty] | C2
16 |  | BEARING SHIELDING | [7 empty] | SINGLE | [5 empty] | DOUBLE |  |  |  | DRAIN PLUG | [15 empty] | C2
17 |  | COUPLING MFR | [17 empty] | AIR FILTER, TYPE: | [15 empty] | C2
18 |  | TYPE | [17 empty] | MANUFACURER: | [9 empty] | ΔP: |  |  |  |  | kg/cm2g | C2
19 |  | MODEL No. | [17 empty] | HEAT EXCHANGER, REQUIRED FLOW: | [14 empty] | m³/hr | C2
20 |  | SUPPLIED BY | [7 empty] | MTD. BY | [9 empty] | MATERIALS, BODY: | [9 empty] | TUBES: | [5 empty] | C2
21 |  | BEARING TEMP. DETECTORS, NUMBER/BEARING | [10 empty] | 2 | [6 empty] | TUBE CONSTRUCTION: | [5 empty] | SINGLE TUBE |  |  |  |  | DOUBLE TUBE |  |  |  |  | C2
22 |  |  | ELEMENT AND SWITCH | [17 empty] | CORROSION ALLOWANCE | [13 empty] | mm | C2
23 |  |  | TYPE | [5 empty] | LOCATION | [10 empty] | JUNCTION BOX / CABLE DETAILS: | [15 empty] | C2
24 |  |  | SET @ |  |  | (ºC) FOR ALARM | [11 empty] | (ºC) FOR SHUTDOWN |  |  | CONDUCTOR MATERIAL FOR MAIN MOTOR LEADS: | [10 empty] | Copper |  |  |  | C2
25 |  |  | MATERIAL | [6 empty] | RESISTANCE | [7 empty] | (ohm) |  |  | MAIN MOTOR LEAD CONDUCTOR DIAMETER | [13 empty] | mm | C2
26 |  | WINDING TEMPERATURE DETECTORS, NUMBER / PHASE | [12 empty] | 2 | [5 empty] | MMAIN MOTOR LEAD INSULATOR DIAMETER | [13 empty] | mm | C2
27 |  |  | ELEMENT AND SWITCH | [16 empty] | MAIN MOTOR LEADS: | [6 empty] | ARMORED CABLE | [5 empty] | FLEXIBLE CONDUIT |  |  | C2
28 |  |  | TYPE | [5 empty] | LOCATION | [10 empty] | CABLE CLAMPS: | [15 empty] | C2
29 |  |  | SET @ |  |  | (ºC) FOR ALARM | [11 empty] | (ºC) FOR SHUTDOWN |  |  | FLEXIBLE | [14 empty] | C2
30 |  |  | MATERIAL | [6 empty] | RESISTANCE | [7 empty] | (ohm) |  |  | TAPPED SCREWS, SIZE / TYPE | [14 empty] | C2
31 |  | SEPARATE JUNCTION BOX FOR WINDING/BEARING TEMP. MONITORS | [17 empty] | MAIN JUNCTION BOX CONTAINS | [15 empty] | C2
32 |  | VIBRATION SWITCHES, MANUFACTURER | [18 empty] | MAIN MOTOR LEADS | [7 empty] | SPACE HEATER LEADS | [6 empty] | C2
33 |  | VIBRATION DETECTORS; MFR | [18 empty] | SURGE ARRESTORS | [7 empty] | STRESS CONES | [6 empty] | C2
34 |  |  | MODEL | [6 empty] | TYPE | [9 empty] | MOTOR ARRANGED FOR DIFFERENTIAL PROTECTION | [15 empty] | C2
35 |  |  | NO PER BEARING | [6 empty] | LOCATION | [10 empty] | SELF BALANCE | [14 empty] | C2
36 |  |  |  | SET @ |  |  | ALARM; |  |  |  |  | SHUTDOWN | [5 empty] | (mm/sec) |  |  | CONVENTIONAL PHASE PHASE DIFFERENTIAL | [14 empty] | C2
37 |  | SEPARATE JUNCTION BOX FOR VIBRATION MONITORS | [18 empty] | SUPPLIED BY | [14 empty] | C2
38 | [19 empty] | BOTH END OF MAIN MOTOR LEADS BROUGHT OUT OF JUNCTION BOX | [15 empty] | C2
39 | TESTING | [18 empty] | SEPARATE JUNCTION BOX FOR SPACE HEATER | [15 empty] | C2
40 | TESTING | [6 empty] | REQUIRED | [5 empty] | WITNESS | [5 empty] | GROUND CONNECTION | [15 empty] | C2
41 |  | PERFORMANCE | [18 empty] | DRILLED AND TAPPED HOLE IN CONDUIT BOX | [14 empty] | C2
42 |  | ROUTINE TEST PER IEC | [18 empty] | GROUND LUG SIZE | [14 empty] | C2
43 |  | SPECIAL TEST | [17 empty] | JUNCTION BOX MOUNTING LOCATION (FACING COUPLING END): | [15 empty] | C2
44 |  | SAMPLE COIL | [18 empty] | RIGHT SIDE |  |  |  |  | LEFT SIDE | [5 empty] | TOP |  |  |  | C2
45 |  | CERTIFIED TEST RESULTS | [17 empty] | JUNCTION BOX ORIENTATION, CABLE ENTRY FROM: | [15 empty] | C2
46 | [20 empty] | TOP |  | BOTTOM |  |  |  | DRIVE END |  |  |  |  | NON-DRIVE END |  |  |  | C2
47 | OTHER (ACCORDING TO VENDOR'S STANDARD) | [12 empty] | REQUIRED | [21 empty] | C2
48 |  | CERTIFICATE OF CONFORMANCE | [16 empty] | MISCELLANEOUS | [16 empty] | C2
49 |  | CLEANLINESS TEST | [16 empty] | SHIPMENT | [5 empty] | DOMESTIC | [7 empty] | EXPORT |  |  | C2
50 |  | BEARING INSPECTION AFTER TEST | [17 empty] | EXPORT BOXING REQUIRED | [15 empty] | C2
51 |  | BEARING CLEARANCE/CRUSH RECORD | [17 empty] | OUTDOOR STORAGE OVER 6 MONTHS | [15 empty] | C2
52 |  | LATERAL CRITICAL SPEED ANALYSIS | [16 empty] | PAINTING/SHIPMENT PREP. | [7 empty] | MFR STANDARD | [8 empty] | C2
53 |  | TORSIONAL CRITICAL SPEED ANALYSIS | [17 empty] | PIPING FIT-UP/ASSEMBLY BEFORE SHIPMENT | [15 empty] | C2
54 |  | VOID FREE COIL DEMONSTRATION | [16 empty] | NAMEPLATE MATERIAL | [7 empty] | 304 SS | [8 empty] | C2
55 |  | STATOR INSPECTION BEFORE VPI | [33 empty] | C2
56 |  | BEARING HOUSING NATURAL FREQUENCY | [33 empty] | C2
57 | REMARKS:
58
59
OWNER DOCUMENT NUMBER | [5 empty] | PROJECT NO. |  |  |  |  | ORIGINATOR |  |  |  |  | AREA |  |  | GROUP |  |  |  | TYPE |  |  |  |  | SIZE |  |  |  |  | SEQUENCE
[6 empty] | 133/17 |  |  |  |  | CCEC |  |  |  |  | PR |  |  | RE |  |  |  | DSH |  |  |  |  | 4 |  |  |  |  | 22022