## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-TB-0011 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1676 |  |  | Transmital Date: 12/10/2022
Document Title: TBE For Fire Water Pump |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-1676 |  |  | Transmital Date: 12/10/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-TB-0011_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Mechanical comments
1 | ARYA SEPHR KEYHAN 1-pressure sensing line is mandatory for all vendors,vendor to confirm 2-Sound pressur for electrical shall be less than 85 dB for diesel pump shall be less than 110 dB 3- automatic air release valve -vacuum breaker in fire pump is according to NFPA 20 , it shall be provided. 4- Compelte unit test and 4 hours mechanical running test for whole package shall be provided and to be withness |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25 | با توجه به اتمام مراحل خریدو مشخص شدن شرکت سازنده، خواهشمند است جهت جلوگیری از تاخیردر مدارک مرتبط با خرید همکاری لازم جهت نهایی شدن مدرک انجام شود.(شرکت کالای پمپ به عنوان سازنده پمپ های آتش نشانی انتخاب شده است)
2 | 5- ITP'comment will be reviwedd after P.O. , 6-vensor shall provide the test curve which recieved the approval of third parties for these size of pump in next revision 7-Rotor balance and coupling balance shall be G2.5 in ITP. 8- Mechanical seal for jocky pump shall be as per API682 , the ASK's Mechanical seal is not acceptable.(Mechacnial seal shall be cart. type) 9-Couplings shall be based on API 671 and for diesel pump shall be Grid Couplings.( Coupling Made of Arya sephr keyhan is not acceptable) |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
3 | 10, vendor to recheck that for I-2 material , RF is suitable. 11- type of skid shall be drip pan , vendor to confirm 12-eccentric and concentic reducer shall be provided 13-NPSH curve shall be provided for max impeller diam. 14- Diesel manufacturer shall be specified and the selected diesel model at least to be specified by vendor 15- flame arrestor, wast cone shall be provided 16- exhaust silencer and flexible joint to be provided by vendor 17- suction and discharge gauge shall be provided by vendor |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
4 | Kalay PUMP 1- Please recheck the gurantee period in proposal 2- NI-Cad batttery is mandatory vendor shall follow 3- Couplings shall be based on API 671 and for diesel pump shall be Grid Couplings.( Coupling Made of Kalay pump is not acceptable) 4- Jocky pump shall be OH type and verticale in-line is not acceptable 5-flame arrestor, wast cone shall be provided 6-NSS/NS shall be mentioned in proposal 7- starting method of fire pump is Open valve, so the proposed main pumps have a negative tolerance at end of curve , so the technical proposal is not acceptable. 8-exhaust silencer and flexible joint to be provided by vendor 9-suction and discharge gauge shall be provided by vendor |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
5 | PETCO exhaust silencer and flexible joint, 2 set NI-cad battery and its charger ,.. to be provided by vendor flame arrestor, wast cone shall be provided Scope of supply & work shall be seal and sigen by vendor Un-price P.O shall be added General arrangment shall be provided |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
6 | Petro rahan BB4 type for jocky pump is not accepted , vendor shall revise your for the main pumps, because of having no suitable margin, the proposed pump is not accepted, in addition of this, the vendor's model of pumps based on impeller dia.are not specified , so this proposal of this vendor is not acceptable . if vendor is willing to be considered as bidder, it is necessary to follow project requirment |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
7 | The TBE is not totally accepted because of lack of informationa and supporting document as following TCL for all vendors , Deviation list, TBE reprort shall be provided by Hirgan All vendors shall provided his P&ID or at least project PID shall be seal and sigen |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
| please find attached file |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
Electrical comments
| پيشنهاد فني براي تمامي وندورها همسنگ گردد. مثلاً اسناد و مدارك فني مربوط به ديزل پمپ، فرم هاي تكميل شده TCL و Deviation List و همچنين Drawing اوليه براي موتورها با نمايش جانمايي باكس مربوط به كابل قدرت، هيتر و RTD از تمامي وندورها دريافت گردد. لازم به ذكر است در خصوص RTD ميبايست مطابق با اسناد قراردادي در نظر گرفته شود. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25 | با توجه به اتمام مراحل خریدو مشخص شدن شرکت سازنده، خواهشمند است جهت جلوگیری از تاخیردر مدارک مرتبط با خرید همکاری لازم جهت نهایی شدن مدرک انجام شود
| آخرين نسخه ديتا شيت برقي موتورهاي فشار متوسط و ضعيف توسط وندور ها تكميل و ارسال گردد. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
| لازم است Specification موتورهاي برقي فشار متوسط و ضعيف از سوي وندورها تاييد و ارسال شود. اين آيتم بايستي در TBE قيد گردد. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
| در ITPهاي ارسالي تست هاي مربوط به موتورها اعم از فشار ضعيف و متوسط و همچنين تابلوهاي محلي مطابق با استانداردهاي IPS-M-EL-131&132 و IEC-60034 لحاظ گردد. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
| آخرين نسخه مدارك در پيشنهاد فني توسط وندور استفاده گردد. بعنوان نمونه رويژن 4 مدرك Mechanical Data Sheets For Fire Water Main Pumps - Elect. Motor Driven با ترنسميتال 1683 ارسال گرديده است در حاليكه در TBE ارسالي رويژن 3 توسط وندورها تكميل و ارسال شده است. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
| با توجه به وجود Deviation از سوي برخي وندورها مثلاً آريا سپهر كيهان و يا كالاي پمپ مقتضي است اين موارد در TBE آورده شوند. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
| در پيشنهاد فني آراسا سپهر كيهان نوع باطري هاي استارتر ديزل سرب اسيد ذكر شده است در حالي كه در TBE نوع باطري ها Ni-Cd قيد شده و تاييد شده است. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
Instrumantion comments
| در پروپوزال فني شركت پتروراشان به سيستم كنترل محلي اشاره نشده است, اين درحالي هست كه در جدول TBE ارائه شده Confirm از سوي وندور ثبت شده است. لطفا در اين خصوص شفاف سازي صورت پذيرد. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25 | با توجه به اتمام مراحل خریدو مشخص شدن شرکت سازنده، خواهشمند است جهت جلوگیری از تاخیردر مدارک مرتبط با خرید همکاری لازم جهت نهایی شدن مدرک انجام شود
| در پروپوزال فني وندور شركت پتكو به سيستم كنترل محلي اشاره نشده است، اين درحالي هست كه در جدول TBE ارائه شده Confirm از سوي وندور ثبت شده است. لطفا در اين خصوص شفاف سازي صورت پذيرد. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
| جدول Deviation براي تمامي وندورها مشخص شود. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
| تمامي Sub Vendor ها براي ادوات ابزادقيق و سيستم كنترل محلي در AVL موجود باشند و در Sub vendor list ارائه گردند. |  | BK-SUR-ENG-MEC-01-06524 | 2022-12-25
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: