## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 13
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | EL | LI | 0002 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL POWER & CONTROL CABLE SCHEDULE نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  |  | Nov.2024 |  | IFA |  |  |  | M.Pourdasht |  |  | M.Fakharian |  | M.Sadeghian
D01 |  |  | Nov.2023 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | S.Faramarzpour
D00 |  |  | June.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: F0Z-709067
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 13
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | LI | 0002 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 51
2 | X | X | X | [5 empty] | 52
3 | X | X | X | [5 empty] | 53
4 | X | X | X | [5 empty] | 54
5 | X | X | X | [5 empty] | 55
6 | X | X | X | [5 empty] | 56
7 | X | X | X | [5 empty] | 57
8 | X | X | X | [5 empty] | 58
9 | X | X | X | [5 empty] | 59
10 |  | X | X | [5 empty] | 60
11 |  | X | X | [5 empty] | 61
12 |  | X | X | [5 empty] | 62
13 |  | X | X |  | ` |  |  |  | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## LEGEND
1. ELECTRICAL CABLE NUMBERING SYSTEM
XXX-XXXXX- XX 1 2 3
(1) 1ST Group (Cable Type Commodity Code):
H: High Voltage Power Cable (20 KV & Above)
M: Medium Voltage Power Cable (3.3, 6 KV & up to 20 KV) |  | شماره صفحه: 1 از 13
L: Low Voltage Power Cable (Voltage Less Than 1KV)
C: Control Cables
I: Instrument Cable
(2) 2ND Group
From Equipment
(3) 3RD Group
Consumer Description: To Equipment Which will be fed.
2. CABLE TYPE
A: Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH)
B: Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE)
C: Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE)
D: Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH)
E: Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE)
F: Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE WITH LEAD SHEATH)
G: Cu/SC/XLPE/SC/SCT/Lsh/Bd/AWA/PVC - N2XSYKYRY (MV SINGLE-CORE WITH LEAD SHEATH)
H: Cu/SC/XLPE /SC/SCT/CWS/Bd/AWA/PVC - N2XSYRY (MV SINGLE-CORE)
I: Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE)
J: CU/SM/XLPE/SM/SC/PVC/SWA/PVC - N2XSEYRY (HV MULTI-CORE)
K: CU/SM/XLPE/SM/SC/PVC/AWA/PVC - N2XSYRY (HV SINGLE-CORE)
L: Cu/PVC/PVC - NYY (LV MULTI-CORE FOR LIGHTING)
R: Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE)
S: CU/XLPE/PVC - N2XY (LV SINGLE-CORE FLEXIBLE OR EPR or H07 RN-F)
Z: MICC FIRE RESISTANTCABLE( Mineral Insulated Copper Cable ) FOR HAZARDOUS AREAS SUCH AS BATTERY ROOMS … .
3. REFERANCE LIST
Area Electrical Cable Route & Section Layou | BK-GCS-PEDCO-120-EL-PY-0005
ELECTRICAL LOAD LIST | BK-GCS-PEDCO-120-EL-LI-0001
Existent MV Switchgear Expansion Single Line Diagram | BK-GCS-PEDCO-120-EL-SL-0003
LV Switchgear-MCC Single Line Diagram | BK-GCS-PEDCO-120-EL-SL-0002
Area Lighting & Small Power Layout | BK-GCS-PEDCO-120-EL-PY-0003
Electrical IO Signal List | BK-GCS-PEDCO-120-EL-LI-0005
Notes:
1- The control cable of IRP Pump will be supplied by vendor
Reference documents are as below:
Electrical Cable Route & Section Layout For Switchgear Building of Well Pads (BK-SSGRL-PEDCO-110-EL-PY-0007)
The reference documents For Cable OD is abhar and gland size is S.E.M.C manufacture
تسهیلات
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره صفحه: 3 از 13
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0002
D02
بسته کاری
GCS
پروژه
BK

## GCS
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size | Cable Size (mm) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | Rout
|  |  |  | FROM | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D01 | M-11SWGA-TR001 | 11 | GCS-11-SWG-001A | GCS-TR-001 | 1250KVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | Transformer-001 11/.42 KV
2 | D01 | C-11SWGA-RCP-01 | 0.11DC | GCS-11-SWG-001A | RCP | - | 16×2.5 | 16C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | From 11KV Switchgear A to RCP
3 | D02 | L-NSWGA-TR001-A1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
4 | D02 | L-NSWGA-TR001-A2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
5 | D02 | L-NSWGA-TR001-A3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear |  | شماره صفحه: 1 از 13
6 | D02 | L-NSWGA-TR001-A4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
7 | D02 | L-NSWGA-TR001-B1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
8 | D02 | L-NSWGA-TR001-B2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
9 | D02 | L-NSWGA-TR001-B3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
10 | D02 | L-NSWGA-TR001-B4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
11 | D02 | L-NSWGA-TR001-C1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
12 | D02 | L-NSWGA-TR001-C2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
13 | D02 | L-NSWGA-TR001-C3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
14 | D02 | L-NSWGA-TR001-C4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
15 | D02 | L-NSWGA-TR001-N1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
16 | D02 | L-NSWGA-TR001-N2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear
17 | D01 | C-NSWGA-TR001-1 | 0.11DC | GCS-400-NSWG-001A | GCS-TR-001 | - | 12×2.5 | 12C | 2.5 | - | - | 20 | M25 | M25 | 24.4 | E | Transformer 001 Mechanical Protection
18 | D02 | C-NSWGA-TR001-2 | - | GCS-400-NSWG-001A | GCS-TR-001 | - | 3×6 | 3C | 6 | - | - | 20 | M20 A | M20 A | 16.8 | E | Neutral CT of Transformer 001
19 | D01 | C-NSWGA-TR001-3 | 0.11DC | GCS-400-NSWG-001A | GCS-TR-001 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 24.4 | E | Interlock/Intertrip to Upstrem
20 | D01 | M-11SWGB-TR002 | 11 | GCS-11-SWG-001B | GCS-TR-002 | 1250KVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | Transformer-002 11/.42 KV
21 | D01 | C-11SWGB-RCP-02 | 0.11DC | GCS-11-SWG-001B | RCP | - | 16×2.5 | 16C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | From 11KV Switchgear B to RCP
22 | D02 | L-NSWGB-TR002-A1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
23 | D02 | L-NSWGB-TR002-A2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
24 | D02 | L-NSWGB-TR002-A3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
25 | D02 | L-NSWGB-TR002-A4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
26 | D02 | L-NSWGB-TR002-B1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
27 | D02 | L-NSWGB-TR002-B2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
28 | D02 | L-NSWGB-TR002-B3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
29 | D02 | L-NSWGB-TR002-B4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
30 | D02 | L-NSWGB-TR002-C1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
31 | D02 | L-NSWGB-TR002-C2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
32 | D02 | L-NSWGB-TR002-C3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
33 | D02 | L-NSWGB-TR002-C4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
34 | D02 | L-NSWGB-TR002-N1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
35 | D02 | L-NSWGB-TR002-N2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear
36 | D01 | C-NSWGA-TR002-1 | 0.11DC | GCS-400-NSWG-001B | GCS-TR-002 | - | 12×2.5 | 12C | 2.5 | - | - | 20 | M25 | M25 | 24.4 | E | Transformer 002 Mechanical Protection
37 | D02 | C-NSWGA-TR002-2 | - | GCS-400-NSWG-001B | GCS-TR-002 | - | 3×6 | 3C | 6 | - | - | 20 | M20 A | M20 A | 16.8 | E | Neutral CT of Transformer 002
38 | D01 | C-NSWGA-TR002-3 | 0.11DC | GCS-400-NSWG-001B | GCS-TR-002 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 24.4 | E | Interlock/Intertrip to Upstrem
39 | D01 | M-11SWGB-TR003 | 11 | GCS-11-SWG-001B | GCS-TR-03 | 800 kVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | from Switchgear 11SWGB to Fire Water Transformer 003
40 | D01 | C-11SWGB-RCP-03 | 0.11DC | GCS-11-SWG-001B | RCP | - | 16×2.5 | 16C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | From 11SWGB Switchgear to RCP for Fire Water
41 | D01 | M-TR003-NGR | 3.3 | GCS-TR-003 | GCS-3.3-NGR-01 | - | 1×95 | 1C | 95 | - | - | 10 | M40 | M40 | 35.7 | H | NGR
42 | D01 | C-3.3SWG-TR003-1 | 0.11DC | GCS-3.3-SWG-001 | GCS-TR-03 | - | 12×2.5 | 12C | 2.5 | - | - | 70 | M25 | M25 | 24.4 | E | Transformer 003 Mechanical Protection
43 | D02 | C-3.3SWG-TR003-2 | - | GCS-3.3-SWG-001 | GCS-TR-03 |  | 3×6 | 3C | 6 | - | - | 70 | M20 A | M20 A | 16.8 | E | Neutral CT of Transformer 003
44 | D01 | M-3.3SWG-TR003 | 3.3 | GCS-TR-03 | GCS-3.3-SWG-001 | - | 3×95 | 3C | 95 | - | - | 70 | M75 | M75 | 68.8 | I | from 3.3 Switchgear to Transformer 003
45 | D01 | M-3.3SWG-P2301A | 3.3 | GCS-3.3-SWG-001 | P-2301A | 300 | 3×95 | 3C | 95 | - | - | 250 | M75 | M75 | 68.8 | I | Fire Water Electric Pump
46 | D02 | C-3.3SWG-LCS | 0.11DC | GCS-3.3-SWG-001 | P-2301A | - | 12×2.5 | 12C | 2.5 | - | - | 250 | M25 | M25 | 24.4 | E | LCS for P-2301A
47 | D02 | C-3.3SWG-IRP-01 | 0.23 | GCS-3.3-SWG-001 | IRP-DCS | - | 5×2.5 | 5C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for P-2301A
47 | D02 | C-3.3SWG-IRP-02 | 0.23 | GCS-3.3-SWG-001 | IRP-F&G | - | 5×2.5 | 5C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-F&G for P-2301A
48 | D01 | M-11SWGA-C2101-A | 11 | GCS-11-SWG-001A | C-2101A | 1250 | 3×95 | 3C | 95 | - | - | 270 | M90 | M90 EX | 87.7 | F | First & Second Stage Gas Compressor C-2101A
49 | D01 | L-11SWGA-SPH-A | 0.23 | GCS-11-SWG-001A | Space Heater | 0.3 | 2×4 | 2C | 4 | 4 | - | 270 | M20 A | M20 EX | 21 | A | Space Heater for Gas Compressor C-2101A
50 | D01 | C-11SWGA-IRP-A | 0.11DC | GCS-11-SWG-001A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 40 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Gas Compressor C-2101A
51 | D02 | C-11SWGA-IRP-A (ESD) | 0.11DC | GCS-11-SWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP (ESD) for Gas Compressor C-2101A
52 | D02 | C-11SWGA-C2101-A | - | GCS-11-SWG-001A | C-2101A | - | 2×4 | 2C | 4 | - | - | 270 | M25 | M25 EX | 22.6 | D | Ammeter for Gas Compressor C-2101A
53 | D02 | C-11SWGA-RTD2101-A1 | - | UCP-A | C-2101A | - | 12×(3×1.5) | 3C | 1.5 | - | - | 300 | M50 | M50 EX | 41 | R | RTD for Gas Compressor C-2101A (From Control Room for Stator)
54 | D02 | C-11SWGA-RTD2101-A2 | - | UCP-A | C-2101A | - | 3×3×1.5 | 9C | 1.5 | - | - | 0 | M32 | M32EX |  |  | RTD for Gas Compressor C-2101A (From Control Room for beraing)
55 | D02 | C-11SWGA-DF2101-A | - | GCS-11-SWG-001A | C-2101A | - | 6×6 | 6C | 6 | - | - | 270 | M32 | M32 EX | - | D | Differential Protection of C-2101A
56 | D01 | M-11SWGA-CAP-A | 11 | GCS-11-SWG-001A | Cap Bank A | 360 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Capacitor Bank for Gas Compressor C-2101A
57 | D02 | C-11SWGA-CAP-A | 0.11DC | GCS-11-SWG-001A | Cap Bank A | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Control for Capacitor Bank of C-2101A
58 | D02 | L-NSWGA-MCC2101A | 0.4 | GCS-400-NSWG-001A | MCC-2101A | 43.9 | 3×35+16 | 5C | 35 | 16 | - | 25 | M32 | M32 | 32.1 | B | Normal Panel for Gas Compressor C-2101A (Auxiliary)
59 | D02 | L-MCC2101A-OH | 0.23 | MCC-2101A | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 250 | M25 | M25 EX | 27.2 | A | Oil Heater for Gas Compressor C-2101A
60 | D01 | C-MCC2101A-OH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Oil Heater C-2101A
61 | D02 | L-MCC2101A-BR | 0.4 | MCC-2101A | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 250 | M25 | M25 EX | 23.5 | A | Barring Device Motor for Gas Compressor C-2101A
62 | D01 | C-MCC2101A-BR01 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Barring Device Motor C-2101A
63 | D02 | C-MCC2101A-BR02 | - | MCC-2101A | Barring Device Motor | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Barring Device Motor C-2101A
64 | D02 | L-MCC2101A-AP | 0.4 | MCC-2101A | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Oil Pump for Gas Compressor C-2101A (P-2101-AP A)
65 | D01 | C-MCC2101A-AP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Oil Pump C-2101A
66 | D02 | C-MCC2101A-AP2 | - | MCC-2101A | Oil Pump | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Oil Pump C-2101A
67 | D02 | L-MCC2101A-OC | 0.4 | MCC-2101A | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 250 | M32 | M32 EX | 26.7 | A | Lube Oil Cooler for Gas Compressor C-2101A (AE-2101-OC A)
68 | D01 | C-MCC2101A-OC1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Lube Oil Cooler C-2101A
69 | D02 | C-MCC2101A-OC2 | - | MCC-2101A | Oil Cooler | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Lube Oil Cooler Motor C-2101A
70 | D02 | L-MCC2101A-LP | 0.4 | MCC-2101A | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 250 | M20 A | M20 EX | 22.6 | A | Cylinder Lubricator Pump for Gas Compressor C-2101A (M-2101-LP A)
71 | D01 | C-MCC2101A-LP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Cylinder Lubricator Pump C-2101A
72 | D02 | C-MCC2101A-LP2 | - | MCC-2101A | Lubricator Pump | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Cylinder Lubricator Pump C-2101A
73 | D02 | L-MCC2101A-LH | 0.23 | MCC-2101A | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 250 | M20 A | M20 EX | 21 | A | Cylinder Lubricator Oil Heater for Gas Compressor C-2101A
74 | D01 | C-MCC2101A-LH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Cylinder Lubricator Oil Heater C-2101A
75 | D02 | L-MCC2101A-AX | 0.4 | MCC-2101A | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Aux Pump Motor for Gas Compressor C-2101A (P-2101-AX A)
76 | D01 | C-MCC2101A-AX1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Aux Pump Motor C-2101A
77 | D02 | C-MCC2101A-AX2 | - | MCC-2101A | Aux Pump Motor | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Aux Pump Motor C-2101A
78 | D02 | L-MCC2101A-WP | 0.4 | MCC-2101A | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Main Pump Motor for Gas Compressor C-2101A (P-2101-WP A)
79 | D01 | C-MCC2101A-WP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Main Pump Motor C-2101A
80 | D02 | C-MCC2101A-WP2 | - | MCC-2101A | Main Pump Motor | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Main Pump Motor C-2101A
81 | D02 | L-MCC2101A-WH | 0.4 | MCC-2101A | Electric Heater | 12 | 3×70+35 | 5C | 70 | 35 | - | 250 | M50 | M50 EX | 47.9 | A | Electric Heater for Gas Compressor C-2101A (P-2101-WH A)
82 | D01 | C-MCC2101A-WH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Electric Heater C-2101A
83 | D02 | L-MCC2101A-WC | 0.4 | MCC-2101A | Water Console | 4 | 3×10 | 3C | 10 | - | - | 250 | M32 | M32 EX | 26.7 | A | Water Console Cooler Motor for Gas Compressor C-2101A (AE-2101-WC A)
84 | D01 | C-MCC2101A-WC1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Water Console Cooler Motor C-2101A
85 | D02 | C-MCC2101A-WC2 | - | MCC-2101A | Water Console | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101A
86 | D02 | C-MCC2101A-EHT | 0.23 | MCC-2101A | Heat Trace A | - | 5x25 | 5C | 25 | 25 | 25 | 300 | M32 | M32 | 32.1 | B | Electrcial Heat Trace for Compressor A | HOLD
87 | D01 | M-11SWGB-C2101-B | 11 | GCS-11-SWG-001B | C-2101B | 1250 | 3×95 | 3C | 95 | - | - | 300 | M90 | M90 EX | 87.7 | F | First & Second Stage Gas Compressor C-2101B
88 | D01 | L-11SWGB-SPH-B | 0.23 | GCS-11-SWG-001B | Space Heater | 0.3 | 2×4 | 2C | 4 | 4 | - | 300 | M25 | M25 EX | 21 | A | Space Heater for Gas Compressor C-2101B
89 | D01 | C-11SWGB-IRP-B | 0.11DC | GCS-11-SWG-001B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 40 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Gas Compressor C-2101B
90 | D02 | C-11SWGB-IRP-B (ESD) | 0.11DC | GCS-11-SWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP (ESD) for Gas Compressor C-2101B
91 | D02 | C-11SWGB-C2101-B | - | GCS-11-SWG-001B | C-2101B | - | 2×4 | 2C | 4 | - | - | 300 | M25 | M25 EX | 22.6 | D | Ammeter for Gas Compressor C-2101B
92 | D02 | C-11SWGB-RTD2101-B1 | - | UCP-B | C-2101B | - | 12×(3×1.5) | 3C | 1.5 | - | - | 330 | M50 | M50 EX | 41 | R | RTD for Gas Compressor C-2101B (From Control Room for Stator)
93 | D02 | C-11SWGB-RTD2101-B2 | - | UCP-B | C-2101B | - | 3×3×1.5 | 9C | 1.5 | - | - | 0 | M32 | M32EX |  |  | RTD for Gas Compressor C-2101B (From Control Room for beraing)
94 | D02 | C-11SWGB-DF2101-B | - | GCS-11-SWG-001B | C-2101B | - | 6×6 | 6C | 6 | - | - | 300 | M25 | M25 EX | - | D | Differential Protection of C-2101B
95 | D01 | M-11SWGB-CAP-B | 11 | GCS-11-SWG-001B | Cap Bank B | 360 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Capacitor Bank for Gas Compressor C-2101B
96 | D02 | C-11SWGB-CAP-B | 0.11DC | GCS-11-SWG-001B | Cap Bank B | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Control for Capacitor Bank of C-2101B
97 | D02 | L-NSWGB-MCC2101B | 0.4 | GCS-400-NSWG-001B | MCC-2101B | 43.9 | 3×35+16 | 4C | 35 | 16 | - | 25 | M32 | M32 | 32.1 | B | Normal Panel for Gas Compressor C-2101B (Auxiliary)
98 | D02 | L-MCC2101B-OH | 0.23 | MCC-2101B | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 280 | M32 | M32 EX | 27.2 | A | Oil Heater for Gas Compressor C-2101B
99 | D01 | C-MCC2101B-OH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Oil Heater C-2101B
100 | D02 | L-MCC2101B-BR | 0.4 | MCC-2101B | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 280 | M25 | M25 EX | 23.5 | A | Barring Device Motor for Gas Compressor C-2101B
101 | D01 | C-MCC2101B-BR1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Barring Device Motor C-2101B
102 | D02 | C-MCC2101B-BR2 | - | MCC-2101B | Barring Device Motor | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Barring Device Motor for Gas Compressor C-2101B
103 | D02 | L-MCC2101B-AP | 0.4 | MCC-2101B | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Oil Pump for Gas Compressor C-2101B (P-2101-AP B)
104 | D01 | C-MCC2101B-AP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Oil Pump C-2101B
105 | D02 | C-MCC2101B-AP2 | - | MCC-2101B | Oil Pump | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Oil Pump for Gas Compressor C-2101B
106 | D02 | L-MCC2101B-OC | 0.4 | MCC-2101B | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 280 | M32 | M32 EX | 26.7 | A | Lube Oil Cooler for Gas Compressor C-2101B (AE-2101-OC B)
107 | D01 | C-MCC2101B-OC1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Lube Oil Cooler C-2101B
108 | D02 | C-MCC2101B-OC2 | - | MCC-2101B | Oil Cooler | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Lube Oil Cooler for Gas Compressor C-2101B
109 | D02 | L-MCC2101B-LP | 0.4 | MCC-2101B | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | A | Cylinder Lubricator Pump for Gas Compressor C-2101B (M-2101-LP B)
110 | D01 | C-MCC2101B-LP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Cylinder Lubricator Pump C-2101B
111 | D02 | C-MCC2101B-LP2 | - | MCC-2101B | Lubricator Pump | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Cylinder Lubricator Pump for Gas Compressor C-2101B
112 | D02 | L-MCC2101B-LH | 0.23 | MCC-2101B | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 280 | M25 | M25 EX | 21 | A | Cylinder Lubricator Oil Heater for Gas Compressor C-2101B
113 | D01 | C-MCC2101B-LH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Cylinder Lubricator Oil Heater C-2101B
114 | D02 | L-MCC2101B-AX | 0.4 | MCC-2101B | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Aux Pump for Gas Compressor C-2101B (P-2101-AX B)
115 | D01 | C-MCC2101B-AX1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Aux Pump Motor C-2101B
116 | D02 | C-MCC2101B-AX2 | - | MCC-2101B | Aux Pump Motor | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Aux Pump for Gas Compressor C-2101B
117 | D02 | L-MCC2101B-WP | 0.4 | MCC-2101B | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Main Pump for Gas Compressor C-2101B (P-2101-WP B)
118 | D01 | C-MCC2101B-WP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 16×2.5 | 16C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Main Pump Motor C-2101B
119 | D02 | C-MCC2101B-WP2 | - | MCC-2101B | Main Pump Motor | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Main Pump for Gas Compressor C-2101B
120 | D02 | L-MCC2101B-WH | 0.4 | MCC-2101B | Electric Heater | 12 | 3×70+35 | 4C | 70 | 35 | - | 280 | M50 | M50 EX | 47.9 | A | Electric Heater for Gas Compressor C-2101B (P-2101-WH B)
121 | D01 | C-MCC2101B-WH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Electric Heater C-2101B
122 | D02 | L-MCC2101B-WC | 0.4 | MCC-2101B | Water Console | 4 | 3×10 | 3C | 10 | - | - | 280 | M32 | M32 EX | 26.7 | A | Water Console Cooler Motor for Gas Compressor C-2101B (AE-2101-WC B)
123 | D01 | C-MCC2101B-WC1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) forWater Console Cooler Motor C-2101B
124 | D02 | C-MCC2101B-WC2 | - | MCC-2101B | Water Console | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101B
125 | D02 | C-MCC2101B-EHT | 0.23 | MCC-2101B | Heat Trace B | - | 5x25 | 5C | 25 | 25 | 25 | 300 | M32 | M32 | 32.1 | B | Electrcial Heat Trace for Compressor B | HOLD
126 | D02 | M-11SWGC-C2101-A | 11 | GCS-11-SWG-001A | C-2101C | 1250 | 3×95 | 3C | 95 | - | - | 330 | M90 | M90 EX | 87.7 | F | First & Second Stage Gas Compressor C-2101C
127 | D01 | L-11SWGC-SPH-C | 0.23 | GCS-11-SWG-001C | Space Heater | 0.3 | 2×4 | 2C | 4 | 4 | - | 330 | M25 | M25 EX | 21 | A | Space Heater for Gas Compressor C-2101C
128 | D01 | C-11SWGC-IRP-C | 0.11DC | GCS-11-SWG-001C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 40 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Gas Compressor C-2101C
129 | D02 | C-11SWGC-IRP-C (ESD) | 0.11DC | GCS-11-SWG-001C | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP (ESD) for Gas Compressor C-2101C
130 | D02 | C-11SWGC-C2101-C | - | GCS-11-SWG-001C | C-2101C | - | 2×4 | 2C | 4 | - | - | 330 | M25 | M25 EX | 22.6 | D | Ammeter for Gas Compressor C-2101C
131 | D02 | C-11SWGC-RTD2101-C1 | - | UCP-C | C-2101C | - | 12×(3×1.5) | 3C | 1.5 | - | - | 360 | M50 | M50 EX | 41 | R | RTD for Gas Compressor C-2101C (From Control Room for Stator)
132 | D02 | C-11SWGC-RTD2101-C2 |  | UCP-C | C-2101C |  | 3×3×1.5 | 9C | 1.5 |  |  | 0 | M32 | M32 EX |  |  | RTD for Gas Compressor C-2101C (From Control Room for Bearing)
133 | D02 | C-11SWGC-2101-C | - | GCS-11-SWG-001C | C-2101C | - | 6×6 | 6C | 6 | - | - | 330 | M25 | M25 EX | - | D | Differential Protection of C-2101C
134 | D02 | M-11SWGC-CAP-A | 11 | GCS-11-SWG-001A | Cap Bank C | 360 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Capacitor Bank for Gas Compressor C-2101C
135 | D02 | C-11SWGC-CAP-C | 0.11DC | GCS-11-SWG-001C | Cap Bank C | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Control for Capacitor Bank of C-2101C
136 | D02 | L-NSWGC-MCC2101B | 0.4 | GCS-400-NSWG-001B | MCC-2101C | 43.9 | 3×35+16 | 4C | 35 | 16 | - | 25 | M32 | M32 | 32.1 | B | Normal Panel for Gas Compressor C-2101C (Auxiliary)
137 | D02 | L-MCC2101C-OH | 0.23 | MCC-2101C | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 310 | M32 | M32 EX | 27.2 | A | Oil Heater for Gas Compressor C-2101C
138 | D01 | C-MCC2101C-OH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Oil Heater C-2101C
139 | D02 | L-MCC2101C-BR | 0.4 | MCC-2101C | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 310 | M25 | M25 EX | 23.5 | A | Barring Device Motor for Gas Compressor C-2101C
140 | D01 | C-MCC2101C-BR1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Barring Device Motor C-2101C
141 | D02 | C-MCC2101C-BR2 | - | MCC-2101C | Barring Device Motor | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Barring Device Motor for Gas Compressor C-2101C
142 | D02 | L-MCC2101C-AP | 0.4 | MCC-2101C | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Oil Pump for Gas Compressor C-2101C (P-2101-AP C)
143 | D01 | C-MCC2101C-AP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Oil Pump C-2101C
144 | D02 | C-MCC2101C-AP2 | - | MCC-2101C | Oil Pump | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Oil Pump for Gas Compressor C-2101C
145 | D02 | L-MCC2101C-OC | 0.4 | MCC-2101C | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Lube Oil Cooler for Gas Compressor C-2101C (AE-2101-OC C)
146 | D02 | C-MCC2101C-OC1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Lube Oil Cooler C-2101C
147 | D02 | C-MCC2101C-OC2 | - | MCC-2101C | Oil Cooler | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Lube Oil Cooler for Gas Compressor C-2101C
148 | D02 | L-MCC2101C-LP | 0.4 | MCC-2101C | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | A | Cylinder Lubricator Pump for Gas Compressor C-2101C (M-2101-LP C)
149 | D01 | C-MCC2101C-LP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Cylinder Lubricator Pump C-2101C
150 | D02 | C-MCC2101C-LP2 | - | MCC-2101C | Lubricator Pump | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Cylinder Lubricator for Gas Compressor C-2101C
151 | D02 | L-MCC2101C-LH | 0.23 | MCC-2101C | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 310 | M25 | M25 EX | 21 | A | Cylinder Lubricator Oil Heater for Gas Compressor C-2101C
152 | D01 | C-MCC2101C-LH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Cylinder Lubricator Oil Heater C-2101C
153 | D02 | L-MCC2101C-AX | 0.4 | MCC-2101C | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Aux Pump Motor for Gas Compressor C-2101B (P-2101-AX C)
154 | D02 | C-MCC2101C-AX1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Aux Pump Motor C-2101C
155 | D02 | C-MCC2101C-AX2 | - | MCC-2101C | Aux Pump Motor | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Aux Pump Motor for Gas Compressor C-2101C
156 | D02 | L-MCC2101C-WP | 0.4 | MCC-2101C | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Main Pump Motor for Gas Compressor C-2101C (P-2101-WP C)
157 | D01 | C-MCC2101C-WP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Main Pump Motor C-2101C
158 | D02 | C-MCC2101C-WP2 | - | MCC-2101C | Main Pump Motor | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Main Pump Motor for Gas Compressor C-2101C
159 | D02 | L-MCC2101C-WH | 0.4 | MCC-2101C | Electric Heater | 12 | 3×70+35 | 4C | 70 | 35 | - | 310 | M50 | M50 EX | 47.9 | A | Electric Heater for Gas Compressor C-2101B (P-2101-WH C)
160 | D01 | C-MCC2101C-WH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Electric Heater C-2101C
161 | D02 | L-MCC2101C-WC | 0.4 | MCC-2101C | Water Console | 4 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Water Console Cooler Motor for Gas Compressor C-2101C (AE-2101-WC C)
162 | D01 | C-MCC2101C-WC1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | - | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Water Console Cooler Motor C-2101C
163 | D02 | C-MCC2101C-WC2 | - | MCC-2101C | Water Console | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101C
164 | D02 | C-MCC2101C-EHT | 0.23 | MCC-2101B | Heat Trace C | - | 5x25 | 5C | 25 | 25 | 25 | 300 | M32 | M32 | 32.1 | B | Electrcial Heat Trace for Compressor C | HOLD
165 | D02 | L-NSWGA-AC2121A | 0.4 | GCS-400-NSWG-001A | AC-2121A | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 2121A
166 | D02 | C-NSWGA-AC2121A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2121A
167 | D02 | C-NSWGA-AC2121A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2121A
168 | D02 | C-NSWGA-AC2121A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2121A
169 | D02 | L-NSWGA-AC2122A | 0.4 | GCS-400-NSWG-001A | AC-2122A | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 2122A
170 | D02 | C-NSWGA-AC2122A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2122A
171 | D02 | C-NSWGA-AC2122A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2122A
172 | D02 | C-NSWGA-AC2122A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2122A
173 | D02 | L-NSWGB-AC2121B | 0.4 | GCS-400-NSWG-001B | AC-2121B | 5.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 2121B
174 | D02 | C-NSWGB-AC2121B-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2121B
175 | D02 | C-NSWGB-AC2121B-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2121B
176 | D02 | C-NSWGB-AC2121B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2121B
177 | D02 | L-NSWGB-AC2122B | 0.4 | GCS-400-NSWG-001B | AC-2122B | 5.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 2122B
178 | D02 | C-NSWGB-AC2122B-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2122B
179 | D02 | C-NSWGB-AC2122B-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2122B
180 | D02 | C-NSWGB-AC2122B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2122B
181 | D02 | L-NSWGA-AC2121C | 0.4 | GCS-400-NSWG-001A | AC-2121C | 5.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 2121C
182 | D02 | C-NSWGA-AC2121C-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2121C
183 | D02 | C-NSWGA-AC2121C-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2121C
184 | D02 | C-NSWGA-AC2121C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 370 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2121C
185 | D02 | L-NSWGA-AC2122C | 0.4 | GCS-400-NSWG-001A | AC-2122C | 5.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 2122C
186 | D02 | C-NSWGA-AC2122C-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2122C
187 | D02 | C-NSWGA-AC2122C-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2122C
188 | D02 | C-NSWGA-AC2122C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 370 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2122C
189 | D02 | L-NSWGA-AC2131A | 0.4 | GCS-400-NSWG-001A | AC-2131A | 7.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 2131A
190 | D02 | C-NSWGA-AC2131A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2131A
191 | D02 | C-NSWGA-AC2131A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2131A
192 | D02 | C-NSWGA-AC2131A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2131A
193 | D02 | L-NSWGA-AC2132A | 0.4 | GCS-400-NSWG-001A | AC-2132A | 7.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 2132A
194 | D02 | C-NSWGA-AC2132A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2132A
195 | D02 | C-NSWGA-AC2132A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2132A
196 | D02 | C-NSWGA-AC2132A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2132A
197 | D02 | L-NSWGB-AC2131B | 0.4 | GCS-400-NSWG-001B | AC-2131B | 7.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 2132A
198 | D02 | C-NSWGB-AC2131B-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2132A
199 | D02 | C-NSWGB-AC2131B-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2132A
200 | D02 | C-NSWGB-AC2131B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2132A
201 | D02 | L-NSWGB-AC2132B | 0.4 | GCS-400-NSWG-001B | AC-2132B | 7.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 2132A
202 | D02 | C-NSWGB-AC2132B-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2132A
203 | D02 | C-NSWGB-AC2132B-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2132A
204 | D02 | C-NSWGB-AC2132B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2132A
205 | D02 | L-NSWGA-AC2131C | 0.4 | GCS-400-NSWG-001A | AC-2131C | 7.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 2131C
206 | D02 | C-NSWGA-AC2131C-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2131C
207 | D02 | C-NSWGA-AC2131C-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2131C
208 | D02 | C-NSWGA-AC2131C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 370 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2131C
209 | D02 | L-NSWGA-AC2132C | 0.4 | GCS-400-NSWG-001A | AC-2132C | 7.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 2132C
210 | D02 | C-NSWGA-AC2132C-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Air Cooler 2132C
211 | D02 | C-NSWGA-AC2132C-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Air Cooler 2132C
212 | D02 | C-NSWGA-AC2132C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 370 | M32 | M32 EX | 29 | D | LCS for Air Cooler 2132C
213 | D02 | L-NSWGE-PKC2203A1 | 0.4 | GCS-400-NSWG-001E | PK-C-2203A | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Instrument & Plant Air Package A
214 | D02 | L-NSWGE-PKC2203A2 | 0.4 | GCS-400-NSWG-001E | PK-C-2203A | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Instrument & Plant Air Package A
215 | D02 | L-NSWGE-PKC2203B1 | 0.4 | GCS-400-NSWG-001E | PK-C-2203B | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Instrument & Plant Air Package B
216 | D02 | L-NSWGE-PKC2203B2 | 0.4 | GCS-400-NSWG-001E | PK-C-2203B | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Instrument & Plant Air Package B
217 | D02 | L-NSWGA-PK2204-1 | 0.4 | GCS-400-NSWG-001A | PK-2204 | 75 | 3×120+70 | 4C | 120 | 70 | - | 280 | M50 | M50 | 51.9 | B | Nitrogen Package
218 | D02 | L-NSWGA-PK2204-2 | 0.4 | GCS-400-NSWG-001A | PK-2204 | 75 | 3×120+70 | 4C | 120 | 70 | - | 280 | M50 | M50 | 51.9 | B | Nitrogen Package
219 | D02 | L-NSWGA-PK2201 | 0.4 | GCS-400-NSWG-001A | PK-2201 | 30 | 3×120+70 | 4C | 120 | 70 | - | 420 | M63 | M63 | 59.3 | Z | LP Flare Package
220 | D02 | L-NSWGB-PK2207 | 0.4 | GCS-400-NSWG-001B | PK-2207 | 1.85 | 4×10 | 4C | 10 | 10 | - | 250 | M32 | M32 EX | 28.1 | A | Corrosion Inhibitor Package (Chemical Package)
221 | D02 | L-NSWGB-PK2101 | 0.4 | GCS-400-NSWG-001B | PK-2101 | 4.4 | 4×25 | 4C | 25 | - | - | 250 | M63 | M63 EX | 53.8 | A | Dehydration Package
222 | D01 | L-PK2101-P100A | 0.4 | PK-2101 | P-100/A | 2.2 | 3×6 | 3C | 6 | - | - | 330 | M25 | M25 EX | 23.5 | A | Lean Teg Circulation Pump A
223 | D02 | C-PK2101-P100A1 | 0.23 | PK-2101 | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Lean Teg Circulation Pump A
224 | D02 | C-PK2101-P100A2 | 0.23 | PK-2101 | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Lean Teg Circulation Pump A
225 | D01 | C-PK2101-P100A3 | 0.23 | PK-2101 | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 330 | M32 | M32 EX | 29 | D | LCS for Lean Teg Circulation Pump A
226 | D01 | L-PK2101-P100B | 0.4 | PK-2101 | P-100/B | 2.2 | 3×6 | 3C | 6 | - | - | 330 | M25 | M25 EX | 23.5 | A | Lean Teg Circulation Pump B
227 | D02 | C-PK2101-P100B1 | 0.23 | PK-2101 | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Lean Teg Circulation Pump B
228 | D02 | C-PK2101-P100B2 | 0.23 | PK-2101 | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Lean Teg Circulation Pump B
229 | D01 | C-PK2101-P100B3 | 0.23 | PK-2101 | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 330 | M32 | M32 EX | 29 | D | LCS for Lean Teg Circulation Pump B
230 | D02 | L-NSWGE-P2203A | 0.4 | GCS-400-NSWG-001E | P-2203A | 3 | 3×10 | 3C | 10 | - | - | 400 | M32 | M32 EX | 26.7 | A | Sump Pump A
231 | D02 | C-NSWGE-P2203A-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Sump Pump A
232 | D02 | C-NSWGE-P2203A-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Sump Pump A
233 | D02 | C-NSWGE-P2203A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M25 EX | 25.3 | D | LCS for Sump Pump A
234 | D02 | L-NSWGE-P2203B | 0.4 | GCS-400-NSWG-001E | P-2203B | 3 | 3×10 | 3C | 10 | - | - | 400 | M32 | M32 EX | 26.7 | A | Sump Pump B
235 | D02 | C-NSWGE-P2203B-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Sump Pump B
236 | D02 | C-NSWGE-P2203B-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Sump Pump B
237 | D02 | C-NSWGE-P2203B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M25 EX | 25.3 | D | LCS for Sump Pump B
238 | D02 | L-NSWGE-P-2202A | 0.4 | GCS-400-NSWG-001E | P-2202A | 9 | 3×25 | 3C | 25 | - | - | 410 | M32 | M32 EX | 32.4 | A | Closed Drain Pump A
239 | D02 | C-NSWGE-P-2202A-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Closed Drain Pump A
240 | D02 | C-NSWGE-P-2202A-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Closed Drain Pump A
241 | D02 | C-NSWGE-P-2202A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M32 | M32 EX | 29 | D | LCS for Closed Drain Pump A
242 | D02 | L-NSWGE-P-2202B | 0.4 | GCS-400-NSWG-001E | P-2202B | 9 | 3×25 | 3C | 25 | - | - | 410 | M32 | M32 EX | 32.4 | A | Closed Drain Pump B
243 | D02 | C-NSWGE-P-2202B-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Closed Drain Pump B
244 | D02 | C-NSWGE-P-2202B-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Closed Drain Pump B
245 | D02 | C-NSWGE-P-2202B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M32 | M32 EX | 29 | D | LCS for Closed Drain Pump B
246 | D02 | L-NSWGE-P-2101A | 0.4 | GCS-400-NSWG-001E | P-2101A | 15 | 3×16 | 3C | 16 | - | - | 210 | M32 | M32 EX | 28.2 | A | Slug Pump A
247 | D02 | C-NSWGE-P-2101A-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Slug Pump A
248 | D02 | C-NSWGE-P-2101A-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Slug Pump A
249 | D02 | C-NSWGE-P-2101A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 210 | M32 | M32 EX | 29 | D | LCS for Slug Pump A
250 | D02 | L-NSWGE-P-2101B | 0.4 | GCS-400-NSWG-001E | P-2101B | 15 | 3×16 | 3C | 16 | - | - | 210 | M32 | M32 EX | 28.2 | A | Slug Pump B
251 | D02 | C-NSWGE-P-2101B-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Slug Pump B
252 | D02 | C-NSWGE-P-2101B-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Slug Pump B
253 | D02 | C-NSWGE-P-2101B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 210 | M32 | M32 EX | 29 | D | LCS for Slug Pump B
254 | D02 | L-NSWGE-P-2302A | 0.4 | GCS-400-NSWG-001E | P-2302A | 18.5 | 3×25 | 3C | 25 | - | - | 215 | M25 | M25 | 26.4 | B | Fire Water Jockey Pump A Panel
255 | D02 | C-NSWGE-P-2302A | 0.23 | GCS-400-NSWG-001E | LCS | - | 2×4 | 2C | 4 | - | - | 215 | M20 A | M20 A | 16.6 | B | Ammeter for Fire Water Jockey Pump A
256 | D02 | L-NSWGE-P-2302B | 0.4 | GCS-400-NSWG-001E | P-2302B | 18.5 | 3×25 | 3C | 25 | - | - | 215 | M25 | M25 | 26.4 | B | Fire Water Jockey Pump B Panel
257 | D02 | C-NSWGE-P-2302B | 0.23 | GCS-400-NSWG-001E | LCS | - | 3×4 | 3C | 4 | - | - | 215 | M20 A | M20 A | 16.6 | B | LCS for Fire Water Jockey Pump B
258 | D02 | L-NSWGB-P-2209 | 0.4 | GCS-400-NSWG-001B | P-2209 | 3 | 3×4 | 3C | 4 | - | - | 90 | M20 A | M20 A | 16.6 | B | Potable Water Pump
259 | D02 | C-NSWGB-P-2209-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Potable Water Pump
260 | D02 | C-NSWGB-P-2209-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Potable Water Pump
261 | D02 | C-NSWGB-P-2209-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 90 | M25 | M25 | 20 | E | LCS for Potable Water Pump
262 | D02 | L-NSWGB-P-2206 | 0.4 | GCS-400-NSWG-001B | P-2206 | 1.5 | 3×4 | 3C | 4 | - | - | 215 | M20 A | M20 A | 16.6 | B | Diesel Oil Pump
263 | D02 | L-NSWGE-IG-2201 | 0.23 | GCS-400-NSWG-001E | IG-2201 | 1 | 5×10 | 5C | 10 | 10 | 10 | 700 | M25 | M25 | 22.3 | B | LP Flare Ignition Package | HOLD
264 | D02 | L-NSWGE-P-2201A | 0.4 | GCS-400-NSWG-001E | P-2201A | 1.1 | 3×10 | 3C | 10 | - | - | 420 | M20 | M20 EX | 20.7 | A | LP Flare K.O. Drum Pump A
265 | D02 | C-NSWGE-P-2201A-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for LP Flare K.O. Drum Pump A
266 | D02 | C-NSWGE-P-2201A-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for LP Flare K.O. Drum Pump A
267 | D01 | C-NSWGE-P-2201A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 10×2.5 | 7C | 2.5 | - | - | 420 | M32 | M32 EX | 29 | D | LCS for LP Flare K.O. Drum Pump A
268 | D02 | L-NSWGE-P-2201B | 0.4 | GCS-400-NSWG-001E | P-2201B | 1.1 | 3×10 | 3C | 10 | - | - | 420 | M20 | M20 EX | 20.7 | A | LP Flare K.O. Drum Pump B
269 | D02 | C-NSWGE-P-2201B-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for LP Flare K.O. Drum Pump B
270 | D02 | C-NSWGE-P-2201B-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for LP Flare K.O. Drum Pump B
271 | D01 | C-NSWGE-P-2201B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 420 | M32 | M32 EX | 29 | D | LCS for LP Flare K.O. Drum Pump B
272 | D02 | L-NSWGA-P-2103A | 0.4 | GCS-400-NSWG-001A | P-2103A | 5.5 | 3×16 | 3C | 16 | - | - | 370 | M25 | M25 EX | 22.2 | A | Glycol Transfer Pump A
273 | D02 | C-NSWGA-P-2103A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP-DCS for Glycol Transfer Pump A
274 | D02 | C-NSWGA-P-2103A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | IRP-ESD for Glycol Transfer Pump A
275 | D01 | C-NSWGA-P-2103A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M25 EX | 25.3 | D | LCS for Glycol Transfer Pump A
276 | D02 | L-NSWGB-P-2103B | 0.4 | GCS-400-NSWG-001B | P-2103B | 5.5 | 3×16 | 3C | 16 | - | - | 370 | M25 | M25 EX | 22.2 | A | Glycol Transfer Pump B
277 | D02 | C-NSWGB-P-2103B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP--DCS for Glycol Transfer Pump B
278 | D01 | C-NSWGB-P-2103B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M25 EX | 25.3 | D | LCS for Glycol Transfer Pump B
279 | D02 | L-NSWGB-P-2102 | 0.4 | GCS-400-NSWG-001B | P-2102 | 1.1 | 3×10 | 3C | 10 | - | - | 340 | M20 | M20 EX | 20.7 | A | Glycol Manual Pump
280 | D02 | C-NSWGB-P-2102-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP--DCS & ESD for Glycol Manual Pump
281 | D02 | C-NSWGB-P-2102-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Glycol Manual Pump
282 | D02 | L-NSWGB-P-2104 | 0.4 | GCS-400-NSWG-001B | P-2104 | 3 | 3×10 | 3C | 10 | - | - | 400 | M20 | M20 EX | 20.7 | A | Glycol Drain Pump
283 | D02 | C-NSWGB-P-2104-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M25 | M25 | 21.6 | E | IRP--DCS & ESD for Glycol Drain Pump
284 | D01 | C-NSWGB-P-2104-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M25 EX | 25.3 | D | LCS for Glycol Drain Pump
285 | D02 | L-NSWGB-CR-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-CR-01 | 10 | 3×25+16 | 4C | 25 | 16 | - | 260 | M40 | M40 EX | 34.4 | A | Main Compressor Crane
286 | D02 | L-NSWGA-CR-02 | 0.4 | GCS-400-NSWG-001A | GCS-400-CR-02 | 5 | 4×10 | 4C | 10 | 10 | - | 200 | M25 | M25 | 22.1 | B | Fire Water Pumps Crane
287 | D02 | L-NSWGB-NDP-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-NDP-01 | 13.7 | 3×70+35 | 3C | 70 | 35 | - | 250 | M50 | M50 EX | 47.9 | A | Process Area Normal Lighting Panel
288 | D02 | L-NSWGE-EDP-01 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-01 | 3.92 | 4×16 | 4C | 16 | 16 | - | 250 | M25 | M25 EX | 22.2 | A | Process Area Emergency Lighting Panel
289 | D02 | L-NSWGA-NDP-02 | 0.4 | GCS-400-NSWG-001A | GCS-400-NDP-02 | 6.6 | 4×35 | 4C | 35 | 35 | - | 220 | M32 | M32 | 28.6 | B | Utility Area Normal Lighting Panel
290 | D02 | L-NSWGE-EDP-02 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-02 | 3.2 | 4×16 | 4C | 16 | 16 | - | 220 | M25 | M25 | 22.2 | B | Utility Area Emergency Lighting Panel
291 | D02 | L-NSWGB-WS-PR-01 | 0.4 | GCS-400-NSWG-001B | WS-PR-01 | 35 | 3×50+25 | 4C | 50 | 25 | - | 250 | M50 | M50 EX | 42.2 | A | First Welding Receptacle (Process Area)
292 | D01 | L-WS-PR-01-WS-PR-02 | 0.4 | WS-PR-01 | WS-PR-02 | 35 | 3×50+25 | 4C | 50 | 25 | - | 75 | M50 | M50 EX | 42.2 | A | to Junction Box for Second Welding Receptacle (Process Area)
293 | D01 | L-WS-PR-01-SC-PR-01 | 0.23 | WS-PR-01 | SC-PR-01 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Fisrt Outlet Socket (Process Area)
294 | D01 | L-WS-PR-02-SC-PR-02 | 0.23 | WS-PR-02 | SC-PR-02 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Second Outlet Socket (Process Area)
295 | D02 | L-NSWGA-WS-PR-03 | 0.4 | GCS-400-NSWG-001A | WS-PR-03 | 35 | 3×50+25 | 4C | 50 | 25 | - | 310 | M50 | M50 EX | 42.2 | A | Third Welding Receptacle (Process Area)
296 | D01 | L-WS-PR-03-WS-PR-04 | 0.4 | WS-PR-03 | WS-PR-04 | 35 | 3×50+25 | 4C | 50 | 25 | - | 50 | M50 | M50 EX | 42.2 | A | to Junction Box for Fourth Welding Receptacle (Process Area)
297 | D01 | L-WS-PR-03-SC-PR-03 | 0.23 | WS-PR-03 | SC-PR-03 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Third Welding Receptacle (Process Area)
298 | D01 | L-WS-PR-04-WS-PR-05 | 0.4 | WS-PR-04 | WS-PR-05 | 35 | 3×50+25 | 4C | 50 | 25 |  | 60 | M50 | M50 EX | 42.2 | A | to Junction Box for Fifth Welding Receptacle (Process Area)
299 | D01 | L-WS-PR-04-SC-PR-04 | 0.23 | WS-PR-04 | SC-PR-04 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Fourth Outlet Socket (Process Area)
300 | D01 | L-WS-PR-05-WS-SC-05 | 0.23 | WS-PR-05 | SC-PR-05 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Fitfth Outlet Socket (Process Area)
301 | D02 | L-NSWGB-WS-UT-01 | 0.4 | GCS-400-NSWG-001B | WS-UT-01 | 35 | 3×50+25 | 4C | 50 | 25 | - | 225 | M40 | M40 | 36.3 | B | First Welding Receptacle (Utility Area)
302 | D02 | L-WS-UT-01-SC-UT-01 | 0.23 | WS-UT-01 | SC-UT-01 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M20 A | M20 A | 16.6 | B | to Junction Box for First Outlet Socket (Utility Area)
303 | D02 | L-NSWGA-WS-UT-02 | 0.4 | GCS-400-NSWG-001A | WS-UT-02 | 35 | 3×50+25 | 4C | 50 | 25 | - | 275 | M40 | M40 | 36.3 | B | Second Welding Receptacle (Utility Area)
304 | D02 | L-WS-UT-02-SC-UT-02 | 0.23 | WS-UT-02 | SC-UT-02 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M20 A | M20 A | 16.6 | B | to Junction Box for Second Outlet Socket (Utility Area)
305 | D02 | L-NSWGA-CP01 | 0.4 | GCS-400-NSWG-001A | GCS-400-CP01 | 5 | 4×10 | 4C | 10 | 10 | - | 425 | M32 | M32 EX | 28.1 | A | Cathodic Protection Transformer Rectifier1
306 | D02 | L-NSWGA-110-CHG001 | 0.4 | GCS-400-NSWG-001A | GCS-110-CHG-001 | 20 | 3x95 | 3C | 95 | - | - | 25 | M25 | M25 | 24.5 | B | 110VDC Charger 1
307 | D01 | L-110-CHG001-FB1 | 0.11DC | GCS-110-CHG-001 | 110-Fuse Box 1 | 7.5 | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | B | DC Charger Fuse Box 1
308 | D01 | L-110CH-FB1-BAT1 | 0.11DC | 110-Fuse Box 1 | 110-Battery Bank 1 | 7.5 | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | B | DC Charger Battery Bank 1
309 | D02 | L-NSWGE-110-CHG002 | 0.4 | GCS-400-NSWG-001E | GCS-110-CHG-002 | 20 | 3x95 | 3C | 95 | - | - | 30 | M25 | M25 | 24.5 | B | 110VDC Charger 2
310 | D01 | L-110-CHG002-FB2 | 0.11DC | GCS-110-CHG-002 | 110-Fuse Box 2 | 7.5 | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | B | DC Charger Fuse Box 2
311 | D01 | L-110CH-FB2-BAT2 | 0.11DC | 110-Fuse Box 2 | 110-Battery Bank 2 | 7.5 | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | B | DC Charger Battery Bank 2
312 | D01 | L-110CH-F05 | 0.11DC | GCS-110-CHG-F05 | 3.3 KV New Switchgear | 0.7 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | To 3.3 KV New Switchgear
313 | D01 | L-110CH-F09 | 0.11DC | GCS-110-CHG-F09 | 0.4 KV New Switchgear A | 0.75 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | To 0.4 KV New Switchgear A & Coupler
314 | D01 | L-110CH-F10 | 0.11DC | GCS-110-CHG-F10 | 0.4 KV New Switchgear B | 0.75 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | To 0.4 KV New Switchgear B
315 | D01 | L-110CH-F11 | 0.11DC | GCS-110-CHG-F11 | 0.4 KV New Switchgear E | 0.7 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | To 0.4 KV New Switchgear E
316 | D01 | L-110CH-F12 | 0.11DC | GCS-110-CHG-F12 | RCP | 0.1 | 2×6 | 2C | 6 | - | - | 40 | M20 A | M20 A | 16.8 | B | To RCP
317 | D02 | L-NSWGA-24-CHG001 | 0.4 | GCS-400-NSWG-001A | GCS-24-CHG-001 | 16.2 | 3(2x(1x150)) | 1C | 150 | - | - | 50 | M50 | M50 | 45.5 | B | 24VDC Charger 1
318 | D02 | L-24-CHG001-FB1 | 0.024DC | GCS-24-CHG-001 | 24-Fuse Box 1 | 5.55 | 2x(1x185) | 1C | 185 | - | - | 20 | M50 | M50 | 50.5 | B | DC Charger Fuse Box 1
319 | D02 | L-24-FB1-BAT1 | 0.024DC | 24-Fuse Box 1 | 24-Battery Bank 1 | 5.55 | 2x(1x185) | 1C | 185 | - | - | 15 | M50 | M50 | 50.5 | B | DC Charger Battery Bank 1
320 | D02 | L-NSWGE-24-CHG002 | 0.4 | GCS-400-NSWG-001E | GCS-24-CHG-002 | 16.2 | 3(2x(1x150)) | 1C | 150 | - | - | 60 | M50 | M50 | 45.5 | B | 24VDC Charger 2
321 | D02 | L-24-CHG002-FB2 | 0.024DC | GCS-24-CHG-002 | 24-Fuse Box 2 | 5.55 | 2x(1x185) | 1C | 185 | - | - | 20 | M50 | M50 | 50.5 | B | DC Charger Fuse Box 2
322 | D02 | L-24-FB2-BAT2 | 0.024DC | 24-Fuse Box 2 | 24-Battery Bank 2 | 5.55 | 2x(1x185) | 1C | 185 | - | - | 15 | M50 | M50 | 50.5 | B | DC Charger Battery Bank 2
323 | D01 | L-24CH-F03 | 0.024DC | GCS-24-CHG-F03 | F&G System Panel | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G System Panel
324 | D01 | L-24CH-F04 | 0.024DC | GCS-24-CHG-F04 | F&G System Panel | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G System Panel (Redundant)
325 | D01 | L-24CH-F05 | 0.024DC | GCS-24-CHG-F05 | F&G Marshaling Panel 1 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G Marshaling Panel 1
326 | D01 | L-24CH-F06 | 0.024DC | GCS-24-CHG-F06 | F&G Marshaling Panel 1 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G System Panel 1 (Redundant)
327 | D01 | L-24CH-F07 | 0.024DC | GCS-24-CHG-F07 | F&G Marshaling Panel 2 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G Marshaling Panel 2
328 | D01 | L-24CH-F08 | 0.024DC | GCS-24-CHG-F08 | F&G Marshaling Panel 2 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G System Panel 2 (Redundant)
329 | D01 | L-24CH-F09 | 0.024DC | GCS-24-CHG-F09 | FACP | 0.9 | 2×50 | 2C | 50 | - | - | 30 | M32 | M32 | 30.2 | B | FACP
330 | D01 | L-24CH-F10 | 0.024DC | GCS-24-CHG-F10 | FACP | 0.9 | 2×50 | 2C | 50 | - | - | 30 | M32 | M32 | 30.2 | B | FACP (Redundant)
331 | D01 | L-24CH-F11 | 0.024DC | GCS-24-CHG-F11 | Fire Protection | 0.8 | 2×120 | 2C | 120 | - | - | 80 | M50 | M50 | 41 | B | Fire Protection & Total Flooding System UCP
332 | D01 | L-24CH-F12 | 0.024DC | GCS-24-CHG-F12 | Fire Protection | 0.8 | 2×120 | 2C | 120 | - | - | 80 | M50 | M50 | 41 | B | Fire Protection & Total Flooding System UCP (Redundant)
333 | D02 | L-NSWGB-110-UPS001 | 0.4 | GCS-400-NSWG-001B | GCS-110-UPS-001 | 43.41 | 3×70+35 | 4C | 70 | 35 | - | 45 | M40 | M40 | 41.6 | B | 110VAC UPS 1
334 | D01 | L-110-UPS001-FB1 | 0.11DC | GCS-110-UPS-001 | 110-Fuse Box 1 | 25 | 2×150 | 2C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | UPS Fuse Box 1
335 | D01 | L-110UPS-FB1-BAT1 | 0.11DC | 110-Fuse Box 1 | 110-Battery Bank 1 | 25 | 2×150 | 2C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | UPS Battery Bank 1
336 | D02 | L-NSWGA-110-UPS002 | 0.4 | GCS-400-NSWG-001E | GCS-110-UPS-002 | 43.41 | 3×70+35 | 4C | 70 | 35 | - | 55 | M40 | M40 | 41.6 | B | 110VAC UPS 2
337 | D01 | L-110-UPS002-FB2 | 0.11DC | GCS-110-UPS-001 | 110-Fuse Box 2 | 25 | 2×150 | 2C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | UPS Fuse Box 2
338 | D01 | L-110UPS-FB2-BAT2 | 0.11DC | 110-Fuse Box 2 | 110-Battery Bank 2 | 25 | 2×150 | 2C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | UPS Battery Bank 2
339 | D02 | L-NSWGE-UPS-Bypass | 0.4 | GCS-400-NSWG-001E | GCS-110-UPS-Bypass | 43.41 | 3×70+35 | 4C | 70 | 35 | - | 55 | M40 | M40 | 41.6 | B | 110VAC UPS By Pass
340 | D01 | L-110UPS-F03 | 0.11AC | GCS-110-UPS-F03 | DCS System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To Power Supply for CPUs
341 | D01 | L-110UPS-F04 | 0.11AC | GCS-110-UPS-F04 | DCS System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To Power Supply for CPUs (Redundant)
342 | D01 | L-110UPS-F05 | 0.11AC | GCS-110-UPS-F05 | DCS System Panel | 0.6 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply
343 | D01 | L-110UPS-F06 | 0.11AC | GCS-110-UPS-F06 | DCS System Panel | 0.6 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply (Redundant)
344 | D01 | L-110UPS-F07 | 0.11AC | GCS-110-UPS-F07 | DCS Marshaling Panel | 0.9 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply
345 | D01 | L-110UPS-F08 | 0.11AC | GCS-110-UPS-F08 | DCS Marshaling Panel | 0.9 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply (Redundant)
346 | D01 | L-110UPS-F09 | 0.11AC | GCS-110-UPS-F09 | ESD System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To Power Supply for CPUs
347 | D01 | L-110UPS-F10 | 0.11AC | GCS-110-UPS-F10 | ESD System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To Power Supply for CPUs (Redundant)
348 | D01 | L-110UPS-F11 | 0.11AC | GCS-110-UPS-F11 | ESD System Panel | 0.78 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply
349 | D01 | L-110UPS-F12 | 0.11AC | GCS-110-UPS-F12 | ESD System Panel | 0.78 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply (Redundant)
350 | D01 | L-110UPS-F13 | 0.11AC | GCS-110-UPS-F13 | ESD Marshaling Panel | 0.58 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply
351 | D01 | L-110UPS-F14 | 0.11AC | GCS-110-UPS-F14 | ESD Marshaling Panel | 0.58 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply (Redundant)
352 | D01 | L-110UPS-F15 | 0.11AC | GCS-110-UPS-F15 | Elecro Gas Compressor UCP A | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP A Ssystem & Marshaling
353 | D01 | L-110UPS-F16 | 0.11AC | GCS-110-UPS-F16 | Elecro Gas Compressor UCP A | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP A Ssystem & Marshaling (Redundant)
354 | D01 | L-110UPS-F17 | 0.11AC | GCS-110-UPS-F17 | Elecro Gas Compressor UCP B | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP B Ssystem & Marshaling
355 | D01 | L-110UPS-F18 | 0.11AC | GCS-110-UPS-F18 | Elecro Gas Compressor UCP B | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP B Ssystem & Marshaling (Redundant)
356 | D01 | L-110UPS-F19 | 0.11AC | GCS-110-UPS-F19 | Elecro Gas Compressor UCP C | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP C Ssystem & Marshaling
357 | D01 | L-110UPS-F20 | 0.11AC | GCS-110-UPS-F20 | Elecro Gas Compressor UCP C | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP C Ssystem & Marshaling (Redundant)
358 | D01 | L-110UPS-F21 | 0.11AC | GCS-110-UPS-F21 | Dehydration Package A (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Dehydration Package A LCP/Analyzer/BMS
359 | D01 | L-110UPS-F22 | 0.11AC | GCS-110-UPS-F22 | Dehydration Package A (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Dehydration Package A LCP/Analyzer/BMS (Redundant)
360 | D01 | L-110UPS-F23 | 0.11AC | GCS-110-UPS-F23 | Dehydration Package B (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Dehydration Package B LCP/Analyzer/BMS
361 | D01 | L-110UPS-F24 | 0.11AC | GCS-110-UPS-F24 | Dehydration Package B (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Dehydration Package B LCP/Analyzer/BMS (Redundant)
362 | D01 | L-110UPS-F25 | 0.11AC | GCS-110-UPS-F25 | Paging System | 1 | 3×4 | 3C | 4 | 4 | 4 | 35 | M20 A | M20 A | 16.6 | B | To Paging System
363 | D01 | L-110UPS-F26 | 0.11AC | GCS-110-UPS-F26 | Paging System | 1 | 3×4 | 3C | 4 | 4 | 4 | 35 | M20 A | M20 A | 16.6 | B | To Paging System (Redundant)
364 | D01 | L-110UPS-F27 | 0.11AC | GCS-110-UPS-F27 | Air Compressor A | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Air Compressor Local UCP A
365 | D01 | L-110UPS-F28 | 0.11AC | GCS-110-UPS-F28 | Air Compressor A | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Air Compressor Local UCP A (Redundant)
366 | D01 | L-110UPS-F29 | 0.11AC | GCS-110-UPS-F29 | Air Compressor B | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Air Compressor Local UCP B
367 | D01 | L-110UPS-F30 | 0.11AC | GCS-110-UPS-F30 | Air Compressor B | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Air Compressor Local UCP B (Redundant)
368 | D02 | L-110UPS-F31 | 0.11AC | GCS-110-UPS-F31 | Air Drayer A | 1.6 | 3×50+25+25 | 3C | 50 | 25 | 25 | 300 | M40 | M40 | 36.3 | B | Air Drayer A Local LCP
369 | D02 | L-110UPS-F32 | 0.11AC | GCS-110-UPS-F32 | Air Drayer A | 1.6 | 3×50+25+25 | 3C | 50 | 25 | 25 | 300 | M40 | M40 | 36.3 | B | Air Drayer A Local LCP (Redundant)
370 | D02 | L-110UPS-F33 | 0.11AC | GCS-110-UPS-F33 | Air Drayer B | 1.6 | 3×50+25+25 | 3C | 50 | 25 | 25 | 300 | M40 | M40 | 36.3 | B | Air Drayer B Local LCP
371 | D02 | L-110UPS-F34 | 0.11AC | GCS-110-UPS-F34 | Air Drayer B | 1.6 | 3×50+25+25 | 3C | 50 | 25 | 25 | 300 | M40 | M40 | 36.3 | B | Air Drayer B Local LCP (Redundant)
372 | D01 | L-110UPS-F35 | 0.11AC | GCS-110-UPS-F35 | Nitrogen Package | 1 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Nitrogen Package Local UCP A/B
373 | D01 | L-110UPS-F36 | 0.11AC | GCS-110-UPS-F36 | Nitrogen Package | 1 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Nitrogen Package Local UCP A/B (Redundant)
374 | D01 | L-110UPS-F37 | 0.11AC | GCS-110-UPS-F37 | Operator WorkStation | 2.964 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Operator WorkStation (Including DCS, ESD, Package)
375 | D01 | L-110UPS-F38 | 0.11AC | GCS-110-UPS-F38 | DCS Engineering Workstation | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | To DCS Engineering Workstation
376 | D01 | L-110UPS-F39 | 0.11AC | GCS-110-UPS-F39 | ESD Engineering Workstation | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | To ESD Engineering Workstation
377 | D01 | L-110UPS-F40 | 0.11AC | GCS-110-UPS-F40 | F&G Operator / Engineering | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | To F&G Operator / Engineering
378 | D01 | L-110UPS-F41 | 0.11AC | GCS-110-UPS-F41 | Printer A | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | To Operator / Engineering Printer A
379 | D01 | L-110UPS-F42 | 0.11AC | GCS-110-UPS-F42 | Printer B | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | To Operator / Engineering Printer B
380 | D01 | L-110UPS-F43 | 0.11AC | GCS-110-UPS-F43 | Printer C | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | To Operator / Engineering Printer C
381 | D02 | L-NSWGE-Non UPS | 0.4 | GCS-400-NSWG-001E | GCS-400-Non UPS | 19.2 | 4×25 | 4C | 25 | 25 | - | 60 | M25 | M25 | 26.4 | B | Non-UPS Load for Instrument
382 | D02 | L-Non UPS-F01 | 0.23 | GCS-400-Non UPS-F01 | F01 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For DCS A (Heater, Fan, Light)
383 | D02 | L-Non UPS-F02 | 0.23 | GCS-400-Non UPS-F02 | F02 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For DCS B (Heater, Fan, Light)
384 | D02 | L-Non UPS-F03 | 0.23 | GCS-400-Non UPS-F03 | F03 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For DCS C (Heater, Fan, Light)
385 | D02 | L-Non UPS-F04 | 0.23 | GCS-400-Non UPS-F04 | F04 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For DCS D (Heater, Fan, Light)
386 | D02 | L-Non UPS-F05 | 0.23 | GCS-400-Non UPS-F05 | F05 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For ESD A (Heater, Fan, Light)
387 | D02 | L-Non UPS-F06 | 0.23 | GCS-400-Non UPS-F06 | F06 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For ESD B (Heater, Fan, Light)
388 | D02 | L-Non UPS-F07 | 0.23 | GCS-400-Non UPS-F07 | F07 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For ESD C (Heater, Fan, Light)
389 | D02 | L-Non UPS-F08 | 0.23 | GCS-400-Non UPS-F08 | F08 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 25 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For F&G A (Heater, Fan, Light)
390 | D02 | L-Non UPS-F09 | 0.23 | GCS-400-Non UPS-F08 | F09 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 25 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For F&G B (Heater, Fan, Light)
391 | D02 | L-Non UPS-F10 | 0.23 | GCS-400-Non UPS-F08 | F10 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 25 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For F&G C (Heater, Fan, Light)
392 | D02 | L-Non UPS-F11 | 0.23 | GCS-400-Non UPS-F09 | F11 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Gas Compressor UCP A (Heater, Fan, Light)
393 | D02 | L-Non UPS-F12 | 0.23 | GCS-400-Non UPS-F09 | F12 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Gas Compressor UCP B (Heater, Fan, Light)
394 | D02 | L-Non UPS-F13 | 0.23 | GCS-400-Non UPS-F09 | F13 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Gas Compressor UCP C (Heater, Fan, Light)
395 | D02 | L-Non UPS-F14 | 0.23 | GCS-400-Non UPS-F10 | F14 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Dehydration BMS A ( if any) (Heater, Socket, Fan, Light)
396 | D02 | L-Non UPS-F15 | 0.23 | GCS-400-Non UPS-F10 | F15 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Dehydration BMS B ( if any) (Heater, Socket, Fan, Light)
397 | D02 | L-Non UPS-F16 | 0.23 | GCS-400-Non UPS-F11 | F16 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 75 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Total Flooding UCP(Heater, Socket, Fan, Light)
398 | D02 | L-Non UPS-F17 | 0.23 | GCS-400-Non UPS-F12 | F17 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Paging Cabinet (Heater, Socket, Fan, Light)
399 | D02 | L-Non UPS-F18 | 0.23 | GCS-400-Non UPS-F13 | F18 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Air Compressor UCP A (Heater, Socket, Fan, Light)
400 | D02 | L-Non UPS-F19 | 0.23 | GCS-400-Non UPS-F13 | F19 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Air Compressor UCP B (Heater, Socket, Fan, Light)
401 | D02 | L-Non UPS-F20 | 0.23 | GCS-400-Non UPS-F14 | F20 | 0.7 | 3×4 | 3C | 4 | 4 | 4 | 25 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Nitrogen package UCP(Heater, Socket, Fan, Light)
402 | D02 | L-Non UPS-F21 | 0.23 | GCS-400-Non UPS-F15 | F21 | 3.5 | 3×10 | 3C | 10 | 10 | 10 | 30 | M25 | M25 | 20.7 | B | Control Desk Sockets
403 | D02 | L-NSWGE-FDP 01 | 0.4 | GCS-400-NSWG-001E | GCS-230-FDP 01 | 1 | 4×4 | 4C | 4 | 4 | - | 210 | M20 A | M20 A | 17.7 | B | Fire Diesel Panel 01 (Electrical Main Motor)
404 | D02 | L-NSWGE-FDP 02 | 0.4 | GCS-400-NSWG-001E | GCS-230-FDP 02 | 1 | 4×4 | 4C | 4 | 4 | - | 210 | M20 A | M20 A | 17.7 | B | Fire Diesel Panel 02 (Diesel Engine)
405 | D02 | L-NSWGE-SPH-01 | 0.4 | GCS-400-NSWG-001E | SPH-01 | 2 | 4×4 | 4C | 4 | 4 | - | 20 | M20 A | M20 A | 17.7 | B | Space Heater & Lighting for New LV Switchgear
406 | D02 | L-NSWGE-SPH-02 | 0.4 | GCS-400-NSWG-001E | SPH-02 | 2 | 4×4 | 4C | 4 | 4 | - | 30 | M20 A | M20 A | 17.7 | B | Space Heater & Lighting for MV Switchgear
407 | D02 | L-NSWGE-EDP-CRM | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-CRM | 10 | 4×16 | 4C | 16 | 16 | - | 75 | M25 | M25 | 24.5 | B | Control Room Emergency Lighting Panel
408 | D02 | L-NSWGE-HVAC-CRM1 | 0.4 | GCS-400-NSWG-001E | GCS-400-HVAC-CRM1 | 97.9 | 3×240+120 | 3C | 240 | 120 | - | 75 | M90 | M90 | 78.4 | B | Control Room Emergency Distribution Panel for HVAC 1
409 | D02 | L-NSWGB-EDP-CRM2 | 0.4 | GCS-400-NSWG-001B | GCS-400-EDP-CRM2 | 97.9 | 3×240+120 | 3C | 240 | 120 | - | 75 | M90 | M90 | 78.4 | B | Control Room Emergency Distribution Panel for HVAC 2
410 | D02 | L-NSWGE-EDP-SWHVAC | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-SWHVAC | 30 | 3×50+25 | 3C | 50 | 25 | - | 75 | M40 | M40 | 42.2 | B | Switchgear Emergency Distribution Panel & HVAC
411 | D02 | L-NSWGE-EDP-WARE | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-WARE | 10.2 | 4×16 | 4C | 16 | 16 | - | 100 | M25 | M25 | 24.5 | B | Warehouse Emergency Distribution Panel & HVAC
412 | D02 | L-NSWGE-EHTC |  | GCS-400-NSWG-001E | EHTC | [11 empty] | Electrical Heat Tracing
413 | D02 | L-NSWGA-CAP-A-01 | 0.4 | GCS-400-NSWG-001A | CAP-01 | 120 | 3×185 | 3C | 185 | - | - | 35 | M63 | M63 | 56.9 | B | Cable 1 of LV Switchgear A Capacitor Bank
414 | D02 | L-NSWGA-CAP-A-02 | 0.4 | GCS-400-NSWG-001A | CAP-01 | 120 | 3×185 | 3C | 185 | - | - | 35 | M63 | M63 | 56.9 | B | Cable 2 of LV Switchgear A Capacitor Bank
415 | D01 | C-NSWGA-CAP-A |  | GCS-400-NSWG-001A | CAP-01 | - | 3×4 | 3C | - | - | - | 35 | M25 | M25 | 20 | E | Control Cable of LV Switchgear A Capacitor Bank
416 | D02 | L-NSWGA-CAP-B-01 | 0.4 | GCS-400-NSWG-001B | CAP-02 | 120 | 3×185 | 3C | 185 | - | - | 25 | M63 | M63 | 56.9 | B | Cable 1 of LV Switchgear B Capacitor Bank
417 | D02 | L-NSWGA-CAP-B-02 | 0.4 | GCS-400-NSWG-001B | CAP-02 | 120 | 3×185 | 3C | 185 | - | - | 25 | M63 | M63 | 56.9 | B | Cable 2 of LV Switchgear B Capacitor Bank
418 | D01 | C-NSWGA-CAP-B |  | GCS-400-NSWG-001B | CAP-02 | - | 3×4 | 3C | - | - | - | 25 | M25 | M25 | 20 | E | Control Cable of LV Switchgear A Capacitor Bank
419 | D02 | L-NSWGA-DG-001A1 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel
420 | D02 | L-NSWGA-DG-001A2 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel
421 | D02 | L-NSWGA-DG-001B1 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel
422 | D02 | L-NSWGA-DG-001B2 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel
423 | D02 | L-NSWGA-DG-001C1 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel
424 | D02 | L-NSWGA-DG-001C2 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel
425 | D02 | L-NSWGA-DG-001N1 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 400 | 1×300 | 1C | - | 300 | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel
426 | D02 | C-NSWGA-DG-001 | 0.11DC | GCS-400-NSWG-001E | GCS-DG-001 | - | 12×2.5 | 12C | 2.5 | - | - | 30 | M25 | M25 | 24.4 | E | To / From LV Switchgear
427 | D01 | M-11SWGA-CAP-1 | 11 | GCS-11-SWG-001A | Existing MV Capacitor Bank 1 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | From New Location of Existing Capacitor Bank1 to Existing MV Cell
428 | D01 | M-11SWGB-CAP-2 | 11 | GCS-11-SWG-001B | Existing MV Capacitor Bank 2 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | From New Location of Existing Capacitor Bank2 to Existing MV Cell
429 | D01 | M-11SWGB-CAP-3 | 11 | GCS-11-SWG-001B | Existing MV Capacitor Bank 3 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | From New Location of Existing Capacitor Bank3 to Existing MV Cell
430 | D02 | L-NSWGE-CCTV | 0.4 | GCS-400-NSWG-001E | CCTV Control Building | 21.69 | 3×95+50 | 3C | 95 | 50 | - | 200 | M63 | M63 | 53.8 | B | GCS CCTV Emergency Distribution Panel & HVAC

## Lighting
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | ROUT
|  |  |  | FROM | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D01 | L-NDP01F01-FLTJB34 | 0.4 | GCS-400-NDP-01/F01 | NEW FLT-34RST-JB | 8 | 5×10 | 5C | 10 | 10 | 10 | 340 | M25 | M25 | 28.3 | A | To Latest Flood Lighting Tower in The Line
2 | D02 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 100 | M20 A | M20 A | 15.3 | Z | From Tower JB to Terminal Box & Floodlight Fixtures
3 | D01 | L-NDP01F02-FLTJB5 | 0.4 | GCS-400-NDP-01/F02 | EXISTING FLT-5RST | 3.5 | 5×10 | 5C | 10 | 10 | 10 | 190 | M25 | M25 | 28.3 | A | To Latest Flood Lighting Tower in The Line
4 | D02 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 | M20 A | M20 A | 15.3 | Z | From Tower JB to Terminal Box & Floodlight Fixtures
5 | D01 | L-NDP02F01-FLTJB35 | 0.4 | GCS-400-NDP-02/F01 | NEW FLT-35RST | 4.5 | 5×10 | 5C | 10 | 10 | 10 | 210 | M25 | M25 | 22.3 | B | To Latest Flood Lighting Tower in The Line |  | شماره صفحه: 1 از 13
6 | D02 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 70 | M20 A | M20 A | 15.3 | Z | From Tower JB to Terminal Box & Floodlight Fixtures
7 | D01 | L-EDP02F01-JB | 0.23 | GCS-400-EDP-02/F01 | FLT-UT-F01-JB | 0.036 | 3×6 | 3C | 6 | 6 | 6 | 65 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
8 | D02 | - | 0.23 | FLT-UT-F01-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
9 | D01 | L-EDP02F02-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F02-JB | 0.018 | 3×6 | 3C | 6 | 6 | 6 | 170 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
10 | D02 | - | 0.23 | FLT-UT-F02-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 5 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
11 | D01 | L-EDP02F03-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F03-JB | 0.018 | 3×6 | 3C | 6 | 6 | 6 | 180 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
12 | D02 | - | 0.23 | FLT-UT-F03-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 5 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
13 | D01 | L-EDP02F04-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F04-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 30 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
14 | D02 | - | 0.23 | FLT-UT-F04-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
15 | D01 | L-EDP02F05-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F05-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 60 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
16 | D02 | - | 0.23 | FLT-UT-F05-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
17 | D01 | L-EDP01F01-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F01-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 220 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
18 | D02 | - | 0.23 | FLC-PR-F01-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
19 | D01 | L-EDP01F02-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F02-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 260 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
20 | D02 | - | 0.23 | FLC-PR-F02-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
21 | D01 | L-EDP01F03-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F03-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 290 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
22 | D02 | - | 0.23 | FLC-PR-F03-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
23 | D01 | L-EDP01F04-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F04-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 320 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
24 | D02 | - | 0.23 | FLC-PR-F04-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 75 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
25 | D01 | L-EDP01F05-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F05-JB | 0.144 | 3×6 | 3C | 6 | 6 | 6 | 230 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
26 | D02 | - | 0.23 | FLC-PR-F05-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 65 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
27 | D01 | L-EDP01F06-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F06-JB | 0.144 | 3×6 | 3C | 6 | 6 | 6 | 270 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
28 | D02 | - | 0.23 | FLC-PR-F06-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 65 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
29 | D01 | L-EDP01F07-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F07-JB | 0.18 | 3×6 | 3C | 6 | 6 | 6 | 320 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
30 | D02 | - | 0.23 | FLC-PR-F07-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 90 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
31 | D01 | L-EDP01F08-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F08-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 260 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
32 | D02 | - | 0.23 | FLC-PR-F08-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 130 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
33 | D01 | L-EDP01F09-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F09-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 100 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
34 | D02 | - | 0.23 | FLC-PR-F09-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 75 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
35 | D01 | L-EDP01F10-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F10-JB | 0.036 | 3×6 | 3C | 6 | 6 | 6 | 160 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
36 | D02 | - | 0.23 | FLC-PR-F10-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings