## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LI-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2487 |  |  | Transmital Date: 11/14/2023
Document Title: Electrical Power & Control Cable Schedule |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2487 |  |  | Transmital Date: 11/14/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-LI-0002_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as AFC after finalizing or minor comments on below prerequisite documents: -Electrical Load List -Electrical Equipment Arrangement Layout For Building -Calculation Note For Cable Sizing -Area Electrical Cable Route & Section Layout -Electrical Cable Route & Section Layout For Building & Shelter -Area Lighting & Small Power Layout -Specification For Power & Control Cables -Electrical I/O Signal List |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اعمال گردید. |  |  | See below item 21.
2 | Control cables shall be considered in a separated sheet. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | کابلهای مربوط به هر تجهیز اعم از قدرت و کنترل در کنار هم آورده شده است. |  |  | Noted and closed.
3 | According to our telephone conversation following cables shall be added to cable list: |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اعمال گردید.
3-1 | The new power MV cable between existing MV capacitor bank and existing MV switchgear |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اعمال گردید. |  |  | Noted and closed.
3-2 | The Power LV cable between generator and diesel generator control panel |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | با وندور ژنراتور می باشد. |  |  | Noted and closed.
3-3 | The Power LV cable between diesel generator control panel and LV switchgear |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | See below item 23.
3-4 | The Control cables between diesel generator and LV switchgear |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | See below item 23.
3-5 | The Power LV cable between LV switchgear and 230VAC UPS (For CCTV system) |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | See below item 24.
3-6 | The Power LV cable for 110VDC/24VDC/110VAC/230VAC UPS outgoing feeders |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | See below item 25.
3-7 | The Control cables between RCP and MV switchgear incomings, Coupling and outgoings |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | Noted and closed.
3-8 | The Control cables between DCS (IRP) and MV/LV switchgears incomings, Coupling and outgoing feeders, AC/DC UPS, diesel generator, transformer, etc. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | See below item 26.
3-9 | The Control cables for interlocks and intertrips |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | See below item 27.
3-10 | The Cables between LV switchgear and capacitor banks (Current sample). |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | Noted and closed.
3-11 | The Cables for differential protection CT |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | See below item 28.
3-12 | Space heater cable for motor |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | Noted and closed.
3-13 | Lighting cables (Especially outdoor area) |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | Noted and closed.
4 | Cable type shall be completely mentioned in cable list such as conductor type, inner and outer insulation (XPLE or PVC), armour, Screen, etc. in legend sheet. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید. |  |  | Noted and closed.
5 | Considered cable type in "cable type" column shall be totally rechecked and modified base on scope of work and project requirement for example the primary side of transformer and LV capacitor bank shall be armour type and lead cover for MV capacitor bank not required. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
6 | Cable type for compressor B, C and related capacitor bank have been mentioned "MAL3". This type has not been define in the legend |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
7 | According to telephone conversation, Control cables between MV/LV switchgear and IRP panel will be installed indoor (In cable gallery), so there is not need to lead cover and relevant cables type shall be modified in cable list (Only for process area shall be considered Lead Cover). |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
8 | Cables length shall be totally rechecked and modified for example according to latest revision of plot plan, fire water pump and jockey pump are near to each other but the cables length are different from each other or 110AC /24VDC will be installed in control room and it seems the related incoming cables shall be modified. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
9 | According to telephone conversation, maximum cable length has not been checked in this document, so it is recommended to checked maximum cable length in cable sizing document for long distance cables. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
10 | It shall be clarify lighting cable (For outgoing feeders of outdoor and indoor LP) will be considered in this document or not? |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
11 | Cable size of NGR shall be rechecked and modified. Meanwhile the size of RTD cable shall be added (10X3X1.5 or not?). |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
12 | According to cable list, all 11KV cables size (and without LC) except 800KVA transformer is 95mm². Therefore, in order to facilitate in purchasing process, it is recommended to change incoming cable size of 800KVA from 70mm² to 95mm². |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
13 | Incoming cable of LV capacitor banks shall be considered 4 core cable instead of 3 core cable. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
14 | According to scope of work and endorsement, Fire resistance cable shall be used instead of MICC cable where required. (It is necessary to considered in hazardous area such as battery room, LP flare package, etc. base on hazardous area classification layout. ) |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
15 | According to our telephone conversation, two separate row shall be considered for HVAC system power cable like as LV capacitor bank . |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | See below item 29.
16 | Type of gland (Ex or Non-Ex) shall be specified base on hazardous area classification layout. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
17 | Reference document for OD cables and gland size shall be attached to document and submitted in next revision to check OD cables and gland size. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | See below item 30.
18 | Tag number for all cables shall be the same according to cable tag numbering procedure in legend sheet. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
19 | Cable destination shall be rechecked and modified for example destination for cables to IRP shall be mentioned IRP instead of pump tag number. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
20 | Complementary comments will be submitted after receive prerequisite and revised documents. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید. |  |  | Noted and closed.
21 | See above item 1: This document shall be revised and issued as AFC after finalizing or minor comments on below prerequisite documents: -Electrical Load List (Based on latest vendors data, deleted HVAC/LP for control building, etc. Meanwhile there is conflict between this document and load list from point of the rated power view such as air compressor and nitrogen package. Moreover the substation HVAC situation has not been specified yet.) -Calculation Note For Diesel Generator Sizing (Based on latest vendors data, deleted HVAC/LP for control building, etc.) -Area Electrical Cable Route & Section Layout (Based on NISOC/PEDCO comments) -AC/DC UPS Sizing and SLD (Based on latest revision of instrument power consumption) -Calculation Note For Cathodic Protection System (Based on NISOC comments) -Calculation Note for Capacitor Banks (Based on NISOC) |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | در صورت هر گونه تغییر در مدارک پیش نیاز این مدر بروز رسانی خواهد گردید.
22 | control Cables between LCP and UCP have not seen in the cable schedule. If these cables will not be seen in the instrument cable schedule, to be added to this document |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | این کابل ها توسط بخش مربوطه در نظر گرفته خواهد شد.
23 | See above item 3-3&3-4: Has not been considered it shall be checked and added. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
24 | See above item 3-5: Shall be rechecked and sized based on rated power of charger not load consumption. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
25 | See above item 3-6: It shall be rechecked based on latest revision of instrument power consumption list and AC/DC UPS single line diagram for example 110VDC cables for 11KV switchgear has not been considered or number of feeders for 24VDC cables shall be compatible with instrument power consumption list. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید.
26 | See above item 3-8: Has not been considered. It shall be rechecked and modified based on latest revision of electrical I/O list for hardware and serial link cables. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | توسط بخش ابزاردقیق ارائه خواهد گردید
27 | See above item 3-9: The Control cables for interlocks and intertrips for both side of 800KVA transformer has not been considered. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
28 | See above item 3-11: The cable for 64REF has not been considered. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
29 | See above item 15: The substation HVAC feeder cables has not been considered. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
30 | See above item 17: The reference documents shall be submitted to check OD and gland size. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | با ارائه یک نوت در مدرک به مرجع کابل ( کابل ابهر ) و گلند ( ماشین سازی شمال ) اشاره گردید که این مراجع در دسترس عموم قراردارد
31 | Switchgear bus tag for emergency feeder shall be rechecked and modified based on latest revision of load list such as sump pump, closed drain pump, slug pump, fire water jockey pump, etc. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید.
32 | Electrical heat tracing cable size shall be added and specified in related row. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید.
33 | GCS-11-SWG-001C , GCS-11-SWG-001E and GCS-400-NSWG-001C shall be rechecked and modified in "from" column based on related feeders. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | اصلاح گردید.
34 | Type of glands shall be rechecked and modified for example the relevant cable glands in outdoor area for gas compressor and air cooler shall be considered EX. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
35 | Type of lighting cables between FLT-JB and Floodlight Fixtures, etc. (Cables type B) shall be rechecked based on latest revision of area lighting and small power layout. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
36 | Fire resistant cable description shall be completed in legend sheet. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
37 | for each one of compressor auxiliary loads, one ammeter have been considered but in the Havayar documents only one ammeter is required for main motor. |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | برای تمام AUX. ها کمپرسور نیز آمپرمتر لحاظ شده است .
38 | control cable number of core need to recheck in order to optimum design. For example as per issued schematic diagrams for LV switchgear, a 5x2.5sqmm cable is enough for air coolers LCS but in the cable schedule this cable has been considered 10x2.5sqmm. or a 12x2.5sqmm is enough for IRP-DCS&ESD cables but these cables have been considered 16x2.5. please recheck and clarify |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید.
39 | cable destination equipment tag number shall be mentioned. For example "LCS" is not acceptable in the equipment tag column |  | BK-SUR-ENG-ELE-02-08836 | 2023-11-27 | لحاظ گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: