## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 15
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0004 | D05
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR F&G SYSTEMS نگهداشت و افزایش تولید میدان نفتی بینک
D05 |  | NOV.2024 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Sadeghian
D04 |  | FEB.2024 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D03 |  | NOV.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number:F0Z-708970
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 15
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 |  | D05
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 | D05 | Page |  | D00 |  | D01 |  | D02 | D03 | D04 | D05
1 | X | X | X |  | X |  | X | X | 65
2 | X | X | X |  | X |  | X | X | 66
3 | X | X | [5 empty] | X | 67
4 | X | X | X |  | X |  | X | X | 68
5 | X | X | X |  | X |  | X | X | 69
6 | X | X | X |  | X |  | X | X | 70
7 | X | X | X |  | X |  | X | X | 71
8 | X | X | X |  | X |  | X | X | 72
9 |  | X | X |  | X |  | X | X | 73
10 |  | X | X |  | X |  | X | X | 74
11 |  | X | X |  | X |  | X | X | 75
12 |  | X | X |  | X |  | X | X | 76
13 |  | X | X |  | X |  | X | X | 77
14 |  | X | X |  | X |  | X | X | 78
15 |  |  | X |  | X |  |  | X | 79
16 |  |  | X |  | X |  |  |  | 80
17 |  |  | X |  | X |  |  |  | 81
18 |  |  | X |  | X |  |  |  | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 15
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0004 | D05
REFERENCES(NOTE 2):
| F&G LOCATION LAYOUT FOR PROCESS Area | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0005
| F&G LOCATION LAYOUT FOR BUILDINGS | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0006
| DATA SHEET FOR MATRIX PANEL | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017
| ESD LEVEL HIERARCHY | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003
| FIRE & GAS DETECTION DESIGN CRITERIA | [7 empty] | BK-GCS-PEDCO-120-IN-DC-0001
GENERAL NOTE
| 1 | ALL LISTED FACP'S SIGNALS SHALL BE MONITORED IN F&G SYSTEM BY MODBUS CONNECTION.
| 2 | REFER TO LATEST VERSION OF REFERENCE DOCUMENTS.
| 3 | ALL RELAYS & I.S. BARRIERS INSTALLED IN F&G PANEL SHALL BE SIL CERTIFIED. ALL RELAYS SHALL BE LINE-MONITORED
| 4 | GALVANIC ISOLATION BARRIER SHALL BE CONSIDERED FOR INTRINSICALLY SAFE (EEXia) LOOPS.
| 5 | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 15
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 | D05
F&G I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 87 |  | 104 | NOTES 4,5 | 104.4
| 2 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 61 |  | 74 | NOTES 4,5 | 73.2
| 3 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 119 |  | 135 | NOTES 4,5 | 142.8
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS: |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS: |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
|  | MAC: |  | MANUAL CALL POINT | [7 empty] | BR: | BLUE BEACON
|  | HN: |  | HORN | [7 empty] | BB: | RED BEACON
|  | LHD: |  | LINEAER HEAT DETECTOR | [7 empty] | FGD: | FLAMMABLE GAS DETECTOR
|  | SD: |  | SMOKE DETECTOR | [7 empty] | TGD: | TOXIC GAS DETECTOR
|  | BL: |  | BELL | [7 empty] | FD: | FLAME DETECTOR
|  | FACP: |  | FIRE ALARM CONTROL PANEL | [7 empty] | IRP: | INTERFACE RELAY PANEL
D05

## IO List for F&G System
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  |  | رشته |  | نوع مدرک | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO |  | 120 |  |  | IN |  | LI | 0004 |  |  | D05
SIGNALS TO F&G SYSTEM
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE |  | FROM |  | TO |  | JB NO. | POWER SUPPLY | Cable Type | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[17 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR PROCESS AREA
1 | MAC-1001 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
2 | MAC-1002 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
3 | HN-1001 | Horn | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
4 | BR-1001 | Beacon - Red | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
5 | BB-1001 | Beacon - Blue | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
6 | BY-1001 | Beacon - Yellow | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
7 | MAC-2001 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
8 | MAC-2002 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
9 | MAC-2003 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
10 | HN-2001 | Horn | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
11 | BR-2001 | Beacon - Red | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
12 | BB-2001 | Beacon - Blue | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
13 | BY-2001 | Beacon - Yellow | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
14 | MAC-3001 | Manual Call Point | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
15 | HN-3001 | Horn | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
16 | BR-3001 | Beacon - Red | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
17 | BB-3001 | Beacon - Blue | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
18 | BY-3001 | Beacon - Yellow | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
19 | MAC-4001 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
20 | MAC-4002 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
21 | HN-4001 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 OF 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
22 | BR-4001 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
23 | BB-4001 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
24 | BY-4001 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
25 | HN-4002 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
26 | BR-4002 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
27 | BB-4002 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
28 | BY-4002 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
29 | MAC-5001 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
30 | MAC-5002 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
31 | HN-5001 | Horn | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
32 | BR-5001 | Beacon - Red | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
33 | BB-5001 | Beacon - Blue | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
34 | BY-5001 | Beacon - Yellow | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
35 | MAC-6001 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
36 | MAC-6002 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
37 | HN-6001 | Horn | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
38 | BR-6001 | Beacon - Red | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
39 | BB-6001 | Beacon - Blue | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
40 | BY-6001 | Beacon - Yellow | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
41 | MAC-7001 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
42 | MAC-7002 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
43 | HN-7001 | Horn | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
44 | BR-7001 | Beacon - Red | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
45 | BB-7001 | Beacon - Blue | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
46 | BY-7001 | Beacon - Yellow | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
47 | MAC-8001 | Manual Call Point | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
48 | MAC-8002 | Manual Call Point | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
49 | MAC-8003 | Manual Call Point | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D05
50 | HN-8001 | Horn | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
51 | BR-8001 | Beacon - Red | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
52 | BB-8001 | Beacon - Blue | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
53 | BY-8001 | Beacon - Yellow | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
54 | MAC-9001 | Manual Call Point | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
55 | MAC-9002 | Manual Call Point | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | DELETED | D05
56 | HN-9001 | Horn | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
57 | BR-9001 | Beacon - Red | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
58 | BB-9001 | Beacon - Blue | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
59 | BY-9001 | Beacon - Yellow | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
60 | FGD-1001 | Flammable Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
61 | TGD-1001 | Toxic Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
62 | FD-2001 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
63 | FD-2002 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
64 | FD-2003 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
65 | FGD-2001 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
66 | FGD-2002 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
67 | FGD-2003 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
68 | FGD-2004 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
69 | TGD-2001 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
70 | TGD-2002 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
71 | TGD-2003 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
72 | TGD-2004 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
73 | FD-3001 | Flame Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
74 | FD-4001A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
75 | FD-4002A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
76 | FD-4003A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
77 | FD-4004A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
78 | FGD-4001A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
79 | FGD-4002A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
80 | FGD-4003A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
81 | FGD-4004A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
82 | TGD-4001A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
83 | TGD-4002A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
84 | TGD-4003A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
85 | TGD-4004A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
86 | FD-4001B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
87 | FD-4002B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
88 | FD-4003B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
89 | FD-4004B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
90 | FGD-4001B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
91 | FGD-4002B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
92 | FGD-4003B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
93 | FGD-4004B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
94 | TGD-4001B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
95 | TGD-4002B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
96 | TGD-4003B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
97 | TGD-4004B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
98 | FD-4001C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
99 | FD-4002C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
100 | FD-4003C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
101 | FD-4004C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
102 | FGD-4001C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
103 | FGD-4002C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
104 | FGD-4003C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
105 | FGD-4004C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
106 | TGD-4001C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
107 | TGD-4002C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
108 | TGD-4003C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
109 | TGD-4004C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
110 | FGD-5001A | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
111 | FGD-5001B | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
112 | FGD-5001C | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
113 | TGD-5001A | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
114 | TGD-5001B | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
115 | TGD-5001C | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
116 | FD-6001 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
117 | FD-6002 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T5 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
118 | FGD-6001 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T6 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
119 | FGD-6002 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T7 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
120 | FGD-6003 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T8 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
121 | TGD-6001 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T9 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
122 | TGD-6002 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T10 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
123 | TGD-6003 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T11 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
124 | LHD-7001 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
125 | LHD-7002 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
126 | FGD-7001 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
127 | FGD-7002 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
128 | FGD-7003 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
129 | TGD-7001 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
130 | TGD-7002 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
131 | TGD-7003 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
132 | FD-8001 | Flame Detector | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (11 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
133 | FD-8002 | Flame Detector | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (12 OF 12) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
134 | PT-2301 | Pressure Transmitter | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
135 | LSLL-2301 | Low Low Level Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(1/8) |  | Eexia Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
136 | LSLL-2302 | Low Low Level Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(1/8) |  | Eexia Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
FOR BUILDING
1 | FGD-1101 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D05
2 | FGD-1102 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
3 | FGD-1103 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
4 | TGD-1101 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
5 | TGD-1102 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
6 | TGD-1103 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
7 | FGD-1201 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
8 | FGD-1202 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
9 | FGD-1203 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
10 | TGD-1201 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
11 | TGD-1202 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
12 | TGD-1203 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
13 | HGD-1101 | Hydrogen Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexia 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
14 | HGD-1102 | Hydrogen Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexia 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D05
16 | HD-1101 | Heat Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
17 | HD-1102 | Heat Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
18 | MAC-1101 | Manual Call Point | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
SIGNALS BETWEEN F&G AND ESD SYSTEM & OTHER SYSTEMS
1 | ESDR0-FG-1101 | ESD 0 Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 12 PAIRx 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
2 | ESDR1A-FG-1101 | ESD 1A Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
3 | ESDR1A-FD-1101 | ESD 1A Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
4 | HVAC-FG-G-1101 | Control building HVAC shut down & damper closed for gas detection | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | HVAC |  | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D05
5 | HVAC-FG-F-1101 | Control building HVAC shut down & damper closed for fire detection | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | HVAC |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D05
6 | DAMP-FG-1101 | Battery Room Damper1 closed | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
7 | DAMP-FG-1102 | Battery Room Damper 2 closed | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP | Battery Room Fan | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
8 | DAMP-FG-G-1101 | Electrical building air intake damper closed for gas detection | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D05
9 | FAN-FG-1101 | Battery Room stand by Fan Activation Command | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
10 | FAN-FG-1102 | Battery Room Standby Fan Activation | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | DELETED | D05
11 | INB-FG-1101 | Inhibit to Boost for UPS Charger 1 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC | 19 PAIRx 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
12 | INB-FG-1102 | Inhibit to Boost for UPS Charger 2 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D05
13 | INB-FG-1103 | Inhibit to Boost for UPS Charger 3 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D05
14 | PISO-FG-1101 | Power Isolation of Battery Bank 1 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D05
15 | PISO-FG-1102 | Power Isolation of Battery Bank 2 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D05
16 | PISO-FG-1103 | Power Isolation of Battery Bank 3 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D05
17 | EXT-FG-1101 | Extinguishing System Activation | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | DELETED | D05
18 | TOT-FG-1101 | Total Flooding System Activation | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | DELETED | D05
19 | Ex-FG-G-1101 | F&G System confirmed Gas Alarm to Existing F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Existing F&G |  | - | - | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | to be finalized based on existing f&g system | D05
20 | Ex-FG-F-1101 | F&G System confirmed Fire Alarm to Existing F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Existing F&G |  | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
21 | Ex-FG-G-1102 | Existing F&G System confirmed Gas Alarm to F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DI-NIS-R |  | Existing F&G |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
22 | Ex-FG-F-1102 | Existing F&G System confirmed Fire Alarm to F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DI-NIS-R |  | Existing F&G |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
23 | HSS-2301A | Pump Start Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | IRP | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
24 | XR-2301A | Pump Running/ Stopped Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
25 | XF-2301A | Pump Fault Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
26 | PAL-2301 | Low Pressure Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | Battery Room Fan | IRP | FGS | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
27 | XM-2301A | Pump Auto/Manual Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS | - |  |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
28 | HSS-2301B | Pump Start Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2301B | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
29 | XM-2301B | PumpAuto/ Manual Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
30 | XR-2301B | Pump Running/ Stopped Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
31 | XF-2301B | Pump Fault Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
32 | PAL-2301B | Low Pressure Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
33 | HSS-2302A | Pump Start Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302A | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
34 | XM-2302A | PumpAuto/ Manual Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
35 | XR-2302A | Pump Running/ Stopped Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
36 | XF-2302A | Pump Fault Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
37 | PALL-2302A | Low Low Pressure Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
38 | HSS-2302B | Pump Start Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302B | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
39 | XM-2302B | PumpAuto/ Manual Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
40 | XR-2302B | Pump Running/ Stopped Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
41 | XF-2302B | Pump Fault Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
42 | PALL-2302B | Low Low Pressure Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
43 | XA-CO2-1101 | MANUAL/AUTO SELECTOR SWITCH STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS | - | - | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
44 | XRE-CO2-1101 | RELEASED STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
45 | XI-CO2-1101 | INHIBIT STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
46 | XF-CO2-1101 | GENERAL FAULT | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
47 | HS-CO2-1101 | AUTOMAT RELEASE COMMAND (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DO-NIS-R |  | FGS | FGS | CO2 Control Panel |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
48 | PSH-2302 | Valve Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2302 |  | FGS | FGS | - | - | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
49 | DSOV-2302 | Valve Open Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2302 |  | - | 24 VDC | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
50 | PSH-2303 | Valve Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2303 |  | FGS | FGS | - | - | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
51 | DSOV-2303 | Valve Open Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2303 |  | - | 24 VDC | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
52 | PSH-2304 | Valve Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2304 |  | FGS | FGS | - | - | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
53 | DSOV-2304 | Valve Open Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2304 |  | - | 24 VDC | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
54 | PSH-2301 | Valve Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2305 |  | FGS | FGS | - | - | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
55 | DSOV-2301 | Valve Open Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2305 |  | - | 24 VDC | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
SIGNALS TO F&G Matrix PANEL
1 | LP-AR1-FD | Fire Alarm For Area 1 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 19 PAIR x 1 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | low frequency pulse for prealarm and high frequency pulse for alarm | D05
2 | LP-AR1-FGD | Flammable Gas Alarm For Area 1 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
3 | LP-AR1-TGD | Toxic Gas Alarm For Area 1 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
4 | LP-AR2-FD | Fire Alarm For Area 2 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
5 | LP-AR2-FGD | FlammableGas Alarm For Area 2 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
6 | LP-AR2-TGD | Toxic Gas Alarm For Area 2 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
7 | LP-AR3-FD | Fire Alarm For Area 3 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
8 | LP-AR4A-FD | Fire Alarm For Area 4A Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
9 | LP-AR4A-FGD | FlammableGas Alarm For Area 4 A Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
10 | LP-AR4A-TGD | Toxic Gas Alarm For Area 4A Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
11 | LP-AR4B-FD | Fire Alarm For Area 4B Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
12 | LP-AR4B-FGD | FlammableGas Alarm For Area 4 B Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
13 | LP-AR4B-TGD | Toxic Gas Alarm For Area 4B Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
14 | LP-AR4C-FD | Fire Alarm For Area 4C Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
15 | LP-AR4C-FGD | FlammableGas Alarm For Area 4C Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
16 | LP-AR4C-TGD | Toxic Gas Alarm For Area 4C Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
17 | LP-AR5-FD | Fire Alarm For Area 5 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 19 PAIR x 1 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
18 | LP-AR5-FGD | FlammableGas Alarm For Area 5 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
19 | LP-AR5-TGD | Toxic Gas Alarm For Area 5 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
20 | LP-AR6-FD | Fire Alarm For Area 6 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
21 | LP-AR6-FGD | FlammableGas Alarm For Area 6 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
22 | LP-AR6-TGD | Toxic Gas Alarm For Area 6 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
23 | LP-AR7-FD | Fire Alarm For Area 7 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
24 | LP-AR7-FGD | FlammableGas Alarm For Area 7 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
25 | LP-AR7-TGD | Toxic Gas Alarm For Area 7 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
26 | LP-AR8-FD | Fire Alarm For Area 8 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
27 | LP-AR9-FD | Fire Alarm For Area 9 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
28 | LP-CB-FD | Fire Alarm For Control Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
29 | LP-CB-FGD | FlammableGas Alarm For Control Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
30 | LP-CB-TGD | Toxic Gas Alarm For Control Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
31 | LP-EB-FD | Fire Alarm For Electrical Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
32 | LP-EB-FGD | FlammableGas Alarm For Electrical Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
33 | LP-EB-TGD | Toxic Gas Alarm For Electrical Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 19 PAIR x 1 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
34 | LP-PSH-2302 | Deluge Valve 2302 Opened Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
35 | LP-PSH-2303 | Deluge Valve 2303 Opened Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
36 | LP-PSH-2304 | Deluge Valve 2304 Opened Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
37 | LP-PSH-2301 | Deluge Valve 2301 Opened Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
38 | LP-P-2301B | Diesel Pump Status Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
39 | LP-P-2301A | Electrical Pump Status Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
40 | LP-CO2-RE | CO2 Release Status Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
41 | PB-DV-2302 | Deluge Valve 2302 Open Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
42 | PB-DV-2303 | Deluge Valve 2303 Open Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
43 | PB-DV-2304 | Deluge Valve 2304 Open Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
44 | PB-DV-2301 | Deluge Valve 2301 Open Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
45 | PB-P-2301B | Diesel Pump Start Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
46 | PB-P-2301A | Electrical Pump Start Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
47 | PB-CO2-CO | CO2 Release Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
48 | PB-RST | RESET Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
49 | PB-ACK-HO | ACK HORN Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - | 19 PAIR x 1 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
50 | PB-ACK | ACK Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D05
51 | PB-INHIBIT | Inhibit to maitenance Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D05
52 | LP-INHIBIT | Inhibit to maitenance Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D05
53 | BUZZER | Audible Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05
D05

## IO List for FACP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO | 120 |  | IN | LI | 0004 | D05
SIGNALS TO FACP
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE | FROM | TO |  | POWER SUPPLY | Cable Type | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[14 empty] | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR BUILDING
FACP LOOP 1
1 | FACP | Output Port of Loop 1 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | MAC-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
2 | MAC-1102 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | MAC-1102 | SD-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
3 | SD-1104 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1104 | SD-1108 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
4 | SD-1103 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1103 | SD-1110 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
5 | MAC-1103 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | MAC-1103 | MAC-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
6 | SD-1102 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1102 | SD-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
7 | SD-1101 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1101 | MAC-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
8 | SD-1121 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1121 | SD-1122 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
9 | SD-1122 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1122 | SD-1123 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
10 | SD-1123 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1123 | SD-1124 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
11 | SD-1124 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1124 | SD-1112 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
12 | SD-1135 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1135 | SD-1136 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
13 | SD-1136 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1136 | SD-1115 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
14 | SD-1128 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1128 | MAC-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
15 | SD-1126 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1126 | BL-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
16 | SD-1108 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1108 | SD-1110 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
17 | SD-1110 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1110 | SD-1112 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
18 | SD-1112 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1112 | SD-1114 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
19 | SD-1114 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1114 | SD-1115 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
20 | SD-1115 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1115 | MAC-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
21 | MAC-1104 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | MAC-1104 | BL-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
22 | BL-1101 | Bell | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BL-1101 | BR-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
23 | BR-1103 | Beacon - Red | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BR-1103 | MAC-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
24 | MAC-1105 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | MAC-1105 | SD-1118 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
25 | SD-1118 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1118 | SD-1120 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
26 | SD-1120 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1120 | HN-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
27 | HN-1101 | Horn | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | HN-1101 | BR-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
28 | BR-1101 | Beacon - Red | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BR-1101 | BB-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
29 | BB-1101 | Beacon - Blue | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BB-1101 | BY-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
30 | BY-1101 | Beacon - Yellow | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BY-1101 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
FACP LOOP 2
1 | FACP | Output Port of Loop 2 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
2 | SD-1105 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1105 | SD-1127 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
3 | SD-1106 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1106 | SD-1130 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
4 | SD-1130 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1130 | SD-1131 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
5 | SD-1131 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1131 | SD-1132 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
6 | SD-1132 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1132 | SD-1129 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
7 | SD-1129 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1129 | SD-1134 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
8 | SD-1134 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1134 | SD-1133 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
9 | SD-1133 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1133 | SD-1128 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
10 | SD-1128 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1128 | SD-1127 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
11 | SD-1127 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1127 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
FACP LOOP 3
1 | FACP | Output Port of Loop 3 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1107 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
2 | SD-1107 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1107 | SD-1109 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
3 | SD-1109 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1109 | SD-1111 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
4 | SD-1111 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1111 | SD-1113 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
5 | SD-1113 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1113 | SD-1116 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
6 | SD-1116 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1116 | SD-1117 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
7 | SD-1117 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1117 | SD-1119 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
8 | SD-1119 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1119 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
FACP LOOP 4
1 | FACP | Output Port of Loop 4 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | HN-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
2 | HN-1201 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | HN-1201 | BR-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
3 | BR-1201 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | BR-1201 | BB-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
4 | BB-1201 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | BB-1201 | BY-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
5 | BY-1201 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | BY-1201 | MAC-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
6 | MAC-1201 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | MAC-1201 | SD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
7 | SD-1201 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | SD-1201 | SD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
8 | SD-1202 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | SD-1202 | MAC-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
9 | MAC-1202 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | MAC-1202 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
FACP LOOP 5
1 | FACP | Output Port of Loop 5 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
2 | SD-1203 | Smoke Detector | Extension of Existing Elect. Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1203 | SD-1204 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
3 | SD-1204 | Smoke Detector | Extension of Existing Elect. Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | SD-1204 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
FACP LOOP 6
1 | FACP | Output Port of Loop 6 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | HN-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
2 | HN-1202 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | HN-1202 | BR-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
3 | BR-1202 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | BR-1202 | BB-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
4 | BB-1202 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | BB-1202 | BY-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
5 | BY-1202 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | BY-1202 | MAC-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
6 | MAC-1203 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | MAC-1203 | LHD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
7 | LHD-1201 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | LHD-1201 | LHD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
8 | LHD-1202 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | LHD-1202 | LHD-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
9 | LHD-1203 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | LHD-1203 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
FACP LOOP 7
1 | FACP | Output Port of Loop 7 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
2 | SD-1301 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | SD-1301 | SD-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
3 | SD-1302 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | SD-1302 | MAC-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
4 | MAC-1302 | Manual Call Point | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | MAC-1302 | SD-1304 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
5 | SD-1304 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | SD-1304 | SD-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
6 | SD-1303 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | SD-1303 | HD-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
7 | HD-1301 | Heat Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | HD-1301 | MAC-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
8 | MAC-1301 | Manual Call Point | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | MAC-1301 | HN-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
9 | HN-1301 | Horn | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | HN-1301 | BR-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
10 | BR-1301 | Beacon - Red | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | BR-1301 | BB-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
11 | BB-1301 | Beacon - Blue | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | BB-1301 | BY-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
12 | BY-1301 | Beacon - Yellow | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | BY-1301 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
FACP LOOP 8
1 | FACP | Output Port of Loop 8 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
2 | SD-1401 | Smoke Detector | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | SD-1401 | SD-1402 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
3 | SD-1402 | Smoke Detector | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | SD-1402 | SD-1403 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
4 | SD-1403 | Smoke Detector | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | SD-1403 | MAC-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
5 | MAC-1401 | Manual Call Point | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | MAC-1401 | HN-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
6 | HN-1401 | Horn | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | HN-1401 | BR-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
7 | BR-1401 | Beacon - Red | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | BR-1401 | BB-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
8 | BB-1401 | Beacon - Blue | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | BB-1401 | BY-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
9 | BY-1401 | Beacon - Yellow | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | BY-1401 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D05
Notes:
1- Non-IS Detector is on the Loop. Level of Alarm is N.A. for such Loop-powered.
D05