| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Design Criteria | Vendor To confirm That All supplied material all in full compliance with Project site condition: - Min/Max air temperature = 0°C / 52°C - Relative humidity = 100% max at 52°C - Altitude = 12 m a.s.l. - Climate = Class 4 (Very High) | Confirmed. Creepage distance is 40mm/kV. | Closed. |  |  |  |
|  | Documents Priority | All The equipment’s shall be engineered, designed, manufactured, tested and installed in accordance with the following standards: - Local Codes & Standards - Iranian Petroleum Standard (IPS) - International Codes & Standards - IEC (International Electro technical Commission) - BS (British Standard) - IEEE (Institute of Electrical and Electronics Engineers) - API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards and codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes and Standards. 4-Vendor Proposal. | All The equipment’s will be engineered, designed, manufactured, tested and installed accordance with the IEC60076 & IPS standards. | Closed. |  |  |  |
|  | Scope of Supply | Minimum Scope of work and supply are in full compliance with Project MR (BK-GCS-PEDCO-120-EL-MR-0001). It has been Listed but not Limited to the following Items: - Full Engineering Services. - Two sets 11/0.42 KV, Hermetically Sealed (1250KVA - One set 11/3.45 KV, Hermetically Sealed (800KVA) - Inspection & Test ACC to ITP/QCP - Site Supervisory Servicers (Optional) | Confirmed. | Closed. |  |  |  |
|  | Deviation List | Technical requirements shall be according to project specification in as minimum except those clearly specified in “deviation form”. BK-GNRAL-PEDCO-000-EL-DC-0001 (Electrical System Design Criteria) BK-GNRAL-PEDCO-000-EL-SP-0004 (Specification for Transformers) | “BK-GNRAL-PEDCO-000-EL-DC-0001 (Electrical System Design Criteria)” had not been received. | Send again. | Submitted. | Closed. |  |
|  | General | Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR, TCL and codes & standards referred in the documents by issuing a New Deviation/Exception List With the respect to latest Modification and revised technical offer for purchaser's review and approval. Otherwise, the vendor must declare full compliance between all documents attached to the Inquiry package. | Deviation form had been submitted. | Project format Shall be Shall be fill Out and Stamp and return to purchaser. Documents attached to the MR. (project format attachment 3 page 13) | Submitted. | Closed. |  |
|  | General | Project Datasheet & TBE Table Shall be fill Out and return to purchaser. | Confirmed. | Project Datasheet Shall be fill Out and stamp and return to purchaser. | Submitted. | Closed. |  |
|  | Scope of Supply | Transformer 800 KVA is 11/3.45 KV. This item will be revised in next revision of data sheet. | Confirmed. | Closed. |  |  |  |
|  | Cables for 1250KVA transformer | - 11 kV Cables Size & Number: 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - 0.42 kV Cable Size & Number 14x(1x300), (CU/XLPE/Bd/AWA/PVC) - Type & Size of Power Cable Glands Primary: M90 Secondary: M40 - Type & Size of Cable Glands (Control Cable) 12x2.5, (CU/PVC/SWA/PVC), M25 - Undrilled Non Magnetic Gland Plated shall be provided. | Confirmed. Cable Gland is purchaser Scope of work. | Closed. |  |  |  |
|  | Cables for 800KVA transformer | - 11 kV Cables Size & Number: 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - 3.45 kV Cable Size & Number 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - Type & Size of Power Cable Glands Primary: M90 Secondary: M75 - Type & Size of Cable Glands (Control Cable) 12x2.5, (CU/PVC/SWA/PVC), M25 - Undrilled Non Magnetic Gland Plated shall be provided. | Confirmed Cable Gland is purchaser Scope of work. | Closed. |  |  |  |
|  | CT for Transformers NISOC_TR-2779 | - Below CTs shall be Considered by Vendor on 1250 KVA Transformer: 2000/1A, 5P10 ,10VA - Below CTs shall be Considered by Vendor on 800 KVA Transformer: 630/1A, 5P10 ,10VA *Note: It is Preliminary and will be final by Switchgear Manufacturer. | Confirmed for conventional size of CTs. | با توجه به اینکه نقطه نوترال ترانس -11/3.3KV 800KVAتوسط NGR زمین شده است بایستی برای حفاظت 51G یک عدد ترانس جریان با مشخصات 100/1A – 5P20 – 15VA و برای حفاظت 64REF یک عدد ترانس مجاز دیگر با مشخصات 100/1A – CL:X – VK: 250V ~ 300V لحاظ گردد ( لازم بذکر است ولتاژ نقطه زانویی پس از قرارداد نهایی خواهد شد( و جهت ترانسفورماتور 11/0.42KV – 1250KVA یک عدد ترانس جریان 2000/1A – 5P20 – 15VA بایستی در نظر گرفته شود . همچنین ترانس های جریان در جعبه کابل قرار میگیرد . | Confirmed. | Closed. |  |
|  | Power Cable Gland | All Required Power Cable Glands & Plugs are in purchaser Scope of work and is ISO metric threaded in accordance with IEC60423. It should be Noted that Gland for Power Cables will be supplied by purchaser. | Confirmed. | Closed. |  |  |  |
|  | Vendor List | Vendor list & sub vendor list of manufacture shall be according to project AVL. Sub-vendor List for Electrical Equipment shall be submitted for review and approval in bid stage. | Sub vendor list is submitted, please review it. | Closed. |  |  |  |
|  | Spare Part | Spare Part for Commissioning and 2 Years Operation shall be Covered all requirement in Project Specification. | Confirmed. | Closed. |  |  |  |
|  | Special Tools | Any Special Tools for Life time Operation shall be included in technical offer. | N.A for distribution transformers. | Closed. |  |  |  |
|  | Specification | Vendor shall submit the reference and experience list (as a separate file) for design & manufacturing of power transformer. | Submitted. | Closed. |  |  |  |
|  | Shipment | Vendor shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification. | Confirmed. | Closed. |  |  |  |
|  | Arrangement | Transformer Outline Drawing shall be completed and LV/MV boxes shall be shown in top view for arrangement in shelter. | Detailed outline drawings will be submitted after P.O. | Not Acceptable Vendor shall prepare preliminary shown in top view for arrangement in shelter in this stage | The location of the cable boxes is shown in the top view on the Outline drawings. | Closed. |  |
|  | Temperature de‐Rating Factors | Vendor shall submitted temperature de‐rating factors of equipment. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated current be equal or higher than rated current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. | Confirmed. Derating curves will be submitted after P.O. | Not Acceptable Vendor shall be followed client requirement. | temperature Derating formula is submitted. | Closed. |  |
|  | ITP & Test Report | Certificate or license, Test reports and type test shall be submitted based on latest revision of IEC 60076. | Sample type tests had been submitted. | Closed. |  |  |  |
|  | As Built | As built documents and drawings are in vendor scope of work. | Confirmed. | Closed. |  |  |  |
|  | NISOC_TR-2779 | ترجیحا روغن مینرال و بدون افزودنی ترانسها از شرکت NYNAS(NYTRO LIBRA) تامین گردد. با توجه به عدم استفاده و اطلاع از کیفیت روغن مینرال شرکت ERAM SHIMI جهت ترانسها ، این شرکت مورد تایید نیست . | با عنایت به تبعات مالی و زمانی زیاد در حال حاضر امکان تامین روغن از برند Nynas میسر نمی باشد. برند Eram shimi از Sub vendor list حذف گردید. | Closed. |  |  |  |
|  | NISOC_TR-2779 | ترجیحاً ورق هسته ها از شرکت های اروپای غربی تامین گردد . | در این مورد، تغییر در Sub vendor list امکان پذیر نمی باشد. | Closed. |  |  |  |
|  | NISOC_TR-2779 | حفاظتهای مکانیکی ترانس که باعث تریپ می شوند می بایست با کنتاکت FAIL SAFE در نظر گرفته شوند . | Confirmed. | Closed. |  |  |  |
|  | NISOC_TR-2779 | به جهت تسهیل در تعویض بوشینگهای ترانس ، لازم است ، بوشینگهای اولیه و ثانویه بر روی کاور بالای مخزن ترانس و یا در بالاترین نقطه از دیواره مخزن نصب گردند. بر این اساس می بایست DRAWINGها ، اصلاح و جهت بررسی ارسال گردند . صرفا شرکت ایران ترانسفو بوشینگها را در بالاترین نقطه از دیواره مخزن نصب نموده است ، در صورت امکان مطابق با ترانسهای موجود بوشینگها در بالای کاور نصب گردند. | با عنایت به نوع ترانسفورماتور های درخواستی (هرمتیک گازی) و با توجه به به تزریق گاز نیترژن یا ازت به بالای مخزن ترانسفورماتور ، امکان قرارگیری بوشینگ ها بر روی کاور میسر نیست. | در لیست مغایرت پروژه ارایه گردد تا نقطه نظر کارفرمای اصلی پروژه اخذ گردد. | امکان قرارگیری بوشینگ ها بر روی کاور میسر نیست. شایان ذکر است مطابق نقشه های ابعادی بوشینگ ها در بالاترین نقطه دیواره های جانبی نصب شده اند. | Closed. |  |
|  | NISOC_TR-2779 | در خصوص امپدانس درصد ترانس ها، پس از نهایی شدن مطالعات شبکه اظهارنظر خواهد شد. | با توجه به موثر بودن امپدانس درصد ترانسفورماتور ها در طرح فنی نهایی، تغییر آن تا قبل از تایید نقشه های ساخت مورد تایید است. همچنین تبعات مالی احتمالی ناشی از تغییر امپدانس درصد نیز اعلام خواهد شد. | Closed. |  |  |  |
|  | NISOC_TR-2779 | با توجه به پاسخ پیمانکار در صورتیکه کلیه شیرهای روغن ( تزریق / تخلیه / نمونه گیری ) و همچنین TAP CHANGER مجهز به قفل و یا با ابزار مخصوص باز و بسته باشند ، نظر خاصی نیست . | مورد تایید است. | Closed. |  |  |  |
|  | NISOC_TR-2779 | با توجه به اینکه رله SUDDEN PRESSURE جهت کلیه ترانسها در نظر و در نقشه OUTLINE DRAWING نمایش داده شده است ، نظری در این خصوص مطرح نیست . | مطابق استاندارد IPS ، رله SUDDEN PRESSURE برای ترانسفورماتورهای با توان بالاتر از 1250KVA می بایست در نظر گرفته شود . لذا رله مذکور در ترانسفورماتور های موضوع استعلام لحاظ نشده است. | Not Acceptable Vendor shall be followed client requirement. | Sudden Pressure relay is considered. | Closed. |  |
|  | NISOC_TR-2779 | نمایشگر سطح روغن می بایست دارای کنتاکت آلارم باشد . | کنتاکتهای فوق لحاظ گردید. | Closed. |  |  |  |
|  | NISOC_TR-2779 | GAS PRESSURE & VACUUM INDICATOR می بایست دارای کنتاکت آلارم باشد (نظر شرکت آریا ترانسفو در این خصوص پذیرفته نیست). | GAS PRESSURE & VACUUM INDICATOR فاقد کنتاکت می باشد. | با توجه به نظر کارفرما ترجیحاًGAS PRESSURE & VACUUM INDICATOR می بایست دارای کنتاکت آلارم باشد که امکان ارایه مورد بالا نمیباشد در لیست مغایرت پروژه ارایه گردد تا نقطه نظر کارفرمای اصلی پروژه اخذ گردد. | در لیست مغایرت ذکر شده است. | Closed. |  |
|  | NISOC_TR-2779 | با توجه به نظر سازندگان مبنی بر اصلاح مدرک OUTLINE DRAWING با لحاظ و نمایش کلیه جزئیات و تجهیزات ترانس ها بعد از عقد قرارداد ( AFTER PO ) به اطلاع می رساند که این مدرک پس از انتخاب سازنده و ارسال مدرک اصلاح شده ، بررسی خواهد شد. | مورد تایید است. | Closed. |  |  |  |
|  | NISOC_TR-2779 | مدرک ITP سازنده منتخب ترانسفورماتورها در مرحله PIM بررسی و نهایی خواهد شد. | مورد تایید است. | Closed. |  |  |  |
|  | Deviation list | فرمت لیست مغایرت ارایه شده مورد تایید نمیباشد و فرمت لیست مغایرت پروژه که در مدرک MR (صفحه 13 از 15) قرار دارد بایستی تکمیل و ممهور گردد. | Confirmed. | Closed. |  |  |  |
|  | Data sheet | Latest revision of project documents such as data sheet shall be completed by vendor and submitted again. | Submitted. | Closed. |  |  |  |