| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Design Criteria | Vendor To confirm That All supplied material all in full compliance with Project site condition : - Min/Max air temperature = 0°C / 52°C - Relative humidity = 100% max at 52°C - Altitude = 12 m a.s.l. - Climate = Class 4 (Very High) | confirmed | Closed. |  |  |  |  |
|  | Documents Priority | All The equipment’s shall be engineered, designed, manufactured, tested and installed in accordance with the following standards: - Local Codes & Standards - Iranian Petroleum Standard (IPS) - International Codes & Standards - IEC (International Electro technical Commission) - BS (British Standard) - IEEE (Institute of Electrical and Electronics Engineers) - API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards and codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes and Standards. 4-vendor proposal | confirmed | Closed. |  |  |  |  |
|  | Scope of Supply | Minimum Scope of work and supply are in full compliance with Project MR (BK-GCS-PEDCO-120-EL-MR-0001). It has been Listed but not Limited to the following Items: - Full Engineering Services. - Two sets 11/0.42 KV, Hermetically Sealed (1250KVA - One set 11/3.45 KV, Hermetically Sealed (800KVA) - Inspection & Test ACC to ITP/QCP - Site Supervisory Servicers (Optional) | 1- Acc to contract 2-Ok 3-Ok 4- Acc to ITP of IRAN TRANSFO 5- Acc to contract | Closed. |  |  |  |  |
|  | Deviation List | Technical requirements shall be according to project specification in as minimum except those clearly specified in “deviation form”. BK-GNRAL-PEDCO-000-EL-DC-0001 (Electrical System Design Criteria) BK-GNRAL-PEDCO-000-EL-SP-0004 (Specification for Transformers) | Deviation list is attached. | Closed. |  |  |  |  |
|  | General | Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR, TCL and codes & standards referred in the documents by issuing a New Deviation/Exception List With the respect to latest Modification and revised technical offer for purchaser's review and approval. Otherwise, the vendor must declare full compliance between all documents attached to the Inquiry package. | Deviation list is attached. | Closed. |  |  |  |  |
|  | General | Project Datasheet & TBE Table Shall be fill Out and return to purchaser. | Datasheet is attached. TBE is not found. | Closed. |  |  |  |  |
|  | Scope of Supply | Transformer 800 KVA is 11/3.45 KV. This item will be revised in next revision of data sheet. | Confirmed | Closed. |  |  |  |  |
|  | Cables for 1250KVA transformer | - 11 kV Cables Size & Number: 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - 0.42 kV Cable Size & Number 14x(1x300), (CU/XLPE/Bd/AWA/PVC) - Type & Size of Power Cable Glands Primary: M90 Secondary: M40 - Type & Size of Cable Glands (Control Cable) 12x2.5, (CU/PVC/SWA/PVC), M25 - Undrilled Non Magnetic Gland Plated shall be provided. | Confirmed (Gland: by customer) Gland plate would be provided for HV and LV cable boxes. It should be noted that cable entry is considered from bottom for both sides. | Closed. |  |  |  |  |
|  | Cables for 800KVA transformer | - 11 kV Cables Size & Number: 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - 3.45 kV Cable Size & Number 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - Type & Size of Power Cable Glands Primary: M90 Secondary: M75 - Type & Size of Cable Glands (Control Cable) 12x2.5, (CU/PVC/SWA/PVC), M25 - Undrilled Non Magnetic Gland Plated shall be provided. | Confirmed (Gland: by customer) gland plate would be provided for HV and LV cable boxes. It should be noted that cable entry is considered from bottom for both sides. | Closed. |  |  |  |  |
|  | CT for Transformers | - Below CTs shall be Considered by Vendor on 1250 KVA Transformer: 2000/1A, 5P10 ,10VA - Below CTs shall be Considered by Vendor on 800 KVA Transformer: 630/1A, 5P10 ,10VA *Note: It is Preliminary and will be final by Switchgear Manufacturer. | Confirmed | با توجه به اینکه نقطه نوترال ترانس -11/3.3KV 800KVAتوسط NGR زمین شده است بایستی برای حفاظت 51G یک عدد ترانس جریان با مشخصات 100/1A – 5P20 – 15VA و برای حفاظت 64REF یک عدد ترانس مجاز دیگر با مشخصات 100/1A – CL:X – VK: 250V ~ 300V لحاظ گردد ( لازم بذکر است ولتاژ نقطه زانویی پس از قرارداد نهایی خواهد شد( و جهت ترانسفورماتور 11/0.42KV – 1250KVA یک عدد ترانس جریان 2000/1A – 5P20 – 15VA بایستی در نظر گرفته شود . همچنین ترانس های جریان در جعبه کابل قرار میگیرد . |  |  |  |  |
|  | Power Cable Gland | All Required Power Cable Glands & Plugs are in purchaser Scope of work and is ISO metric threaded in accordance with IEC60423. It should be Noted that Gland for Power Cables will be supplied by purchaser. | Gland plate would be provided. (Glands: By customer) | Closed. |  |  |  |  |
|  | Vendor List | Vendor list & sub vendor list of manufacture shall be according to project AVL. Sub-vendor List for Electrical Equipment shall be submitted for review and approval in bid stage. | Sub vendor list is attached. | Closed. |  |  |  |  |
|  | Spare Part | Spare Part for Commissioning and 2 Years Operation shall be Covered all requirement in Project Specification. | Attached. | Closed. |  |  |  |  |
|  | Special Tools | Any Special Tools for Life time Operation shall be included in technical offer. | N.A. | Closed. |  |  |  |  |
|  | Specification | Vendor shall submit the reference and experience list (as a separate file) for design & manufacturing of power transformer. | Reference list is attached. | Closed. |  |  |  |  |
|  | Shipment | Vendor shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification. | Acc to IRAN TRANSFO Procedure | Closed. |  |  |  |  |
|  | Arrangement | Transformer Outline Drawing shall be completed and LV/MV boxes shall be shown in top view for arrangement in shelter. | Outline drawing is revised. | Closed. |  |  |  |  |
|  | Comments on deviation list | According to IPS-M-EL-1152 (2), The cover of the tank for sealed type transformer shall be welded to the tank with a continuous weld. Please follow it. | Bolted cover is desirable. welded cover is not suggested due to maintenance issues. | در لیست مغایرت پروژه ارایه گردد تا نقطه نظر کارفرمای اصلی پروژه اخذ گردد. |  |  |  |  |
|  | Comments on outline drawing | The location of HV & LV side of bushing will be finalized later. Please confirm that if is possible to change it in detail design? | Confirmed. | Closed. |  |  |  |  |
|  | Comments on outline drawing | In items 7.16 to 7.20 of data sheet cables of transformers have been specified. In the cable boxes, when more than one conductor are to be connected, sufficient copper bars shall be provided to be connected to the cables indicated in data sheet. It shall be possible to test the cables without damaging the cables or the termination points of the transformer. Vendor shall consider all requirement for installation. The busbar for each phase (on LV busing) shall be such as cables 1*300 to be connected correctly. Please consider on outline drawing. | Busbar is considered for LV side of 1250 kVA transformer. | Closed. |  |  |  |  |
|  | Temperature de‐Rating Factors | Vendor shall submitted temperature de‐rating factors of equipment. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated current be equal or higher than rated current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. | Confirmed | Closed. |  |  |  |  |
|  | ITP & Test Report | Certificate or license, Test reports and type test shall be submitted based on latest revision of IEC 60076. | Confirmed. Has been attached | Closed. |  |  |  |  |
|  | As Built | As built documents and drawings are in vendor scope of work. | Confirmed | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | ترجیحا روغن مینرال و بدون افزودنی ترانسها از شرکت NYNAS(NYTRO LIBRA) تامین گردد. با توجه به عدم استفاده و اطلاع از کیفیت روغن مینرال شرکت ERAM SHIMI جهت ترانسها ، این شرکت مورد تایید نیست . | روغن مینرال و بدون افزودنی و از شرکت پالایش روغن های صنعتی زنگان تامین می گردد. | با توجه به نظر کارفرما ترجیحا روغن مینرال و بدون افزودنی ترانسها از شرکت NYNAS(NYTRO LIBRA) تامین گردد. با توجه به عدم استفاده و اطلاع از کیفیت روغن مینرال شرکت ERAM SHIMI جهت ترانسها ، این شرکت مورد تایید نیست در صورای که امکان ارایه روغن بالا نمیباشد در لیست مغایرت پروژه ارایه گردد تا نقطه نظر کارفرمای اصلی پروژه اخذ گردد. |  |  |  |  |
|  | NISOC_TR-2779 | ترجیحاً ورق هسته ها از شرکت های اروپای غربی تامین گردد . | ورق هسته از شرکت های VIZ روسیه و BAO چین قابل تامین می باشد. | با توجه به نظر کارفرما ترجیحاً ورق هسته ها از شرکت های اروپای غربی بایستی تامین گردد در صورتی که امکان ارایه مورد بالا نمیباشد در لیست مغایرت پروژه ارایه گردد تا نقطه نظر کارفرمای اصلی پروژه اخذ گردد. |  |  |  |  |
|  | NISOC_TR-2779 | حفاظتهای مکانیکی ترانس که باعث تریپ می شوند می بایست با کنتاکت FAIL SAFE در نظر گرفته شوند . | تجهیزات OIL LEVEL SWITCH , SUDDEN PERSSURE RELAY , WINDING THERMOMETER , OIL THERMOMETER دارای کنتاکت حالت FAIL SAFE می باشند . تجهیز PRESSURE RELIEF DEVICE فاقد حالت FAIL SAFE می باشد. | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | سازنده CT های نقطه نول توسط شرکت های ایران ترانسفو معرفی نشده اند . | تامین CT ها از شرکت مگ الکتریک و یا پارس شار بارز می باشد. | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | به جهت تسهیل در تعویض بوشینگهای ترانس ، لازم است ، بوشینگهای اولیه و ثانویه بر روی کاور بالای مخزن ترانس و یا در بالاترین نقطه از دیواره مخزن نصب گردند. بر این اساس می بایست DRAWINGها ، اصلاح و جهت بررسی ارسال گردند . صرفا شرکت ایران ترانسفو بوشینگها را در بالاترین نقطه از دیواره مخزن نصب نموده است ، در صورت امکان مطابق با ترانسهای موجود بوشینگها در بالای کاور نصب گردند. | ترانسفورماتورهای درخواستی از نوع هرمتیک با بالشتک گازی می باشد .بنابراین بوشینگ ها در بالاترین نقطه از دیواره مخزن لحاظ شده است . | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | در خصوص امپدانس درصد ترانس ها ، پس از نهایی شدن مطالعات شبکه اظهارنظر خواهد شد. | امپدانس درصد ترانسفورماتورهای 5% و نهایی می باشد و تغییرات خاصی ندارد | در لیست مغایرت پروژه ارایه گردد تا نقطه نظر کارفرمای اصلی پروژه اخذ گردد. |  |  |  |  |
|  | NISOC_TR-2779 | با توجه به پاسخ پیمانکار در صورتیکه کلیه شیرهای روغن ( تزریق / تخلیه / نمونه گیری ) و همچنین TAP CHANGER مجهز به قفل و یا با ابزار مخصوص باز و بسته باشند ، نظر خاصی نیست . | کلیه شیرها با flange بسته مسدود می شوند . تب چنجر از نوع pad lockable می باشد. | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | با توجه به اینکه رله SUDDEN PRESSURE جهت کلیه ترانسها در نظر و در نقشه OUTLINE DRAWING نمایش داده شده است ، نظری در این خصوص مطرح نیست . | Confirmed. | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | نمایشگر سطح روغن می بایست دارای کنتاکت آلارم باشد . | Confirmed. | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | GAS PRESSURE & VACUUM INDICATOR می بایست دارای کنتاکت آلارم باشد . | GAS PRESSURE & VACUUM INDICATOR فاقد کنتاکت می باشد | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | با توجه به نظر سازندگان مبنی بر اصلاح مدرک OUTLINE DRAWING با لحاظ و نمایش کلیه جزئیات و تجهیزات ترانس ها بعد از عقد قرارداد ( AFTER PO ) به اطلاع می رساند که این مدرک پس از انتخاب سازنده و ارسال مدرک اصلاح شده ، بررسی خواهد شد. | Confirmed. | Closed. |  |  |  |  |
|  | NISOC_TR-2779 | مدرک ITPاولیه میباشد و این مدرک در مرحله PIM بررسی و نهایی خواهد شد. لطفا تایید نمایید. |  |  |  |  |  |  |
|  | Deviation list | فرمت لیست مغایرت ارایه شده مورد تایید نمیباشد و فرمت لیست مغایرت پروژه که در مدرک MR (صفحه 13 از 15) قرار دارد بایستی تکمیل و ممهور گردد. |  |  |  |  |  |  |
|  | Project Document Stamp | MR and all attached documents of MR shall be read, signed and stamped by Vendor. |  |  |  |  |  |  |
|  | Data sheet | Latest revision of project documents such as data sheet shall be completed by vendor and submitted again. |  |  |  |  |  |  |
|  | Data sheet | Vendor shall submitted temperature de‐rating factors of equipment. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated current be equal or higher than rated current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. |  |  |  |  |  |  |
|  | MR | Following items shall be Specified and clarified by vendors : - Commissioning Spare part - - Two years Spare part - Reference list - Guarantee - Preliminary ITP - Packing and transportation - Delivery point |  |  |  |  |  |  |