| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Design Criteria | Vendor To confirm That All supplied material all in full compliance with Project site condition : - Min/Max air temperature = 0°C / 52°C - Relative humidity = 100% max at 52°C - Altitude = 12 m a.s.l. - Climate = Class 4 (Very High) | Confirmed | Closed. |  |  |  |
|  | Documents Priority | All The equipment’s shall be engineered, designed, manufactured, tested and installed in accordance with the following standards: - Local Codes & Standards - Iranian Petroleum Standard (IPS) - International Codes & Standards - IEC (International Electro technical Commission) - BS (British Standard) - IEEE (Institute of Electrical and Electronics Engineers) - API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards and codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes and Standards. 4-vendor Proposal. | Confirmed | Closed. |  |  |  |
|  | Scope of Supply | Minimum Scope of work and supply are in full compliance with Project MR (BK-GCS-PEDCO-120-EL-MR-0001). It has been Listed but not Limited to the following Items: - Full Engineering Services. - Two sets 11/0.42 KV, Hermetically Sealed (1250KVA - One set 11/3.45 KV, Hermetically Sealed (800KVA) - Inspection & Test ACC to ITP/QCP - Site Supervisory Servicers (Optional) | Confirmed | Closed. |  |  |  |
|  | Deviation List | Technical requirements shall be according to project specification in as minimum except those clearly specified in “deviation form”. BK-GNRAL-PEDCO-000-EL-DC-0001 (Electrical System Design Criteria) BK-GNRAL-PEDCO-000-EL-SP-0004 (Specification for Transformers) | This two document not Recivied | Closed. |  |  |  |
|  | General | Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR, TCL and codes & standards referred in the documents by issuing a New Deviation/Exception List With the respect to latest Modification and revised technical offer for purchaser's review and approval. Otherwise, the vendor must declare full compliance between all documents attached to the Inquiry package. | Confirmed | Closed. |  |  |  |
|  | General | Project Datasheet & TBE Table Shall be fill Out and return to purchaser. | Confirmed | Latest revision of project data sheet shall be completed by vendor and submitted again |  |  |  |
|  | Scope of Supply | Transformer 800 KVA is 11/3.45 KV. This item will be revised in next revision of data sheet. | Confirmed | Closed. |  |  |  |
|  | Cables for 1250KVA transformer | - 11 kV Cables Size & Number: 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - 0.42 kV Cable Size & Number 14x(1x300), (CU/XLPE/Bd/AWA/PVC) - Type & Size of Power Cable Glands Primary: M90 Secondary: M40 - Type & Size of Cable Glands (Control Cable) 12x2.5, (CU/PVC/SWA/PVC), M25 - Undrilled Non Magnetic Gland Plated shall be provided. | CONFIRM-ACC SETCTION 11 THIS DOCUMENT .TYPE GALND IS STEEL | Closed. |  |  |  |
|  | Cables for 800KVA transformer | - 11 kV Cables Size & Number: 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - 3.45 kV Cable Size & Number 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - Type & Size of Power Cable Glands Primary: M90 Secondary: M75 - Type & Size of Cable Glands (Control Cable) 12x2.5, (CU/PVC/SWA/PVC), M25 - Undrilled Non Magnetic Gland Plated shall be provided. | Confirm-ACC Section 11 This Document .Type Gland is Steel | Closed. |  |  |  |
|  | CT for Transformers | - Below CTs shall be Considered by Vendor on 1250 KVA Transformer: 2000/1A, 5P10 ,10VA - Below CTs shall be Considered by Vendor on 800 KVA Transformer: 630/1A, 5P10 ,10VA *Note: It is Preliminary and will be final by Switchgear Manufacturer. | Confirmed | با توجه به اینکه نقطه نوترال ترانس -11/3.3KV 800KVAتوسط NGR زمین شده است بایستی برای حفاظت 51G یک عدد ترانس جریان با مشخصات 100/1A – 5P20 – 15VA و برای حفاظت 64REF یک عدد ترانس مجاز دیگر با مشخصات 100/1A – CL:X – VK: 250V ~ 300V لحاظ گردد ( لازم بذکر است ولتاژ نقطه زانویی پس از قرارداد نهایی خواهد شد( و جهت ترانسفورماتور 11/0.42KV – 1250KVA یک عدد ترانس جریان 2000/1A – 5P20 – 15VA بایستی در نظر گرفته شود . همچنین ترانس های جریان در جعبه کابل قرار میگیرد . | Confirmed | Closed. |  |
|  | Power Cable Gland | All Required Power Cable Glands & Plugs are in purchaser Scope of work and is ISO metric threaded in accordance with IEC60423. It should be Noted that Gland for Power Cables will be supplied by purchaser. | Confirm-ACC Section 11 this Document .Type gland is Steel | Closed. |  |  |  |
|  | Vendor List | Vendor list & sub vendor list of manufacture shall be according to project AVL. Sub-vendor List for Electrical Equipment shall be submitted for review and approval in bid stage. | Confirmed | Closed. |  |  |  |
|  | Spare Part | Spare Part for Commissioning and 2 Years Operation shall be Covered all requirement in Project Specification. | Confirmed | Closed. |  |  |  |
|  | Special Tools | Any Special Tools for Life time Operation shall be included in technical offer. | Confirmed | Closed. |  |  |  |
|  | Specification | Vendor shall submit the reference and experience list (as a separate file) for design & manufacturing of power transformer. | Confirmed | Closed. |  |  |  |
|  | Shipment | Vendor shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification. | Confirmed | Closed. |  |  |  |
|  | Arrangement | Transformer Outline Drawing shall be completed and LV/MV boxes shall be shown in top view for arrangement in shelter. | Confirmed | Closed. |  |  |  |
|  | Temperature de‐Rating Factors | Vendor shall submitted temperature de‐rating factors of equipment. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated current be equal or higher than rated current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. | Confirmed | Closed. |  |  |  |
|  | ITP & Test Report | Certificate or license, Test reports and type test shall be submitted based on latest revision of IEC 60076. | Confirmed. Has been attached | We cannot find test reports please send again. |  |  |  |
|  | As Built | As built documents and drawings are in vendor scope of work. | Confirmed | Closed. |  |  |  |
|  |  | با توجه به نظر کارفرما ترجیحا روغن مینرال و بدون افزودنی ترانسها از شرکت NYNAS(NYTRO LIBRA) تامین گردد. |  |  | confirmed | Closed. |  |
|  |  | حفاظتهای مکانیکی ترانس که باعث تریپ می شوند می بایست با کنتاکت FAIL SAFE در نظر گرفته شوند . |  |  | confirmed | Closed. |  |
|  |  | با توجه به نظر کارفرما ترجیحاً ورق هسته ها از شرکت های اروپای غربی بایستی تامین گردد در صورتی که امکان ارایه مورد بالا نمیباشد در لیست مغایرت پروژه ارایه گردد تا نقطه نظر کارفرمای اصلی پروژه اخذ گردد. |  |  | BAO steel is | Closed. |  |
|  |  | به جهت تسهیل در تعویض بوشینگهای ترانس ، لازم است ، بوشینگهای اولیه و ثانویه بر روی کاور بالای مخزن ترانس و یا در بالاترین نقطه از دیواره مخزن نصب گردند. بر این اساس می بایست DRAWINGها ، اصلاح و جهت بررسی ارسال گردند . در صورت امکان مطابق با ترانسهای موجود پروژه بوشینگها در بالای کاور نصب گردند. |  |  | The bushings is on upper point . and type transformer hermetic gas Cushion | Closed. |  |
|  |  | ترجیحاً ورق هسته ها از شرکت های اروپای غربی تامین گردد |  |  | It's BAO steel. | Closed. |  |