## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-TB-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2779 |  |  | Transmital Date: 9/15/2024
Document Title: TBE For Transformers |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2779 |  |  | Transmital Date: 9/15/2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-TB-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | The size of 1250KVA transformer shall be rechecked and modified based on latest vendor data such as HAVAYAR&AAC, latest revision of I&C consumption list, control building LP/HVAC (new control building shall be considered). It shall be rechecked and modified after finalization load list based on NISOC and PEDCO comments. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | بر اساس آخرین ویرایش مدرک لیست بار الکتریکی، ترانسفورماتور 1250 کیلوولت آمپر کفایت خواهد کرد. در حال حاضر ترانس 1250 بارهای LV و 800 برای آب آتشنشانی منظور می گردد. |  |  | Noted &Closed.
2 | Latest revision of project documents such as data sheet shall be completed by vendor and submitted again. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | بین ویرایش دوم و سوم از مدرک Data Sheet تفاوتی وجود ندارد و فقط ویرایش سوم به صورت AFC تولید شده است. از اینرو شرکت آریا تراسفو و کیان ترانسفو ویرایش دوم را تکمیل نموده اند که مورد تأیید است. |  |  | Noted &Closed.
3 | Following items shall be added to TCL and shall be clarified by vendors: |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18
3-1 | MR and all attached documents of MR shall be read, signed and stamped by Vendor. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | هر سه سازنده مدرک MR را ممهور نموده اند. |  |  | Noted &Closed.
3-2 | Vendor shall submitted temperature de‐rating factors of equipment. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated current be equal or higher than rated current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | شرکت آریا ترانسفو و کیان ترانسفو پذیرفته است. |  |  | Noted &Closed.
3-3 | Certificate or license, Test reports and type test shall be submitted based on latest revision of IEC 60076. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | شرکت آریا ترانسفو و کیان ترانسفو ارائه نموده اند. |  |  | See below item 12.1
3-4 | Added to item 12, Vendor List: Sub vendor list shall be submitted and following items shall be specified in sub vendor list: -Manufacture -Country of origin -Model |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | شرکت آریا ترانسفو و کیان ترانسفو ارائه نموده اند. |  |  | Noted &Closed.
3-5 | As built documents and drawings are in vendor scope of work. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | هر دو شرکت آریا ترانسفو و کیان ترانسفو تأیید نموده اند. |  |  | Noted &Closed.
3-6 | Native completed deviation from Purchase Order or Purchaser procurement documents shall be submitted in next revision. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | شرکت آریا ترانسفو اعلام نموده است. ولی شرکت کیان ترانسفو مغایرتی ندارد. |  |  | Noted &Closed.
3-7 | All electrical equipment which is not in MOP and project AVL is not accepted after P.O. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | تمامی سازندگان از لیست بلند نفت می باشند. |  |  | Noted &Closed.
3-8 | Catalogue of all equipment such as transformer, CT, etc. shall be submitted by Vendor. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | شرکت آریا ترانسفو و کیان ترانسفو ارائه نموده اند. |  |  | Noted &Closed.
3-9 | Preliminary ITP shall be submitted at this stage and will be finalized in the PIM meeting. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | شرکت آریا ترانسفو و کیان ترانسفو ارائه نموده اند. |  |  | Noted &Closed.
4 | Conclusion column in devotion list shall be completed by consultant. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | نتیجه گیری تکمیل خواهد شد. |  |  | Will be checked later.
5 | All rows in TBE that has been mentioned "Clarification is Required", shall be approved by vendor otherwise it shall be mentioned in deviation list and shall be clarified. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | اعمال خواهد شد. |  |  | Noted &Closed.
6 | The cables size in TCL shall be updated based on latest revision of cable list (TR-2487). |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | اصلاح گردید. |  |  | Noted &Closed.
7 | As per latest project document (data sheet and SLD) one CT is required on 800kVA transformer neutral point. But in the clarifications it has been deleted. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | مطابق با اخرین ویرایش تک خطی، یک عدد CT با نسبت 100 به یک بر روی نقطه نوترال در نظر گرفته شده است. |  |  | Noted &Closed.
8 | Complementary comments will be submitted after receiving revised document. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | در صورت وجود کامنت، اعمال خواهد شد. |  |  | Noted &Closed.
9 | Following items to be added to TBE: - Commissioning Spare part - Two years Spare part - Reference list - Guarantee - Preliminary ITP - Packing and transportation - Delivery point - Deviation List |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | شرکت آریا ترانسفو و کیان ترانسفو در پاسخ کامنت های آن کارفرمای محترم، تمامی این آیتمها را تأیید نموده اند. |  |  | See below item 12.2, 12.3, 13.1.
10 | Latest revision of MR and related attached documents (TR-2780) shall be signed and stamped by all vendors. |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25 | لحاظ گردید.
11 | Arya Transformer: No Comment |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25
12 | Kian Transformer: |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25
12.1 | Sample of test reports and certificates have not been issued. |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25 | بعد از قرارداد تست رپورت های ترانس ها ارسل خواهد شد.
12.2 | issued reference projects are dry type transformers, reference list for sealed type transformer shall be issued. |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25 | لحاظ گردید
12.3 | Following items to be added to commission spare part list as per 13-E&C-QC-SP-1 table 2-24 (MR attachment for spare part) : BUSHING (HV/LV) HV/LV BUSHING O-RING & WASHER |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25 | لحاظ گردید.
12.4 | Neutral point CT on 800kVA transformer star point shall be two cores as per data sheet item 8.9 Core 1: 630/1A, 5P10 ,10VA Core 2: 630/5A, Class X |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25 | لحاظ گردید.
13 | Iran Transfo: |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25
13.1 | Following items to be added to commission spare part list as per 13-E&C-QC-SP-1 table 2-24 (MR attachment for spare part) : BUSHING (HV/LV) HV/LV BUSHING O-RING & WASHER |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25 | لحاظ گردید.
13.2 | Neutral point CT on 800kVA transformer star point shall be two cores as per data sheet item 8.9 Core 1: 630/1A, 5P10 ,10VA Core 2: 630/5A, Class X |  | BK-SUR-ENG-ELE-03-09557 | 2024-09-25 | لحاظ گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: