| Row | Clarification Title | Bidder reply (1st round) | Conclusion (2nd round) | Bidder reply (2nd round) |  | Conclusion (final/TCM) |
| --- | --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |  |
|  | Vendor to confirm that in case of contradiction between this TCL and offer; vendor confirmation of compliance through this technical clarification is governed and shall be followed by vendor after order. In such case offer won’t be considered as basis of any claim after order. | Noted and confirmed. | Closed. |  |  |  |
|  | Bidder shall confirm his full compliance to meet all purchaser documents listed and attached to MR, code / standards listed in MR with ref. No. “BK-GCS-PEDCO-120-ME-MR-0010 “as well as MR requirements. All deviations shall be listed in project deviation form, attach to this TCL, signed and stamped. Notes: 1-Any exception and deviation from the requirements of MR and the related specifications including referenced codes & standards shall be clearly declared by vendor in writing for purchaser’s approval at bid stage by using of the format included in “Letter Of Conformity” attached to material requisition. Raising no deviation to any single requirement means full compliance of vendor quotation to that requirement. Purchaser has no responsibility to discover deviations or alternatives scattered over the proposal in addition to what proclaimed explicitly in deviation list; hence such deviation (if any) is disregarded and shall not be considered for vendor claim in future. (Vendor to confirm) 2- Bidder shall confirm that all MR attachments listed in MR are available for her for review at bid stage. 3-Considering items 1 & 2, please note that any deviation at detail stage will not be accepted by purchaser. 4- MR scope of work and supply shall be signed and stamped by vendor. | Noted and confirmed, all deviations will be mentioned in the deviation list (chapter 3 in the technical specification), documents that are not submitted is mentioned in the pumps datasheet, letter of conformity is not found. | Vendor's deviation list will be finalized before P.O in clarification meeting. Please refer to technical comments on Deviation list. | Noted. |  |  |
|  | Bidder shall provide following documents while bidding: 1- Copy of valid quality system certificate(ISO 9001/2 or 3) 2- Sub- vendors / sub-suppliers list. 3- Deviation list with letter of conformity (Refer to item A2 above) 4- Reference and Experience List 5- Joint venture agreement (If any) with any company to design / fabrication of equipment. In case of joint venture ; qualified documents of the company who is part of joint venture shall be also submitted | 1,2,3,4- Noted and confirmed. 5-Noted, joint venture for this project will not be considered. | Closed. |  |  |  |
|  | Bidder shall submit selected Sub-Vendor List based on Project AVL, before proceeding with any purchasing activity. Vendors shall be selected from A.V.L Based On Products. Please confirm. | Noted, please submit project AVL. | Project AVL shall be followed by vendor as attachment#1 | Noted, Attachment 1 is not submitted. |  |  |
|  | Bidder to confirm that surface preparation and painting of all equipment material including valves , pipes , fittings and everything within the package are in accordance with project painting specification with ref. "BK-GNRAL-PEDCO-000-PI-SP-0006" attached to MR. | Noted and confirmed. | Closed. |  |  |  |
|  | Bidder to confirm that Packing, Marking, transporting procedure (BK-GNRAL-PEDCO-000-QC-PR-0045) for Shipment will be done in accordance to the project specification attached to the MR. | Noted and confirmed. | Closed. |  |  |  |
|  | Inspection and Test Plan / Quality Control Plan and their related inspection level (Witness, Hold, Review and Approval) shall be at least in accordance with MR and all project requirement such as NDT PROCEDURE. Any deviation is not accepted unless otherwise specified in deviation list and approved by Purchaser. | Noted and confirmed at this stage. Preliminary ITP attached to the technical specification (chapter 11) and ITP will be finalized after P.O at PIM. | Closed, ITP will be finalized during PIM. |  |  |  |
|  | Bidder to confirm that for all pressure parts and those required special consideration or stainless steel as well as for supports the material certificate should be in accordance with EN 10204, 3.1 Material certificate for non-pressure parts shall be in accordance with EN 10204,3.1 or 2.2 | Noted and confirmed for non-pressure parts, for pressure parts material certificate is as per EN10204 3.2. | Accepted except for shaft which shall be considered EN 10204 3.1 | Noted and confirmed for shaft without original certificate. |  |  |
|  | Bidder to confirm that all native files due to all calculations and drawings shall be submitted for purchaser approval after order. | Noted and confirmed. | Closed. |  |  |  |
|  | Following documents shall be submitted at bid stage (as a minimum requirement): 1. Vendor Catalogue 2. Quality Assurance Manual /Quality Management System Certificate (according to latest rev. of ISO) 3. P&IDs 4. Manufacturing Master Time Schedule Per Equipment (Including Design, Procurement, Fabrication, Test, Packing, Delivery) 5-Sectional drawing with BOM shall be submitted by vendor. 6-Noise Data 7-GA DWG with outline dimension, weights, suction and discharge nozzle load table and etc. shall be submitted by vendor in next revision. GAD shall include the arrangement of Pumps & their drivers and all auxiliaries. (driver, coupling, seal plan, cooling system (if any) and lubrication system (if any) 8. Utility Consumption List | 1-Noted, pumps catalogues have been already sent at previous stage. 2-Noted and confirmed. 3-Noted, after P.O. 4-Noted, delivery time will be mentioned in the technical specification (chapter 5) and time schedule will be submitted after P.O. 5-Noted, after P.O. 6-Noted, after P.O. 7-Noted, preliminary GA drawings will be submitted at next stage (chapter 13 in the technical specification) and finalized GA drawings with all details will be submitted after P.O at engineering phase. 8-Noted, after P.O. | 1,2,4,5,6,7,8 closed 3- Preliminary P&ID will be submitted on next Rev. | 3-Noted, after P.O. |  |  |
|  | Bidder shall confirm the scope of work and supply are fully in accordance with MR and its attachment with following items: 1- The consequences of HAZOP and SIL study shall be in vendor scope of supply and work. 2- Participation in technical meeting whenever it is necessary by Purchaser/Client to close engineering document after order is in vendor scope 3- Lifting lugs for erection with sling shackle and etc. shall be designed and supplied by vendor 4-N2 preservation with pressure regulator, valve & flexible hoses during transportation & 18 months of site storage based on requirements in MR shall be in vendor scope of supply / work. 5- All utility conditions shall be as per document "Process basis of Design Document; Doc. No: BK-GNRAL-PEDCO-000-PR-DB-0001 ". Moreover, bidder shall consider utility noted condition as per project design data. If other utility condition is needed, whole required facilities is in vendor scope of work/supply. 6- Anchor bolts | Noted and confirmed, all deviations about scope of work and supply are mentioned in the technical specification (chapter 3), N2 charge kit for this project is not required. | Noted and close. Refer to deviation list. |  |  |  |
|  | Vendor shall confirm Pumps and Equipment’s are fully suitable for outdoor installation/operation under project site conditions “Process Basis of Design; BK-GNRAL-PEDCO-000-PR-DB-0001 “without requiring any additional protection. | Noted and confirmed. | Closed. |  |  |  |
|  | Vendor shall send references list for each pump category with the following information: - Specified pumps models - Range of temperature - Capacity of the pumps - Differential head | Noted, reference list attached to the technical specification (chapter 15). | Closed. |  |  |  |
|  | Pre-commissioning, commissioning and start up spare parts shall be supplied by vendor. Vendor shall confirm to provide all required spare parts as per project spare part list attached to MR. | Noted and confirmed. | Closed. |  |  |  |
|  | Following items shall be considered (supplied) and included in the bid documentation: • Spare parts for commissioning and start-up • Spare parts for two years operation; a qualified and complete list based on E&C-QC-SP-1 • Capital spare parts (as option / if any) | Noted and confirmed. | Closed. |  |  |  |
|  | List of special tools required for the quoted pumps. Necessary special tools for erection/ installation and maintenance, if any, shall be included in supply. | Noted, special tools for this project are not applicable. | Noted |  |  |  |
|  | Vendor shall warranty the engineering, materials and workmanship of the equipment/goods. Under this warranty, all materials, parts, and assemblies found to be defective during the guarantee period shall be replaced free of charge by VENDOR. | Noted, this matter will be followed for guarantee duration (if vendor made a mistake), please be noted pump material selection and guarantee is chemistry and it is not our scope. | Closed. |  |  |  |
|  | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the date of mechanical completion & start-up, whichever occurs later. Also bidder to confirm performance guarantee requirements based on relevant data sheets & specifications (attached to the equipment PMR). | Noted and confirmed. | Closed. |  |  |  |
| PROCESS |  |  |  |  |  |  |
|  | All Equipment shall be designed as per project design criteria | Noted and confirmed. | Closed. |  |  |  |
| MECHANIC |  |  |  |  |  |  |
|  | The manufacturer should fill all the datasheets of the pumps with doc No: BK-GCS-PEDCO-120-ME-DT-0020 BK-GCS-PEDCO-120-ME-DT-0021 BK-GCS-PEDCO-120-ME-DT-0023 BK-GCS-PEDCO-120-ME-DT-0025 BK-GCS-PEDCO-120-ME-DT-0026 BK-GCS-PEDCO-120-ME-DT-0035 | Noted and confirmed. | Please revised according to technical comments | Noted, Final technical proposal will be sent and finalized before P.O |  |  |
|  | Design and supply of all interconnecting piping between equipment and all instruments, valves and … on them is in the vendor's scope. Also all between skid piping (including supporting) c/w all instrument and valve on them shall be designed, prefabricated and supplied by vendor. Detailed isometric DWGs shall be submitted for them. Note1: On skid piping to be assembled at vendor's shop. Note2; outside skid piping to be prefabricated and match marked for site assembling. | Noted and confirmed. | Closed. |  |  |  |
|  | ASTM number and grade of all supplied material to be specified. | Noted and confirmed, this matter will be specified in the pumps datasheet (chapter 13 in the technical specification) | Noted |  |  |  |
|  | Design and supply of heat tracing c/w supports, clips, and other provisions (including panels, heating cables and relevant connectors, electrical cables, junction boxes and thermostats) shall be part of the vendor scope. | Noted, heat tracing for this project is not applicable. | Closed. |  |  |  |
|  | Positive material identification (PMI), pickling and passivation for non-carbon steel material to be included in vendor’s scope of work. | Noted and confirmed. | Closed. |  |  |  |
|  | Test procedures shall be Submitted by vendor based on project´s document. | Noted, preliminary ITP attached to the technical specification (chapter 11) and ITP will be finalized after P.O at PIM. | Closed, ITP will be finalized during PIM. |  |  |  |
|  | Couplings shall be of two-piece, flexible, spacer type, permitting change of flexible membrane without disturbing the alignment of shafts. | Noted, please be noted pumps are non-API type so coupling is non-API type. (for non-API type coupling this matter will be followed after P.O.) | Noted coupling selection shall be followed as per Para 4.15 specification For Centrifugal Pumps For General Services (DOC NO: BK-GCS-PEDCO-120-ME-SP-0004). | Noted and confirmed, API type couplings for pumps will be considered by ASK. |  |  |
|  | The coupling guard shall be of non-sparking material. | Noted and confirmed. | Closed. |  |  |  |
|  | Design code for Centrifugal pumps, and sealing system shall be ISO 5199, IPS-M-PM-115. and API 682 4th Ed, respectively (w/considering relevant project specifications for centrifugal pump for General Services “Doc. No. BK-GCS-PEDCO-120-ME-SP-0004" | Noted, pumps are non-API type, so mechanical seals are non API type. Seal supply system for this project is not applicable. | Not Accepted. | Noted and confirmed, mechanical seals will be provided as per API682 standard. |  |  |
|  | Seal data sheet (based on API 682 4th Ed.) shall be provided by vendor after order to be approved by Purchaser. | Noted, pumps are non-API type, so mechanical seals are non-API type. | Not Accepted, refer to previous item. | Noted and confirmed, mechanical seals will be provided as per API682 standard. |  |  |
|  | All flange connection at battery limit shall be according to ASME B16.5, please confirm. | Noted and confirmed. | Closed. |  |  |  |
|  | 4 hour mechanical running test after oil stabilization is required | Noted, this matter is for API type pumps and it will not follow for non-API type pumps. | Closed. |  |  |  |
|  | All pumps shall have capacity curves continuously rising to shut-off. The head rise shall be at least 10% (not exceeding 20%) of the head at rated capacity | Noted and confirmed. | Closed. |  |  |  |
|  | The rated impeller diameter shall not be greater than 97% of the maximum impeller diameter and not less than 105% of minimum impeller Diameter. | Noted and confirmed. | Closed. |  |  |  |
|  | For pumps operating in parallel, the minimum head rise to closed valve shall be 15%. | Noted and confirmed. | Closed. |  |  |  |
|  | Pumps shall have stable head capacity curves which continuously rise to shut off. The Shut off head at rated speed shall be between 110 to 120 percent of the head at rated capacity. | Noted and confirmed. | Closed. |  |  |  |
|  | The rated duty point shall be between 70% and 120% of the best efficiency point of the furnished impeller. | Noted and confirmed. | Closed. |  |  |  |
|  | The pump casings shall be provided with a drain connection at its lowest point. Drains shall be piped and valved to the edge of the base plate and suitably braced. | Noted and confirmed. | Closed. |  |  |  |
|  | Electrical motors shall be appropriate for working temperature or Maximum Ambient Temperature whichever is greater | Noted and confirmed. | Closed. |  |  |  |
|  | Electrical motor should be sized based on Figure 2, paragraph 4.2 of ISO 5199 but shall not be less than 125% of pump's mechanical power at all range of motor operation from end curve to shut off. | Noted and confirmed. | Closed. |  |  |  |
|  | Allowable external forces and moments on nozzle should be conformed to Spec. No.: BK-GCS-PEDCO-120-ME-SP-0004 | Noted and confirmed. | Closed. |  |  |  |
|  | Bidder to consider the stainless steel name plate (including information as per PURCHASER advices) for the equipment. | Noted and confirmed. | Closed. |  |  |  |
|  | Please specify overhead clearance (maintenance area) on pumps outline drawing. | Noted, this matter will be specified in the finalized GA drawings after P.O at engineering phase. | Closed, will be finalized after P.O |  |  |  |
|  | Please indicate the pump rotation direction on GAD | Noted, this matter will be specified in the finalized GA drawings after P.O at engineering phase. | Closed. |  |  |  |
|  | Attached TBE form (Attachment#1) to be filled and sent via next response on TCL. | Noted and confirmed, filled TBE will be sent at next stage. | Noted. |  |  |  |
|  | New item |  | for all pumps Use air cooling, Cooling water is not applicable | Noted, cooling utility for project mechanical seals is not applicable. |  |  |
| PIPING & MATERIAL |  |  |  |  |  |  |
|  | Please send us General Arrangement Drawing of Pumps | Noted, preliminary GA drawings will be submitted at next stage (chapter 13 in the technical specification) and finalized GA drawings with all details and dimensions will be submitted after P.O at engineering phase. | Closed. |  |  |  |
|  | Catalogue for equipment shall be issued by vendor. | Noted, pumps catalogues have been already sent at previous stage. | Closed. |  |  |  |
|  | NEW ITEM |  | For S-8 material, the Impeller wear ring and case wear ring: Hard faced A351 Gr CF3M. | Noted and confirmed. |  |  |
| SAFETY |  |  |  |  |  |  |
|  | Vendor confirms that the Noise level @ 1m will not exceed 85 dB | Noted and confirmed. | Closed. |  |  |  |
| ELECTRICAL |  |  |  |  |  |  |
|  | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. IPS-E-EL-100 (1), IPS-M-EL-131 (2). | Noted and confirmed. | Closed. |  |  |  |
|  | All Electrical equipment shall be suitable for environmental data based on process design criteria. | Noted and confirmed . | Closed. |  |  |  |
|  | All documents related to electro motor shall be submitted by vendor such as, motor data sheet, motor outline drawing & etc. | Noted, all motors documents will be submitted after P.O. | Closed. |  |  |  |
|  | Vendor list & sub vendor list of manufacture shall be according to project AVL. | Noted, please submit project AVL. | Project AVL shall be followed by vendor as attachment#1 | Noted and confirmed |  |  |
|  | A complete set of spare parts for commissioning shall be supplied for each motor. | Noted and confirmed. | Closed. |  |  |  |
|  | The equipment shall be factory tested. Certified copies of test reports shall be submitted to the purchaser. | Noted and confirmed. | Closed. |  |  |  |
|  | Data sheet & Specification of LV induction motor have been attached to MR. Please follow them. | Noted and confirmed. | Closed. |  |  |  |
|  | Data sheet for LV induction motor shall be filled and submitted. | Noted and confirmed, motors datasheet will be filled after P.O. | Closed. |  |  |  |
|  | Principle of motor sizing shall be specified for all motors. | Noted and confirmed, motors power will be mentioned in the pumps datasheet (chapter 13 in the technical specification) | All required API & IEC coefficient to calculate nameplate power of electrical motors shall be considered by vendor. | Noted and confirmed. |  |  |
|  | For LV (400V) electric motors internal & external earth lugs shall be considered | Noted and confirmed. | Closed. |  |  |  |
|  | Motor painting color shall be RAL 7032. | Noted and confirmed. | Closed. |  |  |  |
|  | Low Voltage Electric motors (P<=150kW) shall be suitable for 400V±5% and 50Hz±2% , windings shall be delta connected and motor shall be suitable for DOL starting method. | Noted and confirmed. | Closed. |  |  |  |
|  | Starting current with positive tolerances shall not exceed from specified values in below (related to motor rated current): 750% for motors with rated power P<=75kW 650% for motors with rated power 75<P<=150kW | Noted and confirmed (except for motor power= 4 kw and 5.5 kw in SAFE zone), this motors are with routine structurer and they are not customized, so locked current for mentioned motors may be more than 8. | IPS-M-EL-131(2) shall be followed by vendor. | Noted and confirmed. |  |  |
|  | Motors shall be capable to starting their load with 80% of voltage at its terminals | Noted and confirmed. | Closed |  |  |  |
|  | Since power rated of motor will be finalized later, therefore size of cable & gland will be submitted after PO. Vendor shall follow the requirement. | Noted and confirmed. | Closed |  |  |  |
|  | Inspection/test of motors shall be according to MR. | Noted and confirmed at this stage, all motor tests scope will be finalized after P.O. | Closed |  |  |  |
|  | Motor bearings, fan & space heater shall be Considered in two years spare part list. | Noted and confirmed. | Closed |  |  |  |
|  | For outdoor motors, sun/rain protection canopy shall be considered by vendor. | Noted and confirmed, please specify motors that will be installed at outdoor. | Closed, All pumps will be installed at outdoor. |  |  |  |
|  | Please clarify for items in MRQ, electrical heat tracing is required or not? If heat tracing required, providing materials (heater cable, thermostat box, electric panel etc) and design (isometric drawings, calculation, bill of material) will be in vendor scope of work/supply. | Noted, heat tracing for this project is not required. | Closed. |  |  |  |
| STRUCTURE |  |  |  |  |  |  |
|  | The exact dimensions and size of the skid and the proper alignment under the skid shall be determined. | Noted, this matter will be specified in the finalized GA drawings after P.O at engineering phase. | Closed. |  |  |  |
|  | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2. also according to ASCE 7 (2010) Seismic Zone is equal to Zone 3 with Seismic Importance Factor 1.25 | Noted and confirmed. | Closed. |  |  |  |
|  | According to project spec. mean hourly with 50Yr return period speed shall be considered 120 Km/hr. | Noted, this matter will be specified after P.O at engineering phase. | Closed. |  |  |  |
|  | The type and location of the anchor bolt should be provided by vendor. This item shall be considered in G.A. Drawings. | Noted and confirmed, this matter will be specified in the finalized GA drawings. | Closed. |  |  |  |
|  | The static and dynamic loads of the equipment shall be presented at the foundation leve l. The elevation and location of the equipment center of mass shall be determined. | Noted and confirmed, this matter will be specified in the finalized GA drawings. | Closed. |  |  |  |
|  | The following codes & standards should be considered in the civil & structure section: AWS , ASCE7-10 , INBC6 | Noted and confirmed. | Closed. |  |  |  |
| QC |  |  |  |  |  |  |
|  | Vendor shall sign and stamp all engineering documents which are attached to PMR without Deviation. | Noted and confirmed, but all deviations will be mentioned in the technical specification (chapter 3) | Noted and closed. The deviation list is checked individually. |  |  |  |
|  | Vendor shall confirm and guarantee suitability of selected materials of each pump parts according to material class for pump service. Please check all selected or proposed materials. | Noted, pump material selection is chemistry and it is not our scope. | Material shall be guaranteed by vendor for pump's condition | Noted, not scope. |  |  |
|  | Vendor shall confirm to supply raw materials from approved vendor list and submit all required material certificates for TPI approval before manufacturing. | Noted, EN10204 3.2 for pressure parts and EN10204 2.2 for non pressure parts will be followed. | Accepted except for shaft which shall be considered EN 10204 3.1 | Noted and confirmed for shaft without original certificate. |  |  |
|  | Vendor shall confirm to issue and take client approval for vendor documents as per VPIS before any raw material supply or manufacturing. | Noted, EN10204 3.2 for pressure parts and EN10204 2.2 for non pressure parts will be followed. | Accepted except for shaft which shall be considered EN 10204 3.1 | Noted and confirmed for shaft without original certificate. |  |  |
|  | Vendor shall confirm material selection for each part of package is suitable for service condition and design life. | Noted, pump material selection is chemistry and it is not our scope. | Material shall be guaranteed by vendor for pump's condition | Noted, not scope. |  |  |
|  | Welding book (including WPS, PQR, weld map and NDT map) shall be prepared by vendor and submitted for purchaser approval (pressure parts, and structural). No welding shall be commenced before receiving approved welding book. | Noted and confirmed. | Closed. |  |  |  |
|  | Vendor to confirm, the package shall be designed and constructed so that requires minimum site work (preparation and welding) while fulfills transportation limits. | Noted and confirmed. | Closed. |  |  |  |
|  | Vendor shall confirm to have full responsibility on quality control of manufactured equipment and shall be responsible for any deviations or non-conformities before, during and after manufacturing and after installation and start up. | Noted and confirmed. | Closed. |  |  |  |
|  | Vendor shall confirm to employ certified and expert workers and inspectors and to use calibrated measuring instruments according to regulations of ISO 3834 and ISO 9001. | Noted, we can provide ISO9001 certificate for our equipment, ISO 3834 certificate cannot provide. | Closed. |  |  |  |
|  | Vendor shall confirm to perform and report all required inspection and tests according to project specification and datasheets and reference standards and approved ITP including visual, dimensional, NDT, PMI, PWHT, Hardness, Hydrotest, Performance, Running, … | Noted and confirmed. | Closed. |  |  |  |
|  | Vendor shall confirm to observe health & safety precautions and regulations during manufacturing for workers, inspectors, engineers and visitors. Vendor shall confirm observe environmental regulations during manufacturing processes such as casting, machining, welding, blasting, etc. | Noted and confirmed. | Closed. |  |  |  |
|  | Vendor to confirm to prepare final data book according to project FDB requirements. | Noted and confirmed. | Closed. |  |  |  |
| INSTRUMENT |  |  |  |  |  |  |
|  | NEW ITEM |  | Instruments related to seal plans( if any) shall be supplied by pump Vendor as per API 682 and data sheet. |  | Noted, instrument for project seal plans is not applicable. |  |
|  | NEW ITEM |  | Instrument reference documents shall be followed by Vendor which are: -BK-GNRAL-PEDCO-000-IN-SP-0001 SPECIFICATION FOR INSTRUMENTATION -BK-GNRAL-PEDCO-000-IN-SP-0004 SPECIFICATION FOR INSTRUMENT AND CONTROL OF PACKAGE UNIT SYSTEM (PU) -BK-GNRAL-PEDCO-000-IN-SP-0010 SPECIFICATION FOR INSTRUMENTF&G CABLES |  | Noted and confirmed. |  |
|  | NEW ITEM |  | P&ID for mechanical seal and instrument data sheet (if any) to be provided before order. |  | Noted, not applicable. |  |

| # | Clarification Description NISOC Letter 1403/07/29 03/2294/291846 | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- |
| مکانیک |  |  |  |  |
| 1. | سازندگان دست دوم کالا (Sub Vendor List) نیز می بایست از لیست سازندگان مجاز انتخاب گردند. | ملاحظه شد و مورد تایید است. |  |  |
| 2. | کالای یدکی می بایست بر اساس پیشنهاد سازنده و حداقلهای مندرج در پیوست 11 کتابچه اسناد پیمان تهیه گردد. | ملاحظه شد و مورد تایید است. |  |  |
| برق |  |  |  |  |
| 1. | از آنجا که الکتروموتورهای پروژه باید براساس مشخصات فنی اختصاصی پروژه تامین گردند ( دارای مشخصات فنی و داده برگ اختصاصی میباشند) لذا لازم است محصول پیشنهادی بر این اساس تامین گردد و از ارسال مشخصات فنی عمومی موتور های موجود در بازار خودداری شود. | ملاحظه شد، الکتروموتورها سفارشی ساز بوده و تا حد امکان اسپک پروژه رعایت خواهد شد. |  |  |
| 2. | سازندگان پمپ مدارک الکتروموتور را بدون درج اطلاعات فنی در داده برگ پروژه صرفا مهمور نموده اند و موضوع پیش گفته سبب مشکلاتی در پروژه ها و مغایرت پس از سفارش گذاری خواهد شد . | ملاحظه شد، از آنجایی که کلیه جزئیات موتورها پس از سفارش گذاری توسط تامین کننده موتور مشخص می شود لذا مدارک موتور از قبیل دیتاشیت ها پس از سفارش توسط تامین کننده مربوطه ارائه خواهد شد. |  |  |
| 3. | سازندگان میبایست در مدرکی مجزا Deviation list را ارائه نمایند و به صراحت در آیتمی مجزا به مدارک الکتریکال (شامل داده برگ الکتروموتور، مدرک مشخصات فنی الکتروموتور و IPS-N-EL-131(2 اشاره نموده و هر گونه مغایرت با مدارک الکتریکال را اعلام نمایند. اعلام انحرافات به صورت NOTE در انبوه مدارک مکانیک قابل بررسی نیست) | ملاحظه شد، تمامی انحرافات در بخش 3 پیشنهاد فنی ذکر شده است. |  |  |
| 4. | موتورها باید بصورت بدون هیتر طراحی و تامین شوند و کلیه روتین تست های کارخانه ای بر اساس ملاحظات استاندارد IPS-M-EL-131 باید در کارخانه سازنده الکتروموتور و با حضور کارفرما محقق گردد. | ملاحظه شد و مورد تایید است. |  |  |
| 5. | از آنجا که تست کارخانهای در محل سازنده الکتروموتور و با حضور کارفرما صورت پذیرد و حداقل تستهای کارخانهای در IPS تعیین گردیده است لذا سازندگان نسبت به موضوع پیش گفته به صراحت شفاف سازی نمایند. | ملاحظه شد، درصورت در خواست این مورد امکان حضور نماینده کارفرما در محل کارخانه تامین کننده (برند وم: آلمان، برند هیوسانگ: کره جنوبی) می باشد و هزینه این مورد به صورت مجزا اعلام خواهد شد. |  |  |
| 6. | مطابق داده برگ الکتروموتور پروژه , Explosion Protection of Motor بصورت Zone 2 , IIB, T3 در محیط خطر باید در نظر گرفته شود | ملاحظه شد، این مورد در ویرایش جدید پیشنهاد فنی در نظر گرفته خواهد شد. |  |  |
| 7. | در خصوص موارد مطروحه در بخش QC جدولTCL به اطلاع میرساند موضوعات مطروحه مورد پدیرش نبوده و میبایست پیش از عقد قرارداد به تایید کارفرما برسد. | ملاحظه شد، در خصوص این موارد در جلسه فنی تصمیم گیری خواهد شد. |  |  |
| 8. | موارد مطروحه در بند 18 جدول TCL در خصوص کالای یدکی مورد پذیرش نیست. | ملاحظه شد، بند 18 مشخص گردد. |  |  |
| 9. | ITP بدلیل نقص فراوان نسبت به ملاحظات اشاره شده در MR (دستور العمل بازرسی خرید و ساخت کالا و آزمون های بند 9-4 استاندارد IPS-M-EL-131) مورد تایید نیست. | ملاحظه شد، ITP در PIM نهایی خواهد شد. |  |  |
| 10. | جهت سازنده الکتروموتور صرفا در به شرکتهای هیوسانگ و وم در لیست سازندگان فرعی اشاره شده و فاقد جزئیات فنی مورد نیاز در مقطع کالا است. | ملاحظه شد، کلیه جزئیات موتورها پس از سفارش توسط تامین کننده مربوطه مشخص می شود و تا حد امکان اسپک پروژه در این خصوص رعایت خواهد شد. |  |  |
| 11. | مدرک Technical Spec سازنده صفحه 31(داده برگ نکمیل شده مکانیک در بخش Note اشاره نموده است که در مدرک Document Number BK-GNRAL-PEDCO-000-EL-SP-0017, Noted is Not Found پیدا نشده است بنظر میرسد مدرک مربوط به موتور mv می باشد. | ملاحظه شد، در این صورت نیاز به مدرک مربوطه نمی باشد. |  |  |
| 12. | سازنده مدارک الکتریکال را صرفا مهمور نموده و هیچگونه داده ای و مشخصاتی بر اساس مدارک الکتریکال پروژه ارائه ننموده است. | ملاحظه شد، کلیه جزئیات موتورها پس از سفارش توسط تامین کننده مربوطه مشخص می شود و تا حد امکان اسپک پروژه در این خصوص رعایت خواهد شد. |  |  |
| 13. | رعایت موضوعات مندرج الزامی است. | ملاحظه شد. |  |  |

| # | Clarification Description PEDCO Letter 1403/06/24 'BK-SUR-ENG-MEC-03-09533 | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |
| 1. | No deviation can be checked except those mentioned in Deviation list. | Confirmed. |  |  |
| Mechanical comments :(TECHNICAL SPECIFICATION) |  |  |  |  |
| 1. | - PAGE 6 OF 100 , SCOPE OF SUPPLY : - All motor junction boxes complete with necessary terminal shall be supply by vendor - scope of work of Instrumentation including wiring from MCC to Main motor to be clarified | Noted, JB for motors will be supplied by ASK but LCSs and wiring from MCC to electromotors are not our scope, controls are not our scope and wiring just at electro-pumps skid will be considered by ASK. |  |  |
| 2. | PAGE 11,12,13 OF 100 ,DEVIATION LIST : Item 1 : Material shall be guaranteed by vendor for pump's condition Item 2: Not Accepted. In according to project document (SPECIFICATION FOR CENTRIFUGAL PUMPS FOR GENERAL SERVICES) all mechanical seal shall be in according to API 682. Item 3 : Accepted except for shaft which shall be considered EN 10204 3.1 item 4 & 6 & 12 & 14 : Not necessary, clarify Item 5 & 7 & 10 & 15: To Note that contrary flange shall be selected by respect to pump and related pipe specification. Item 9 : Explain the reasons of changing Item 11 : After deciding on item 9 Item 18: Not Accepted. In according to project document (SPECIFICATION FOR CENTRIFUGAL PUMPS FOR GENERAL SERVICES), Coupling shall be of stainless steel flexible element with steel coupling hubs provided with spacer. | Noted, 1-Noted, material selection is not our scope. 2-Confirmed, API682 will be followed for mechanical seals. 3-Confirmed for shaft without original certificate. 4,6,12,14-Pumps nozzle size or rating is different from piping size, for this matter contrary flange can be considered. 5,7,10,15- Contrary flange will be supplied by ASK and mating flange or reducer shall be provided by purchaser. 9-Pump length is 4m and for reduce of vibration, selected VS1 type pump with 1450 rpm speed is more suitable, VS4 type with 1450 rpm is bigger and has lower efficiency and with 2950 rpm is with more vibration and lower efficiency than VS1 type pump. 11-Noted. 18-Confirmed, API671 standard for coupling will be considered |  |  |
| 3. | PAGE 29 of 100, Sub vendor list: All sub vendors shall be from AVL. Also all part of mechanical seal and Flush plan shall be supplied from AVL | Noted, please submit project AVL. |  |  |
| 4. | Data sheet : - page 34 & 41 & 62 of 100 : Note 5 : Material shall be guaranteed by vendor for pump's condition - page 34 & 41 & 62 of 100 : Note 6 : Not Accepted. In according to project document(SPECIFICATION FOR CENTRIFUGAL PUMPS FOR GENERAL SERVICES), Mechanical seal shall be as per API 682 -Page 34 & 41 & 62 of 100 : Note 13 : Note contrary flange shall be selected by respect to pump and related pipe specification. - PAGE 36 & 43 & 57 & 64 OF 100 : all attached document to MR shall be submitted to vendor by contractor and vendor shall be stamped it. - Page 48 & 55 & 69 of 100 : Note 6 : Material shall be guaranteed by vendor for pump's condition - Page 48 & 55 & 69 of 100 : Note 7 : Not Accepted. In according to project document(SPECIFICATION FOR CENTRIFUGAL PUMPS FOR GENERAL SERVICES), Mechanical seal shall be as per API 682 - Page 50 of 100 : Material is not approved by Client and it cannot be checked.it shall be finalized after Client approval. -Page 64 of 100 : Material : Material of impeller and wear rings shall be ASTM A48 Class 30B Page 75 of 100 : Spare part list : spare part list shall be in compliance with BINAK project spare part list | -Noted, material selection is chemistry and it is not our scope. -Noted and confirmed, API682 standard for mechanical seals will be followed. -Noted, contrary flange will be supplied by ASK and mating flange or reducer shall be supplied by purchaser. -Noted, signed and stamped MP and its attachments have been already sent at previous stage. -Noted and confirmed, API682 standard for mechanical seals will be followed. -Please specify requested material. -Noted and confirmed, A48 class 30B will be considered at next stage. -Noted, project spare part scope has been already followed, if you have any comment please inform us. |  |  |
| 5. | NPSH Margin at end of curve shall be compared | Noted, NPSHr @ end of curve for all pumps is lower than NPSHa. |  |  |
| Electrical comments : |  |  |  |  |
| 1. | 1- گروه گازي كليه موتورهاي ضد انفجار به صورت IIB در پيشنهاد فنی در نظر گرفته شود. 2- ديتا شيت موتورهاي الكتريكي فشار ضعيف موجود در پيوست MR باييستي توسط سازندگان تكميل و مهر و امضا شده در پيشنهاد فني ارائه گردد. 3- كليه تستها وبازرسي ها با توجه به دستور العمل بازرسي و خريد كالا موجود در پيوست MR در جلسه PIM نهايي خواهد شد. | - ملاحظه شد و در ویرایش جدید پیشنهاد فنی در نظر گرفته خواهد شد. - ملاحظه شد، از آنجایی که کلیه مشخصات و جزئیات موتورها پس از سفارش گذاری توسط تامین کننده مشخص می شود بنابراین این مورد پس از سفارش الکتروموتورها توسط تامین کننده تکمیل خواهد شد. - ملاحظه شد و مورد تایید است. |  |  |
| 2. | مطابق نقشه Area classification layout پمپهاي P-2203A/B Sump Pumps در ناحيه Zone I قرار دارند و بايستي ضد انفجار با درجه حفاظت Zone 1,Ex’d’, IIB, T3 باشند | ملاحظه شد و در ویرایش جدید پیشنهاد فنی اصلاح خواهد شد. |  |  |
| 3. | گواهي نامه هاي IP و گواهي نامه هاي ضد انفجار براي موتورها بايستي به مدارك ليست شده در بخش 6 مدرك technical specification موجود در پيشنهاد فني اضافه گردد. | ملاحظه شد و مورد تایید است، این مورد در پیشنهاد مالی لحاظ خواهد شد. |  |  |