## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2747 |  |  | Transmital Date: 8/18/2024
Document Title: Existent MV Switchgear Expansion Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0305-EL-TR-2747 |  |  | Transmital Date: 8/18/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0003_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در نقشه می بایست LCS مربوط به الکتروپمپ آتش نشانی و CT مربوط به آن نمایش داده شود. |  | 1403-2294-229168 | 1403/06/19 | نمایش داده شد.
2 | پوش باتن استاپ الکتروموتور کمپرسور در LEGEND مدرک نمایش داده شود. |  | 1403-2294-229168 | 1403/06/19 | نمایش داده شد.
3 | CTCB الکترو موتور کمپرسور مطابق با ویرایش های قبل 60/1A در نظر گرفته شود. |  | 1403-2294-229168 | 1403/06/19 | لحاظ گردید.
4 | مطابق با ویرایش پیشین و مدارک سازنده RATED CURRENT فیدر ها در مدرک نمایش داده شود. |  | 1403-2294-229168 | 1403/06/19 | اعمال گردید.
5 | مطابق با نقشه ی فیدر های موجود در اسناد پایه نیازی به در نظر گرفتن کنتور بر روی فیدر های 11KV ترانسی ها نیست و می توان آن را حذف نمود. |  | 1403-2294-229168 | 1403/06/19 | درفیدرهای فوق کنتور حذف گردیده است و صرفاً یک عدد مولتی فانکشن لحاظ شده است.
6 | با توجه به اسناد سازنده کمپرسورها توان الکترو موتورهای مربوطه به 1070KW@55OC اصلاح گردد. |  | 1403-2294-229168 | 1403/06/19 | اعمال گردید.
7 | توان الکترو موتور پمپ آتش نشانی در مدرک قید گردد. |  | 1403-2294-229168 | 1403/06/19 | اعمال گردید.
8 | با رفع موارد مذکور،نظری مطرح نیست و ادامه روند طراحی بلامانع می باشد. |  | 1403-2294-229168 | 1403/06/19 | -
16
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: