Hirgan Energy

Technical Offer for F&G Device

Binak Oilfield Development

Your Ref:   BK-GCS-PEDCO-120-IN-MR-0007_D01

Our Ref: 	0327008-Tec-Rev01

| Prepared: | Approved: | Date: |
| --- | --- | --- |
| Sina Sadeghi | Peyman Tajbakhsh | 13 November 2024 |

# Introduction

We thank you for your enquiry and take pleasure in submitting this proposal for the goods requested. The unit price stated includes all applicable discounts.

I trust this is of interest, if you need any additional information, please do not hesitate to contact me.

## Client Contact

Mr. Salarvand,

Kiomars Salarvand

Logistics Lead

Hirgan Energy Eng. Co.

+98 21 880620 70 Ext. 504

Email: k.salarvand@hirgan-di.com

www.hirganenergy.com

## Tima Kala Tehran Eng. Co. Point of Contact

Peyman Tajbakhsh

Vice President

Tima Kala Tehran Engineering Co.

No.7, Moshiri St., Dr. Mofateh Ave.,

Tehran, Iran

Email : pet@tima.ir

Tel Contact:  +98 21 88 83 19 55

Cell Contact: +98 912 389 80 44

1	Introduction	2

1.1	Client Contact	2

1.2	Tima Kala Tehran Eng. Co. Point of Contact	2

2	General	4

2.1	Subject	5

2.2	Revision	5

3	Fire and Gas Detection Devices	6

3.1	Flammable Gas Detector- IRmax	6

3.2	Flammable Gas Detector (Duct Mount)- IRmax Remote Display	8

3.3	Toxic Gas Detector- Xgard IQ	10

3.4	Toxic H2S Gas Detector (Duct Mount)– Xgard IQ	12

3.5	UV/IR Flame Detector - FL500	14

3.6	Outdoor Fire/Toxic/Flammable Gas Horn – E2S	16

3.7	Outdoor Toxic Gas Blue Beacon – E2S	19

3.8	Outdoor Fire Red Beacon – E2S	21

3.9	Outdoor Flammable Gas Yellow Beacon – E2S	24

3.10	Addressable Safe Area Flashing Beacon (Red) – XP95	27

3.11	H2 Gas Detector -Xgard IQ	28

3.12	Outdoor Manual Call Point – E2S	30

3.13	Addressable Safe Area Manual Call Point-Discovery	33

3.14	Linear Heat Detector FT88R- Signaline	35

3.15	Addressable Smoke Detector- Discovery	38

3.16	Alarm Bell – Apollo (klaxon)	43

3.17	Explosion Proof Heat Detector – Oggioni	44

3.18	Addressable Heat Detector-Discovery	46

4	Special Tools	50

4.1	Gas Calibration Kit	50

4.2	Flame Detector Tester – TL105	51

4.3	Smoke/Heat Detector Tester– SOLO814	51

5	Commissioning Spare Part	52

6	Optional Two Years Spare Parts	53

7	Site Supervision for Installation	54

8	Optional Training	54

9	Deviation	55

10	Clarification	57

11	Commercial Proposal	58

11.1	Fire and Gas Devices	58

11.2	Special Tools	59

11.3	Commissioning Spare Part	59

11.4	Optional SAT, Site Supervision and Training	60

11.5	Optional Two Years Spare Parts	61

11.6	Total Commercial offer	61

12	Terms	63

13	Tender Validity	63

14	Payment	63

15	Delivery Time	63

16	Delivery terms	63

17	Declaration of Guaranty	63

18	After Sales Service	63

# General

## Subject

This Technical proposal covers the, inspection, testing, calibration, packing, training and warranty of:

“Binak Oilfield Development – Surface Facilities; New Gas Compressor Station “

This study takes into account the accepted safety standards that currently apply in the petroleum industry for offshore/onshore installations.

The answer has been design as the specification as follow:

| Document Number | Revision | Description |
| --- | --- | --- |
| BK-GCS-PEDCO-120-IN-MR-0007_D01 | D01 | MR |
| BK-GCS-PEDCO-120-IN-DT-0016_D04 | D02 | Data Sheet for F&G Device |
| BK-GCS-PEDCO-120-IN-LI-0008_D03 | D03 | F&G Detector List |
| TCL-TimaKala | D01 | Technical clarification |

## Revision

| Number | Revision | Date | Description |
| --- | --- | --- | --- |
| 1 | 00 | 28-JULY-2024 | Based on Project Document as described above |
| 2 | 01 | 12-Nov-24 | Based on Project Document as described above |

# Fire and Gas Detection Devices

## Flammable Gas Detector- IRmax

IRmax is an ultra-compact infrared (IR) gas detector that delivers rapid, fail-safe detection of hydrocarbon gases and vapors. The reliability of IRmax has been proven in hot, cold, wet and saline environments, making it ideal for offshore. IRmax's unique STAY-CLIR optical components are treated with a highly durable coating that completely prevents faults due to condensation.

| Sensor Type Accuracy Operating Temperature Power Consumption Ingress Protection Humidity Repeatability Zero Drift Span Stability Self-diagnostic Operating voltage Detection Range Response Time Linearity ATEX Certification Enclosure Material Electrical Output Cable Entry Life time Operation Display | Dual path/ Dual wave length Infra-Red ± 2% of full scale - 40°C to + 75°C Max 1 Watt IP66 0 to 100% RH non-condensing ± 2% of full scale ± 2% of full scale Per Year Maximum < 5 % FSD Self-test and fault signal capability 12-32 V dc 0-100% LEL CH4 T90 <4 sec ± 3% of full scale EExd IIC T4(-40°C to +75°C) SIL2 Certified- according to IEC-61508 316 stainless steels 3-wire 4-20mA with HART over 4-20 1xM20 and 1x 1/2” NPT cable gland entry 10 Years Display with button for configuration and acknowledge with 3 color LED indicator |
| --- | --- |

Note: Stainless Steel tag plate, Stainless Steel Sunshade Splash Guard, Ex M20 Cable gland, 2” pipe mounting kit including bolts and nots are included.

Part Number: IRMAX-AA-AC-011-AF-01(CH4)

Manufacture: Crowcon /UK

| Flammable Gas Detector (Process Area) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | FGD-1001 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-2001 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-2002 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-2003 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-2004 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4001A | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4002A | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4003A | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4004A | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4001B | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4002B | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4003B | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4004B | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4001C | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4002C | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4003C | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-4004C | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-5001A | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-5001B | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-5001C | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-6001 | Flammable Gas Detector | EExd Zone1, IIB T4 | AI-IS-R | Conventional |
|  | FGD-6002 | Flammable Gas Detector | EExd Zone1, IIB T4 | AI-IS-R | Conventional |
|  | FGD-6003 | Flammable Gas Detector | EExd Zone1, IIB T4 | AI-IS-R | Conventional |
|  | FGD-7001 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-7002 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-7003 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |

  - Flammable Gas Detector (Duct Mount)- IRmax Remote Display

IRmax is an ultra-compact infrared (IR) gas detector that delivers rapid, fail-safe detection of hydrocarbon gases and vapours. The IRmax gas detection system offers the choice of a detector only, a local gas/status display, a remote gas/status display or non-intrusive calibration via an I.S. calibration tool or hand-held HART communicator.

| Size Weight IP Sensor Type Material Power Connection Electrical output Operating temperature Humidity Repeatability Zero drift Linearity Response time Functional safety Detection range Display Indicator EMC Approval HART | 261 x 75 x 57mm 2.4 Kg IP66 Infra-red SS316 12-30 VDC One M20 or ½” NPT cable gland entry 4-20 mA sink or source -40°C to +75°C 0-95 % RH none condensing +/- 2% FSD +/- 2% FSD per year maximum +/- 3% of full-scale T90< 4 sec SIL2 0-100 % LEL Hexane Fixed 4- digit LCD with back-light 3 color LED indicator EN50270, FCC CFR47 Part 15B, ICES-003 Ex II 2 GD Ex db ia IIC T4 Gb (Tamb -40°C ≤ Ta ≤ +75°C) Ex II 2 GD Ex tb ia IIIC T135°C Db (Tamb -40°C ≤ Ta +40°C) HART over 4-20 mA |
| --- | --- |

Note: Stainless Steel tag plate and Duct/Wall mounting Kit with bolts and nuts and 20 (at least 15 meter) meter IS connecting cable between sensor and display are included.

Part Number: IRMAX-BT-AC-011-AF-03

Manufacturer: Crowcon / UK

| Flammable Gas Detector (Building - HVAC) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | FGD-1101 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-1102 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-1103 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-1201 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-1202 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FGD-1203 | Flammable Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |

## Toxic Gas Detector- Xgard IQ

XgardIQ is an intelligent and versatile gas detector and transmitter compatible with Crowcon’s full range of sensor technologies. Available fitted with a variety of flammable, toxic or oxygen gas sensors. Providing analogue 4-20mA and RS-485 Modbus signals as standard, The 316 stainless steel are available with three M20 or1/2”NPT cable entries.

| Wiring type Sensor Type: Resolution: Relay Expected operating life Linearity Accuracy Zero drift: Stabilization time: Repeatability Life time Operating Temperature: Ingress Protection: Humidity: Operating voltage: Detection Range: Response Time: ATEX Certificate: Enclosure Material: Electrical Output: Display Cable Entry: | - wire sink or source Electrochemical 1PPM Included SPCO relays for conventional connection >36 months <5% full scale <3% full scale <3% per year 60 sec 2%FSD > 2 Years - 40°C to + 75°C (Transmitter), - 30°C to + 70°C (Sensor) IP66 0 to 90% RH non-condensing 14-32 V dc< 4w 0-100 PPM H2S T90~ 40 sec Ex II 2 G Exd iallC T4 Gb (Tamb -40C to +75C) 316 stainless steel 4-20mA current sink or source (Auto-Sense or manual selection), HART, warning and fault signals are configurable, Alarm and Fault Relay OLED 128 x 64 pixels, yellow text on black background |
| --- | --- |

Note: Stainless steel tag plate, stainless steel Sunshade, Ex brass nickel plated M20 Cable gland, 2” pipe mounting kit including bolts and nots and splash guard are included.

Part Number: XIQ-ZZ-S1-011-H-R-A (Transmitter), XIQ-IL (Sensor)

Manufacturer: Crowcon / UK

| Toxic Gas Detector (Process Area) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | TGD-1001 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-2001 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-2002 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-2003 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-2004 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4001A | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4002A | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4003A | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4004A | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4001B | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4002B | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4003B | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4004B | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4001C | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4002C | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4003C | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-4004C | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-5001A | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-5001B | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-5001C | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-6001 | Toxic Gas Detector | EExd Zone1, IIB T4 | AI-IS-R | Conventional |
|  | TGD-6002 | Toxic Gas Detector | EExd Zone1, IIB T4 | AI-IS-R | Conventional |
|  | TGD-6003 | Toxic Gas Detector | EExd Zone1, IIB T4 | AI-IS-R | Conventional |
|  | TGD-7001 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-7002 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-7003 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |

## Toxic H2S Gas Detector (Duct Mount)– Xgard IQ

XgardIQ is an intelligent and versatile gas detector and transmitter compatible with Crowcon's full range of sensor technologies. Available fitted with a variety of flammable, toxic or oxygen gas sensors.

Providing analogue 4-20mA and RS-485 Modbus signals as standard, the 316 stainless steels are available with three M20 or1/2"NPT cable entries.

| Wiring type Sensor Type: Detection Range: Expected operating life Linearity Zero drift: Accuracy Stabilization time: Operating Temperature: Ingress Protection: Humidity: Operating voltage: Resolution: Response Time: ATEX Certificate: SIL rating Enclosure Material: Self-diagnostic Electrical Output: Display Cable Entry: | 3 wire sink or source Electrochemical 0-50PPM >24 Months <5% full scale <1% per Year NA 60 sec - 40°C to + 75°C (- 30°C to + 50°C for Sensor) IP66 Up to 95% RH non-condensing 14-32 V dc< 4w 1 PPM T90~38 sec Ex II 2 G Exd iallC T4 Gb (Tamb -40C to +75C) SIL2 316 stainless steel Fault detection and will be signaled 3 wire 4-20mA current sink or source (Auto-Sense or manual selection); Without Relay OLED 128 x 64 pixels, yellow text on black background With 3 color LED indicator Three M20 |
| --- | --- |

Note: Ex M20 Cable gland, SS tag plate, Duct mounting kit with bolt & nuts installation accessories.

Part Number: XIQ-AA-S1-011-Z-Z-A (transmitter) + XIQ-IL (Sensor H2S 0-50 PPM)

Manufactured: Crowcon/UK

| Toxic Gas Detector (Building - HVAC) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | TGD-1101 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-1102 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-1103 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-1201 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-1202 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | TGD-1203 | Toxic Gas Detector | Zone2, IIB T4 | AI-IS-R | Conventional |

  - UV/IR Flame Detector - FL500

The FL500 Ultraviolet / Infrared Flame Detector delivers high speed flame detection with increased false alarm immunity in a compact design. The FL500 UV/IR Flame Detector monitors for radiation emitted by a flame in both the ultraviolet (UV) and infrared (IR) spectral ranges. This UV/IR combination provides a fast response time and increased false alarm immunity against sources of radiation for reliable protection.

| Sensor type Built in Self-Test Operating Temp Range/Response Field of View Spectral Response Indication Operating Voltage Typical Current Output Signal Power Consumption Enclosure Material Ingress Protection Weight Cable Entry Ex Marking Certification | UV/IR Yes – Every Two Minutes -55°C to +85°C 24 meter in less than 12 sec for standard Methane Flame 27 meter in 6 sec for standard n-Heptane Flame 130° Max. Conical UV (185 to 260nm) & IR (4.35 microns) Three color LED 20-36 Vdc 80 to 150mA 4-20mA and Relay 3W Max SS316 IP66 4 Kg 2x M25 Ex db IIC T5 Gb; Ex tb IIIC T100°C Db II 2 G D FM, IECEx, ATEX, SIL3, |
| --- | --- |

Note: Stainless Steel tag plate, Stainless Steel Sunshade, swivel mounting bracket, 2” pipe mounting Kit with bolts and nuts are included

Part Number: FL500-5-5-1-2-1-1-1-1

Manufacturer: General Monitors (Acquired by MSA) – USA

| Toxic Gas Detector (Process Area) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | FD-2001 | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-2002 | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-2003 | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-3001 | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4001A | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4002A | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4003A | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4004A | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4001B | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4002B | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4003B | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4004B | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4001C | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4002C | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4003C | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-4004C | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-6001 | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-6002 | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-8001 | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |
|  | FD-8002 | Flame Detector | Zone2, IIB T4 | AI-IS-R | Conventional |

## Outdoor Fire/Toxic/Flammable Gas Horn – E2S

The flameproof BexS110 alarm sounders are suitable for Zone 1, 2, 21 & 22 applications. Approved to IECEx, ATEX, Ex EAC and INMETRO standards. Available as SIL 1 and SIL 2 compliant.

| Wiring type Max Output No of Tones No of Stages Vol Control Ingress Protection: Humidity Operating voltage: Current Consumption ATEX Certificate: SIL Approval Enclosure Material: Cable Entry: Weight Color | 2 Wire 117 dB @ 1 meter 32 3 Stage, Negative or Positive Switching Yes IP66 0 to 95% RH non-condensing 24 V dc @24vdc 265mA Ex II 2 G Exdb eb llC T4 Gb (Tamb -50C to +55C) Yes, SIL2 IEC61508 Marine grade copper free LM6 Aluminium 2xM20 1Kg Red |
| --- | --- |

Note: Stainless steel tag plate, stainless steel Sunshade, Ex brass nickel plated M20 Cable gland, 2” pipe mounting kit including bolts and nots and mounting bracket are included.

Note1: Junction box (EX “e” type with 7 armored output cable) for each conventional Horns & related beacons and cable gland for connection to junction box are included in scope of supply.

Note2: Two different tones one for Flammable/Toxic gas detection (non-continuous) and one for fire detection (continuous). Each tone shall be activated by receiving dedicated signal.

Part Number: BEXS110DFDC024AN4A1R

Manufacturer: E2S / UK

Din-Rail Output AV Controller (5 A) - Discovery

The DIN-Rail Sounder Controller is used to control the operation of

a zone of externally powered sounders and to report their status to

Apollo compatible analogue control equipment. The Sounder Controller enables sounders to be operated continuously or be pulsed, one second on, one second off. Sounders may be operated individually or in groups and, whichever address mode has been applied, may be synchronized when in pulsed operation.

| Supply Voltage | 17V-28 V dc |
| --- | --- |
| Sounders operated | max 1.7 mA |
| Fault (yellow LED on) | 3.6 mA |
| Yellow LED enabled | 4.5 mA |
| Relay off | 3 mA at 35 V |
| Sounders and red LED on | 47 mA at 35 V |
| Sounder circuit voltage | 12 - 35 V dc |
| Sounder circuit current max | 5 A at 35 V dc (resistive load) |
| Operating temperature | -20ºC to +70ºC |
| Humidity (no condensing or icing) | 0% to 95% RH |
| IP Rating | IP20 |
| Radiated emissions | to BS EN 61000-6-3:2001 |
| Environmental | to BS EN 54 -18:2005 |
| Dimensions | 110 mm high x 107 mm wide x 20 mm deep |
| Weight | 95 g |
| Parameter | Value |
| Supply Voltage | 17V-28 V dc |

Note: The Din-Rail AV Controller includes a Exd Aluminum junction box and mounting accessories, allowing for the integration of output conventional devices into an Addressable Loop.

Part Number: 55000-182APO

Manufacturer: Apollo

| Horn |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
| Process Area |  |  |  |  |  |
|  | HN-1001 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-2001 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-3001 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-4001 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-4002 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-5001 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-6001 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-7002 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-8001 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | HN-9001 | Horn | Zone2, IIB T4 | DO-NIS-R | Conventional |
| Building |  |  |  |  |  |
|  | HN-1101 | Flame Detector | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | HN-1201 | Flame Detector | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | HN-1202 | Flame Detector | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | HN-1301 | Flame Detector | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | HN-1401 | Flame Detector | Zone2, IIB T4 | DO-NIS-R | Addressable |

## Outdoor Toxic Gas Blue Beacon – E2S

The flameproof BexBG21 21 Joule, 520 candela Xenon beacons are suitable for Zone 1, 2, 21 & 22 applications. Approved to IECEx, ATEX, Ex EAC and INMETRO standards. SIL1 compliant.

| Wiring type Energy Flash Rate Intensity Lens Color Lens Guard Ingress Protection Humidity Operating voltage: ATEX Certificate: SIL Approval Enclosure Material: Cable Entry: Weight Body Color | 2 Wire 21 J 1 Hz, 2 Hz Min 520 Cd Blue Yes IP66 0 to 95% RH non-condensing 24 V dc Ex II 2 G Exdb eb llC T3 Gb (Tamb -50C to +70C) Yes, SIL1 IEC61508 Marine grade copper free LM6 Aluminium 2xM20 2.65 Kg Red |
| --- | --- |

Note: Stainless steel tag plate, stainless steel Sunshade, Ex brass nickel plated M20 Cable gland, 2” pipe mounting kit including bolts and nots and mounting bracket are included.

Part Number:  BexBG21DPDC024AN1A1R/B

Manufacturer: E2S / UK

| Beacon - Blue |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
| Process Area |  |  |  |  |  |
|  | BB-1001 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-2001 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-3001 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-4001 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-4002 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-5001 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-6001 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-7002 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-8001 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BB-9001 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Conventional |
| Building |  |  |  |  |  |
|  | BB-1101 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BB-1201 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BB-1202 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BB-1301 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BB-1401 | Beacon - Blue | Zone2, IIB T4 | DO-NIS-R | Addressable |

## Outdoor Fire Red Beacon – E2S

The flameproof BexBG21 21 Joule, 520 candela Xenon beacons are suitable for Zone 1, 2, 21 & 22 applications. Approved to IECEx, ATEX, Ex EAC and INMETRO standards. SIL1 compliant.

| Wiring type Energy Flash Rate Intensity Lens Color Lens Guard Ingress Protection Humidity Operating voltage: ATEX Certificate: SIL Approval Enclosure Material: Cable Entry: Weight Body Color | 2 Wire 21 J 1 Hz, 2 Hz Min 520 Cd Red Yes IP66 0 to 95% RH non-condensing 24 V dc Ex II 2 G Exdb eb llC T3 Gb (Tamb -50C to +70C) Yes, SIL1 IEC61508 Marine grade copper free LM6 Aluminium 2xM20 2.65 Kg Red |
| --- | --- |

Note: Stainless steel tag plate, stainless steel Sunshade, Ex brass nickel plated M20 Cable gland, 2” pipe mounting kit including bolts and nots and mounting bracket are included.

Part Number:  BexBG21DPDC024AN1A1R/R

Manufacturer: E2S / UK

| Beacon -Red |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
| Process Area |  |  |  |  |  |
|  | BR-1001 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-2001 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-3001 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-4001 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-4002 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-5001 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-6001 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-7002 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-8001 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BR-9001 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Conventional |
| Building |  |  |  |  |  |
|  | BR-1101 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BR-1201 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BR-1202 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BR-1301 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BR-1401 | Beacon - Red | Zone2, IIB T4 | DO-NIS-R | Addressable |

| Beacon -Red |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
| Process Area |  |  |  |  |  |
|  | BR-1103 | Beacon - Red | Unclassified | DO-NIS-R | Addressable l |

## Outdoor Flammable Gas Yellow Beacon – E2S

The flameproof BexBG21 21 Joule, 520 candela Xenon beacons are suitable for Zone 1, 2, 21 & 22 applications. Approved to IECEx, ATEX, Ex EAC and INMETRO standards. SIL1 compliant.

| Wiring type Energy Flash Rate Intensity Lens Color Lens Guard Ingress Protection Humidity Operating voltage: ATEX Certificate: SIL Approval Enclosure Material: Cable Entry: Weight Body Color | 2 Wire 21 J 1 Hz, 2 Hz Min 520 Cd Yellow Yes IP66 0 to 95% RH non-condensing 24 V dc Ex II 2 G Exdb eb llC T3 Gb (Tamb -50C to +70C) Yes, SIL1 IEC61508 Marine grade copper free LM6 Aluminium 2xM20 2.65 Kg Red |
| --- | --- |

Note: Stainless steel tag plate, stainless steel Sunshade, Ex brass nickel plated M20 Cable gland, 2” pipe mounting kit including bolts and nots and mounting bracket are included.

Part Number:  BexBG21DPDC024AN1A1R/Y

Manufacturer: E2S / UK

| Beacon - Yellow |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
| Process Area |  |  |  |  |  |
|  | BY-1001 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-2001 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-3001 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-4001 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-4002 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-5001 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-6001 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-7002 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-8001 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
|  | BY-9001 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Conventional |
| Building |  |  |  |  |  |
|  | BY-1101 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BY-1201 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BY-1202 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BY-1301 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Addressable |
|  | BY-1401 | Beacon - Yellow | Zone2, IIB T4 | DO-NIS-R | Addressable |

Din-Rail Output AV Controller (5 A) - Discovery

The DIN-Rail Sounder Controller is used to control the operation of

a zone of externally powered sounders and to report their status to

Apollo compatible analogue control equipment. The Sounder Controller enables sounders to be operated continuously or be pulsed, one second on, one second off. Sounders may be operated individually or in groups and, whichever address mode has been applied, may be synchronized when in pulsed operation.

| Supply Voltage | 17V-28 V dc |
| --- | --- |
| Sounders operated | max 1.7 mA |
| Fault (yellow LED on) | 3.6 mA |
| Yellow LED enabled | 4.5 mA |
| Relay off | 3 mA at 35 V |
| Sounders and red LED on | 47 mA at 35 V |
| Sounder circuit voltage | 12 - 35 V dc |
| Sounder circuit current max | 5 A at 35 V dc (resistive load) |
| Operating temperature | -20ºC to +70ºC |
| Humidity (no condensing or icing) | 0% to 95% RH |
| IP Rating | IP20 |
| Radiated emissions | to BS EN 61000-6-3:2001 |
| Environmental | to BS EN 54 -18:2005 |
| Dimensions | 110 mm high x 107 mm wide x 20 mm deep |
| Weight | 95 g |
| Parameter | Value |
| Supply Voltage | 17V-28 V dc |

Note: The Din-Rail AV Controller includes a Ex d Aluminum junction box and mounting accessories, allowing for the integration of output conventional devices into an Addressable Loop.

Part Number: 55000-182APO

Manufacturer: Apollo

## Addressable Safe Area Flashing Beacon (Red) – XP95

The Open-Area Alarm Devices are loop-powered, wall

mounted devices designed for use in open areas and can be

connected to any XP95, Discovery or Core Protocol system.

The range includes sounders, Visual indicators and Sounder

Visual indicators all designed to fit a common mounting base.

Open-Area Alarm Devices

Product Information. Three tones on standard devices; Apollo, Slow-whoop and DIN all of which comply with EN 54-3

| Tube power Lamp type Current Body Color Lens Color Power supply Cable entry type IP Wiring Operating temperature Weight Material | 2J Xenon 333μA @ 24 VDC Red Red 24 VDC 2xM20 Addressable flasher safe area IP65 2 wire -25 to 70°C 0.25 Kg Flame retardant polycarbonate |
| --- | --- |

Note: Stainless Steel Tag plate, non-Ex Cable gland and installation accessories are included.

Part Number: 55000-009

Manufacturer: Apollo/UK

| Beacon-Red (Building) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | BR-1103 | Beacon - Red | Safe Area | DO-NIS-R | Addressable |

## H2 Gas Detector -Xgard IQ

XgardIQ is an intelligent and versatile gas detector and transmitter compatible with Crowcon's full range of sensor technologies. Available fitted with a variety of flammable, toxic or oxygen gas sensors.

Providing analogue 4-20mA and RS-485 Modbus signals as standard, The 316 stainless steel are available with three M20 or1/2"NPT cable entries.

| Wiring type Sensor Type: Detection Range: Expected operating life Accuracy Linearity Zero drift: Stabilization time: Operating Temperature: Ingress Protection: Humidity: Operating voltage: Resolution: Response Time: ATEX Certificate: SIL rating Enclosure Material: Self-diagnostic Electrical Output: Display Cable Entry: | 3 wire sink or source Pellistor – Hydrogen (H2) 0-100% LEL >36 Months < ±3% of full scale (-30ºC to +60ºC) < ±1.5% of full-scale 1% per month 15 sec - 40°C to + 75°C IP66 Up to 95% RH non-condensing 14-32 V dc< 4w 0.1 PPM T90~15 sec Ex II 2 G Exd iallC T4 Gb (Tamb -40C to +75C) SIL2 316 stainless steel Fault detection and will be signaled 3 wire 4-20mA current sink or source (Auto-Sense or manual selection); Relay Module, HART comms enabled OLED 128 x 64 pixels, yellow text on black background With 3 color LED indicator Three M20 |
| --- | --- |

Note1: Ex M20 Cable gland, Collector Cone, Stainless steel tag plate, pipe mounting kit including bolts and nots are included.

Part Number: XIQ-ZZ-S1-011-H-R-A (transmitter) + XIQ-AF (sensor, Hydrogen)

Manufactured: Crowcon/UK

| Beacon-Red (Building) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | HGD-1101 | Hydrogen Gas Detector | Zone1, IIC T4 | AI-IS-R | Conventional |
|  | HGD-1102 | Hydrogen Gas Detector | Zone1, IIC T4 | AI-IS-R | Conventional |

## Outdoor Manual Call Point – E2S

The BexCP3-BG break glass manual call points are designed for the harshest of environments and approved for Zone 1, 2, 21 and 22 explosion proof hazardous areas for the control of fire and gas alarm systems. SIL2 compliant to IEC61508 (2010).

| Wiring type Switch rating Operating Temperature: Ingress Protection: Humidity: Operating voltage: ATEX Certificate: SIL Approval Enclosure Material: Electrical Output: Cable Entry: Weight Color Detection Principle Test Key | 2 Wire 30 v DC Max Current 5 A - 40°C to + 70°C IP66 0 to 95% RH non-condensing 24 V dc Ex II 2 G Exdb eb llC T6 Gb (Tamb -40C to +70C) Yes, SIL2 IEC61508 Marine grade copper free LM6 Aluminium Digital Contact SPDT 3xM20 0.8 Kg RAL3000 Red Lift the flap and break the glass, Latch Type, Dual Action, equipped with opening key for test, maintenance and reset Yes |
| --- | --- |

Note: Stainless steel tag plate, stainless steel Sunshade, Ex brass nickel plated M20 Cable gland, 2” pipe mounting kit including bolts and nots and EOL are included.

Part Number: BEXCP3ABGSSLAP1A1RN24

Manufacturer: E2S / UK

DIN-Rail Mini Switch Monitor Module – XP95

The XP95 Marine DIN-Rail Mini Switch Monitor Module is a miniature interface with an entirely new housing. The unit is designed to fit into equipment with limited space or mounted within an enclosure such as a manual call point.

Part Number: 55000-760APO

Manufacturer: Apollo

Note1:  Exe Junction Box, EOL resistor, SS Tag Plate and Mounting Accessories are included.

Note2: The mini switch Apollo comes with a junction box that enables the addition of input conventional devices to an Addressable Loop.

| Manual Call Point – Conventional Hazardous Area |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
| Process Area |  |  |  |  |  |
|  | MAC-1001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-1002 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-2001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-2002 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-2003 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-3001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-4001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-4002 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-5001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-5002 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-6001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-6002 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-7001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-7002 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-8001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-8002 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-9001 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | MAC-9002 | Manual Call Point | Zone2, IIB T4 | DI-NIS-R | Conventional |
| Building |  |  |  |  |  |
|  | MAC-1101 | Manual Call Point | EEx”d” Zone2, IIB T4 | - | Addressable |
|  | MAC-1201 | Manual Call Point | EEx”d” Zone2, IIB T4 | - | Addressable |
|  | MAC-1203 | Manual Call Point | EEx”d” Zone2, IIB T4 | - | Addressable |
|  | MAC-1301 | Manual Call Point | EEx”d” Zone2, IIB T4 | - | Addressable |
|  | MAC-1401 | Manual Call Point | EEx”d” Zone2, IIB T4 | - | Addressable |

## Addressable Safe Area Manual Call Point-Discovery

The Waterproof Addressable Manual Call Point has been designed to operate on a loop of intelligent fire detection devices and when activated interrupts the polling cycle for a very fast response. The Waterproof Addressable Manual Call Point is available with and without isolator. It is intended for outdoor applications or areas where water ingress or high humidity is a problem.

| Type Supply voltage Protocol Protocol voltage Current powerup Current Normal Current alarm Operating temperature Humidity Vibrating impact and shock IP Approval and standards Dimension Weight LED indicator Color Cable entry Operation function Reset | Addressable manual call point for safe area 17-28 VDC Discovery, XP95, Core protocol 5-9 V peak to Peak 1 ma@24 VDC 100µA @ 24 VDC 4 ma @24VDC -30°C to +70°C 0% to 95%RH EN 54-11 IP67 EN 54-11, CPR, BOSEC, ESC, FG, SBSC, 114mm height x 114mm width x 74mm depth 325 g Yes Red 3xM20 Push the Resettable element (Latch Type without need to replacing the glass) With Reset key |
| --- | --- |

Note: Stainless Steel tag plate, Non-Ex Cable gland, Test key and mounting installation accessory are included

Part Number: 58200-950 APO

Manufacturer: Apollo /UK

| No | Tag | Description | Area Classification | I/O Type (Addre./Conv.) |
| --- | --- | --- | --- | --- |
|  | MAC-1102 | Manual Call Point | Unclassified | Addressable |
|  | MAC-1103 | Manual Call Point | Unclassified | Addressable |
|  | MAC-1104 | Manual Call Point | Unclassified | Addressable |
|  | MAC-1105 | Manual Call Point | Unclassified | Addressable |
|  | MAC-1202 | Manual Call Point | Unclassified | Addressable |
|  | MAC-1302 | Manual Call Point | Unclassified | Addressable |

## Linear Heat Detector FT88R- Signaline

Signaline Fixed Temperature Linear Heat Detector (Signaline FT) detects a buildup of heat anywhere along its length. When any point along the length of the cable reaches a predetermined temperature, an alarm is initiated. Signaline FT is available in four different temperature settings and two outer cover options making the Signaline FT suitable for use in a very wide range of applications

| Model Signaline Alarm temperature Max ambient temp. Conductor resistance Max voltage Dielectric withstand Tensile strength Overall diameter Weight Outer sheath material Colour Approvals | FT-88R 88°C (190°F) 70°C (158°F) 0.19Ω/M or 0.0579Ω/FT @20°C 42Vdc or 30Vac (UL) 500Vdc 1700 N/mm² Minimum bend radius 75mm 3.5mm 12kg/500M PVC White FM, UL, cUL, KFI |
| --- | --- |

Note1: Ex “e” Aluminum junction box, M20-Os Cable gland, EOL resistor and installation accessory are in our scope of supply.

Part number: FT-88R

Manufacture: Signaline/UK

DIN-Rail Mini Switch Monitor Module – XP95

The XP95 Marine DIN-Rail Mini Switch Monitor Module is a miniature interface with an entirely new housing. The unit is designed to fit into equipment with limited space or mounted within an enclosure such as a manual call point.

Part Number: 55000-760APO

Manufacturer: Apollo

Note1: The mini switch Apollo comes with a Ex “e” junction box that enables the addition of input conventional devices to an Addressable Loop.

| Manual Call Point – Safe Area |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
| Process Area |  |  |  |  |  |
|  | LHD-7001 | Linear Heat Detector | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | LHD-7002 | Linear Heat Detector | Zone2, IIB T4 | DI-NIS-R | Conventional |
|  | LHD-1201 | Linear Heat Detector | Zone2, IIB T4 | DI-NIS-R | Addressable |
|  | LHD-1202 | Linear Heat Detector | Zone2, IIB T4 | DI-NIS-R | Addressable |
|  | LHD-1203 | Linear Heat Detector | Zone2, IIB T4 | DI-NIS-R | Addressable |

## Addressable Smoke Detector- Discovery

The Discovery Optical Detector has a white molded polycarbonate case with wind-resistant smoke inlets. The two indicator LEDs are red in alarm. Within the case is a printed circuit board which, on one side, has the light-proof chamber with integral gauze surrounding the optical measuring system and, on the other, the signal processing and communications electronics.

| Analogue Value Nominal | 4 |
| --- | --- |
| Analogue Value | 23 +0/-4 |
| Alarm Level Analogue Value | 55 |
| Chamber Type | Chevron |
| Protocol Voltage | 5 to 9V peak to peak |
| Power-Up Surge Current | 1mA |
| Maximum Power-Up Time | 10 seconds |
| Status Indicator - Alarm | Red |
| Quiescent Current | 440μA |
| Quiescent Current Tested At | 24V dc |
| Alarm Current (At 24 Volts) | 3.4mA |
| Humidity | 0% to 95% (no condensation or icing) |
| Operating Temperature | -40 to 70°C |
| IP Rating Value | IP44 |
| Standards | EN 54-7 |
| Approvals | SBSC ,AFNOR ,BOSEC ,CPR ,FG ,VdS - LPCB |
| Weight | 105g |
| Colour | White |
| Materials Housing | Flame Retardant Polycarbonate |
| Materials Terminals | Nickel plated stainless steel |
| Product Length | 42mm |
| Product Diameter | 100mm |
| Detection Principle | Photo-electric light scattering. |

Note: SS Tag plate, Plastic back box, non-Ex Cable gland, installation base and bolt & nuts included.

Part Number: Detector 58000-600APO

45681-210 (Base)

45681-204 (Back Box)

Manufacturer: Apollo /UK

| No | Tag | Description | Area Classification | I/O Type (Addre./Conv.) |
| --- | --- | --- | --- | --- |
|  | SD-1101 | Smoke Detector | Unclassified | Addressable |
|  | SD-1102 | Smoke Detector | Unclassified | Addressable |
|  | SD-1103 | Smoke Detector | Unclassified | Addressable |
|  | SD-1104 | Smoke Detector | Unclassified | Addressable |
|  | SD-1105 | Smoke Detector | Unclassified | Addressable |
|  | SD-1106 | Smoke Detector | Unclassified | Addressable |
|  | SD-1107 | Smoke Detector | Unclassified | Addressable |
|  | SD-1108 | Smoke Detector | Unclassified | Addressable |
|  | SD-1109 | Smoke Detector | Unclassified | Addressable |
|  | SD-1110 | Smoke Detector | Unclassified | Addressable |
|  | SD-1111 | Smoke Detector | Unclassified | Addressable |
|  | SD-1112 | Smoke Detector | Unclassified | Addressable |
|  | SD-1113 | Smoke Detector | Unclassified | Addressable |
|  | SD-1114 | Smoke Detector | Unclassified | Addressable |
|  | SD-1115 | Smoke Detector | Unclassified | Addressable |
|  | SD-1116 | Smoke Detector | Unclassified | Addressable |
|  | SD-1117 | Smoke Detector | Unclassified | Addressable |
|  | SD-1118 | Smoke Detector | Unclassified | Addressable |
|  | SD-1119 | Smoke Detector | Unclassified | Addressable |
|  | SD-1120 | Smoke Detector | Unclassified | Addressable |
|  | SD-1121 | Smoke Detector | Unclassified | Addressable |
|  | SD-1122 | Smoke Detector | Unclassified | Addressable |
|  | SD-1123 | Smoke Detector | Unclassified | Addressable |
|  | SD-1124 | Smoke Detector | Unclassified | Addressable |
|  | SD-1125 | Smoke Detector | Unclassified | Addressable |
|  | SD-1126 | Smoke Detector | Unclassified | Addressable |
|  | SD-1127 | Smoke Detector | Unclassified | Addressable |
|  | SD-1128 | Smoke Detector | Unclassified | Addressable |
|  | SD-1129 | Smoke Detector | Unclassified | Addressable |
|  | SD-1130 | Smoke Detector | Unclassified | Addressable |
|  | SD-1131 | Smoke Detector | Unclassified | Addressable |
|  | SD-1132 | Smoke Detector | Unclassified | Addressable |
|  | SD-1133 | Smoke Detector | Unclassified | Addressable |
|  | SD-1134 | Smoke Detector | Unclassified | Addressable |
|  | SD-1135 | Smoke Detector | Unclassified | Addressable |
|  | SD-1136 | Smoke Detector | Unclassified | Addressable |
|  | SD-1201 | Smoke Detector | Unclassified | Addressable |
|  | SD-1202 | Smoke Detector | Unclassified | Addressable |
|  | SD-1203 | Smoke Detector | Unclassified | Addressable |
|  | SD-1204 | Smoke Detector | Unclassified | Addressable |
|  | SD-1301 | Smoke Detector | Unclassified | Addressable |
|  | SD-1302 | Smoke Detector | Unclassified | Addressable |
|  | SD-1303 | Smoke Detector | Unclassified | Addressable |
|  | SD-1304 | Smoke Detector | Unclassified | Addressable |
|  | SD-1401 | Smoke Detector | Unclassified | Addressable |
|  | SD-1402 | Smoke Detector | Unclassified | Addressable |
|  | SD-1403 | Smoke Detector | Unclassified | Addressable |

Remote LED Indicator – Apollo

The MiniDisc Remote Indicator is a light-weight, compact, red LED indicator for use in fire protection systems. The MiniDisc remote indicator is only 20mm high and 80mm in diameter. It comprises two parts—the base which is installed onto a wall or soffit and the lid which is fitted to the base with a bayonet lock.

| Voltage A and C point Maximum current B and C Operating Temperature Detector range Connection Standard and Approval Dimension Material Ingress Protection Cable entry Installation method | 5-36 V DC 25 mA -10°C to +60°C Orbis , Series65 VNIIPO, CNBOP,KAZAKSTHAN 80 mm diameter x 20 mm high White flame retardant polycarbonate IP67 M20 Inside backbox |
| --- | --- |

Note: Stainless Steel tag plate, installation accessories and back box are included.

Part Number: 53832-070

Manufacturer: Apollo/UK

| Remote LED Indicator for false ceiling and floor |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
| Building |  |  |  |  |  |
|  | SD-1103 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1105 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1106 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1107 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1109 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1111 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1113 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1116 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1117 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1119 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1203 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1204 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1301 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1302 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1303 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |
|  | SD-1304 | Remote LED Indicator | Unclassified | DI-NIS-R | Addressable |

## Alarm Bell – Apollo (klaxon)

The Fire Bell is a motorized bell designed for fire alarm applications. Its low current consumption and universally recognizable alarm sound makes it an ideal choice for many alarm systems.

Designed for ease of installation, it features a robust steel gong.

- Low current consumption

- Universally recognizable sound

- Diode polarized

- Approved to EN54-3

| Ingress Protection Operating Temperature Sound level Current Gong size Construction Color Humidity Power supply | IP33 -10ºC to +55ºC Up to 95 dB @ 1meter 20 ma 6” Steel Red 90% RH 24 V DC |
| --- | --- |

Note: SS Tag plate and installation accessories are included.

Part Number: 29600-400

Manufacturer: Apollo (Klaxon) / UK

| Bell (Building) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | BL-1101 | Bell | Unclassified | DO-NIS-R | Addressable |

## Explosion Proof Heat Detector – Oggioni

TMP2 series conventional heat detectors, includes an electronic circuit for signal conditioning generated by the transducer. The electrical signal of the transducer, is transformed effectively into an engineered output performance giving different interface solutions.

TMP2 detectors are particularly suitable in very dangerous environmental conditions such as in the presence of corrosive elements or condensing steams. TMP2 detectors comply with the specific response and environmental test requirements of the European standard. EN54-5 CPD certification pending. Certified ATEX II 2 G EEx-d IIC T6.

| Connection Sensor | 2 wire Semi-conductor |
| --- | --- |
| Approval | ATEX II 2G Ex d IIC T6 |
| Protection Degree | IP65 (Probe IP67) |
| Short-term repeatability | ±2% FSD 60 min. |
| Long-term repeatability | ±3% FSD 3 months. |
| Accuracy (linearity) | ±1% FSD |
| EMC Approval | EN61000-4 |
| Operating temperature | -20 to 110 °C |
| Humidity for Storage and Operation | 90% R.H. n.c. |
| Supply Voltage | 10-30 Vdc |
| Supply current | About 20/30 uA in normal conditions and > 20 mA in alarm conditions. Supply fuse 50 mA |
| Connection | 2 conductors cable |
| Cable Entry | 2x1/2" |
| Overall dimensions | 170x100x70 mm |
| Weight Heat classification Self-reset Storage temp Storage life | 150 g Static and rate of rise Auto reset type -40 to 85°C 10 years |
| Life time | 7 years |
| Power consumption | 20/30 uA in normal conditions > 20 mA in alarm |

Note: EOL resistor, Exd JB, Stainless Steel Tag Plate and Mounting Accessories are included.

Part Number: TMP2-TO-B-R-1-A

Manufacturer: Oggioni / Italy

| Ex Heat Detector |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type | I/O Type (Addre./Conv.) |
|  | HD-1101 | Heat Detector | Zone1, IIC T4 | DI-NIS-R | Conventional |
|  | HD-1102 | Heat Detector | Zone1, IIC T4 | DI-NIS-R | Conventional |

## Addressable Heat Detector-Discovery

The Discovery Heat Detector uses a single thermistor to sense

the air temperature at the detector position. The thermistor

is connected in a resistor network, which produces a voltage

output dependent on temperature. The design of the resistor

network, together with the processing algorithm in the microcontroller,gives an approximately linear characteristic from10ºC to 80ºC.

| Analogue Value | 23 +4/-0 |
| --- | --- |
| Alarm Level Analogue Value | 55 |
| Chamber Type | Chevron |
| Heat Classification | A1R |
| Protocol Voltage | 5 to 9V peak to peak |
| Power-Up Surge Current | 1mA |
| Maximum Power-Up Time | 10 seconds |
| Status Indicator - Alarm | Red |
| Quiescent Current | 400μA |
| Quiescent Current Tested At | 24V dc |
| Sampling Frequency | +L2 Loop in & out positive |
| Alarm Current (At 24 Volts) | 3.5mA |
| Humidity | 95% to 0% (no condensation or icing) |
| Operating Temperature | -40 to 70°C |
| IP Rating Value | IP44 |
| - Conformance EN 54-5 |  |
| Standards | - EN 54-7 |
| Approvals | - FG, SBSC, BOSEC, CPR, LPCB - VdS |
| Weight | 105g |
| Color | White |
| Materials Housing | Flame Retardant Polycarbonate |
| Product Dimension (Wo/Base) | 100 mm diameter x 42 mm height |
| Detection Principle | - Temperature sensitive resistance |

Note: Stainless steel Tag plate, Plastic back box, non-Ex Cable gland, 1X IS Barrier for Battery Room, installation base and bolt & nuts included.

Part Number: 58000-400APO

45681-210 (Base)

45681-204 (Back Box)

Manufacturer: Apollo/UK

| Addressable Heat detector |  |  |  |  |
| --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type (Addre./Conv.) |
|  | HD-1301 | Heat Detector | Unclassified | Addressable |

Remote LED Indicator - Apollo

The MiniDisc Remote Indicator is a light-weight, compact, red LED indicator for use in fire protection systems. The MiniDisc remote indicator is only 20mm high and 80mm in diameter. It comprises two parts—the base which is installed onto a wall or soffit and the lid which is fitted to the base with a bayonet lock.

| Voltage A and C point Maximum current B and C Operating Temperature Detector range Connection Standard and Approval Dimension Material Ingress Protection Cable entry Installation method | 5-36 V DC 25 mA -10°C to +60°C Orbis , Series65 VNIIPO, CNBOP,KAZAKSTHAN 80 mm diameter x 20 mm high White flame retardant polycarbonate IP67 M20 Inside backbox |
| --- | --- |

Note: Stainless steel tag plate, installation accessories and back box are included.

Part Number: 53832-070

Manufacturer: Apollo/UK

| Remote LED indicator for false ceiling |  |  |  |  |
| --- | --- | --- | --- | --- |
| No | Tag | Description | Area Classification | I/O Type (Addre./Conv.) |
|  | HD-1301 | Heat Detector | Unclassified | Addressable |

.

# Special Tools

## Gas Calibration Kit

Calibration and test Kit for Calibration and maintenance of flammable gas detector.

This includes:

| - 1x Cylinder 110 Liter, 1000PSI, 2.5% Methane in Air Calibration Gas - 1x Cylinder 110 Liter, 1000PSI, 2.2% H2 in Air Calibration Gas - 1x Cylinder 110 Liter, 1000PSI, 25 ppm H2S in Air Calibration Gas |  |
| --- | --- |
| - 1 x Xgard IQ calibration cap - 1 x IRmax calibration cap |  |
| - 1x Flow Regulator 0.5 Lit/Min |  |
| - 4-meter hoses |  |

## Flame Detector Tester – TL105

The TL105 is a battery-operated, explosion-proof test lamp designed specifically to test all General Monitors Flame Detectors including (but not limited to) the FL500, FL4000H, and any of the FL3100 Series detectors. The TL105 operates up to 35 feet from the flame detector

## Smoke/Heat Detector Tester– SOLO814

| Includes: - SOLO 330 Access Pole 6 meter - SOLO 424 Heat detector tester - SOLO 100 Access Pole - SOLO 200 Removal Tool - SOLO 610 Carrying Bag - SOLO 330 Aerosol Dispenser |  |
| --- | --- |

Part Number: SOLO814

Manufacturer: SOLO/UK

# Commissioning Spare Part

- 5 x   Glasses for all Manual Call Point

- 20 x EOL resistor for all related detectors

- 20 - meter LHD

# Optional Two Years Spare Parts

| Item | Description | % | Qty. |
| --- | --- | --- | --- |
|  | IR GAS DETECTOR- IRMAX CROWCON | 20% | 5 |
|  | IR GAS DETECTOR DUCT MOUNT – IRMAX CROWCON | 20% | 1 |
|  | TOXIC GAS DETECTOR – XGARD IQ CROWCON | 20% | 5 |
|  | TOXIC GAS DETECTOR DUCT MOUNT – XGARD IQ | 20% | 1 |
|  | UV/IR FLAME DETECTOR – FL500 MSA | 20% | 4 |
|  | EXPLOSION POOF SIREN ALARM SOUNDER – E2S | 10% | 1 |
|  | EXPLOSION PROOF BEACON (RED) –E2S | 10% | 1 |
|  | EXPLOSION PROOF BEACON (BLUE) –E2S | 10% | 1 |
|  | EXPLOSION PROOF BEACON (YELLOW) –E2S | 10% | 1 |
|  | ADDRESSABLE SAFE AREAR FLASHING BEACON (RED) – XP95 | 10% | 1 |
|  | HYDROGEN GAS DETECTOR- XGARD IQ | 20% | 1 |
|  | MANUAL CALL POINT EXD-E2S | 20% | 4 |
|  | ADDRESSABLE SAFE AREA MANUAL CALL POINT-DISCOVERY | 20% | 1 |
|  | LINEAR HEAT DETECTOR- SIGNALINE | 20% | 15 |
|  | ADDRESSABLE SMOKE DETECTOR- DISCOVERY | 20% | 10 |
|  | ALARM BELL – APOLLO (KLAXON) | 10% | 1 |
|  | EXPLOSION PROOF HEAT DETECTOR – OGGIONI | 20% | 1 |
|  | ADDRESSABLE HEAT DETECTOR-DISCOVERY | 20% | 1 |

# Site Supervision for Installation

Tima Kala Tehran engineers will attend in site for supervision, commissioning and test and this will take into account man/ day according to purchaser requirements.

# Optional Training

Training by Tima Kala Tehran engineers will be as follow items:

•	Design configuration assistance to CONTRACTOR

•	Operator training courses

•	Maintenance training courses

•	Site installation and commissioning support.

Note: It will take into account man / day

Training at Tima Kala Tehran office in Tehran is free of charge

# Deviation

We have the following deviation from project specification:

| No | Reference Doc | Item | Project Data sheet Specification | Tima Deviation |
| --- | --- | --- | --- | --- |
|  | Datasheet Rev-04 | All devices | Humidity 100 % RH | Humidity Max 95 % RH |
|  | Datasheet Rev-04 | IR Flammable gas detector - IRmax | Case Color: Red | Case Color: Stainless Steel |
|  | TCL-D01 Item 23 | IR Flammable gas detector - IRmax | 2 digital Auxiliary switches for L/H alarm signals | Analogue 4~20mA, High and low alarms can be transmitted as analog output (mA) signals to the control system. |
|  | Datasheet Rev-04 | Toxic Gas Detector – Xgard Bright | Response time 5 sec | Response time T90 ~ 38 sec Electrochemical sensors with response times under 5 seconds are not available. |
|  | Datasheet Rev-04 | UV/IR flame detector | M20 cable entry | 2 X 25mm cable entry |
|  | Datasheet Rev-04 | Hydrogen gas detector - Xgard Bright | Response time 5 sec | Response time 30 sec |
|  | Datasheet Rev-04 | Manual call point Exd | LED indicator | Not Applicable |
|  | Datasheet Rev-04 | Manual call point Exd | M20 cable entry | M25 cable entry |
|  | Datasheet Rev-04 | Manual call points Addressable | Aluminum body material | Polycarbonate |
|  | Datasheet Rev-04 | Linear Heat Detector | Temperature rises 8° C Per minutes | Fix Alarm Temperature |
|  | Datasheet Rev-04 | Linear Heat Detector | Weather proof available | Not available |
|  | Datasheet Rev-04 | Addressable smoke detector | IP54 | IP44 |
|  | Datasheet Rev-04 | Addressable smoke detector | Stainless steel Name plate material | Polycarbonate |
|  | Datasheet Rev-04 | Addressable smoke heat & detector - Discovery | Operating temperature -10 ºC to 90 ºC | Operating temperature -40°C to +70°C |
|  | Datasheet Rev-04 | Addressable smoke detector – Discovery | Aluminum body material | polycarbonate |
|  | TCL-D01 | Remote LED Indicator | IP54 | IP44 |
|  | Datasheet Rev-04 | Bell | Adjustable intensity | Not applicable |
|  | Datasheet Rev-04 | Bell | Selectable Tone | 1 tone |
|  | Datasheet Rev-04 | Bell | IP54 | IP33 |
|  | Datasheet Rev-04 | Addressable Heat Detector-Discovery | Aluminum body material | polycarbonate |

# Clarification

- Please clarify the T90 response time for gas detectors.

- Addressable Smoke and heat detector with an aluminum body does not exist in the market

- Generally, the IP 54 rating not applicable for bell, addressable smoke and heat detector, remote LED indicator.

- Please clarify about note item 9 on horn

- Please clarify the requirements for the IS barrier for LHD cable

- Please specify whether the tank for LHD installation is a fixed roof or a floating roof.

- Should the required bell be addressable or conventional?

# Commercial Proposal

## Fire and Gas Devices

| Item | Description | Qty. | Unit Price Euro | Total Price Euro |
| --- | --- | --- | --- | --- |
|  | Flammable Gas Detector- IRmax | 26 | --- | --- |
|  | Flammable Gas Detector (Duct Mount)- IRmax Remote Display | 6 | --- | --- |
|  | Toxic Gas Detector- Xgard IQ | 26 | --- | --- |
|  | Toxic H2S Gas Detector (Duct Mount)– Xgard IQ | 6 | --- | --- |
|  | UV/IR Flame Detector - FL500 | 20 | --- | --- |
|  | Outdoor Fire/Toxic/Flammable Gas Horn – E2S | 15 | --- | --- |
|  | Outdoor Toxic Gas Blue Beacon – E2S | 15 | --- | --- |
|  | Outdoor Fire Red Beacon – E2S | 15 | --- | --- |
|  | Outdoor Flammable Gas Yellow Beacon – E2S | 15 | --- | --- |
|  | Addressable Safe Area Flashing Beacon (Red) – XP95 | 1 | --- | --- |
|  | H2 Gas Detector -Xgard IQ | 2 | --- | --- |
|  | Outdoor Manual Call Point – E2S | 23 | --- | --- |
|  | Addressable Safe Area Manual Call Point-Discovery | 6 | --- | --- |
|  | Linear Heat Detector FT88R- Signaline | 75m | --- | --- |
|  | Addressable Smoke Detector- Discovery | 47 | --- | --- |
|  | Alarm Bell – Apollo (klaxon) | 1 | --- | --- |
|  | Explosion Proof Heat Detector – Oggioni | 2 |  |  |
|  | Addressable Heat Detector-Discovery | 1 |  |  |
|  | Total | --- |  | Euro |

Note: Please note that above mentioned prices are including all required accessories such as mounting kit, junction boxes, tag plate, bolts and nuts, ETC.

## Special Tools

| Item | Description | Qty. | Unit Price EUR |  | Total Price EUR |
| --- | --- | --- | --- | --- | --- |
| 1 | Gas Calibration Kit | 1 Set |  | --- | --- |
| 2 | Smoke/Heat Detector Tester Kit SOLO814 | 1 Set |  | --- | --- |
| 3 | Flame Detector Tester | 1 Set |  | --- | --- |
|  | Total | --- |  | Euro |  |

## Commissioning Spare Part

| Item | Description | Qty. | Unit Price EUR |  | Total Price EUR |
| --- | --- | --- | --- | --- | --- |
| 1 | Commissioning Spare Part As Described above in section 5 | 1 Set |  | --- | --- |
|  | Total | --- |  | Euro |  |

## Optional SAT, Site Supervision and Training

| Item | Description | Qty. | Unit Price EUR |  | Total Price EUR |
| --- | --- | --- | --- | --- | --- |
| 1 | Site supervision | Man/day |  | --- | ---- |
| 2 | Training | Man/day |  | --- | ---- |

## Optional Two Years Spare Parts

| Item | Description | Qty. | Unit Price Euro | Total Price Euro |
| --- | --- | --- | --- | --- |
|  | IR GAS DETECTOR- IRMAX CROWCON | 5 | --- | --- |
|  | IR GAS DETECTOR DUCT MOUNT – IRMAX CROWCON | 1 | --- | --- |
|  | TOXIC GAS DETECTOR – XGARD IQ CROWCON | 5 | --- | --- |
|  | TOXIC GAS DETECTOR DUCT MOUNT – XGARD IQ | 1 | --- | --- |
|  | UV/IR FLAME DETECTOR – FL500 MSA | 4 | --- | --- |
|  | EXPLOSION POOF SIREN ALARM SOUNDER – E2S | 1 | --- | --- |
|  | EXPLOSION PROOF BEACON (RED) – E2S | 1 | --- | --- |
|  | EXPLOSION PROOF BEACON (BLUE) – E2S | 1 | --- | --- |
|  | EXPLOSION PROOF BEACON (YELLOW) – E2S | 1 | --- | --- |
|  | ADDRESSABLE SAFE AREAR FLASHING BEACON (RED) – XP95 | 1 | --- | --- |
|  | HYDROGEN GAS DETECTOR- XGARD IQ | 1 | --- | --- |
|  | MANUAL CALL POINT EXD-E2S | 4 | --- | --- |
|  | ADDRESSABLE SAFE AREA MANUAL CALL POINT-DISCOVERY | 1 | --- | --- |
|  | LINEAR HEAT DETECTOR- SIGNALINE | 15 | --- | --- |
|  | ADDRESSABLE SMOKE DETECTOR- DISCOVERY | 10 | --- | --- |
|  | ALARM BELL – APOLLO (KLAXON) | 1 | --- | --- |
|  | EXPLOSION PROOF HEAT DETECTOR – OGGIONI | 1 | --- | --- |
|  | ADDRESSABLE HEAT DETECTOR-DISCOVERY | 1 | --- | --- |
|  | Total | --- |  | Euro |

## Total Commercial offer

| Item | DESCRIPTION | Qty. | Unit Price EUR | Total Price EUR |
| --- | --- | --- | --- | --- |
|  | Fire and Gas Devices | 1 Set | --- | --- |
|  | Special Tools | 1 Set | --- | --- |
|  | Commissioning Spare Parts | 1 Set | --- | --- |
|  | FAT | 1 Set | FREE | FREE |
| Total |  |  | --- EUR |  |

# Terms

# Tender Validity

30 Days after bid date

# Payment

30% in advance, 65% after delivery and 5% after final book

All payments in IRR based on SANA rate on day of payment.

# Delivery Time

7 months after advance payment

# Delivery terms

DDP Site

# Declaration of Guaranty

18 months

# After Sales Service

10 Years