Hirgan Energy

Deviation List

Your Ref:   BK-GCS-PEDCO-120-IN-MR-0007_D01

Our Ref: 	0327008-Tec-Rev01

| Prepared: | Approved: | Date: |
| --- | --- | --- |
| Sina Sadeghi | Peyman Tajbakhsh | 13 November 2024 |

| No | Reference Doc | Item | Project Data sheet Specification | Tima Deviation |
| --- | --- | --- | --- | --- |
|  | Datasheet Rev-04 | All devices | Humidity 100 % RH | Humidity Max 95 % RH |
|  | Datasheet Rev-04 | IR Flammable gas detector - IRmax | Case Color: Red | Case Color: Stainless Steel |
|  | TCL-D01 Item 23 | IR Flammable gas detector - IRmax | 2 digital Auxiliary switches for L/H alarm signals | Analogue 4~20mA, High and low alarms can be transmitted as analog output (mA) signals to the control system. |
|  | Datasheet Rev-04 | Toxic Gas Detector – Xgard Bright | Response time 5 sec | Response time T90 ~ 38 sec Electrochemical sensors with response times under 5 seconds are not available. |
|  | Datasheet Rev-04 | UV/IR flame detector | M20 cable entry | 2 X 25mm cable entry |
|  | Datasheet Rev-04 | Hydrogen gas detector - Xgard Bright | Response time 5 sec | Response time 30 sec |
|  | Datasheet Rev-04 | Manual call point Exd | LED indicator | Not Applicable |
|  | Datasheet Rev-04 | Manual call point Exd | M20 cable entry | M25 cable entry |
|  | Datasheet Rev-04 | Manual call points Addressable | Aluminum body material | Polycarbonate |
|  | Datasheet Rev-04 | Linear Heat Detector | Temperature rises 8° C Per minutes | Fix Alarm Temperature |
|  | Datasheet Rev-04 | Linear Heat Detector | Weather proof available | Not available |
|  | Datasheet Rev-04 | Addressable smoke detector | IP54 | IP44 |
|  | Datasheet Rev-04 | Addressable smoke detector | Stainless steel Name plate material | Polycarbonate |
|  | Datasheet Rev-04 | Addressable smoke heat & detector - Discovery | Operating temperature -10 ºC to 90 ºC | Operating temperature -40°C to +70°C |
|  | Datasheet Rev-04 | Addressable smoke detector – Discovery | Aluminum body material | polycarbonate |
|  | TCL-D01 | Remote LED Indicator | IP54 | IP44 |
|  | Datasheet Rev-04 | Bell | Adjustable intensity | Not applicable |
|  | Datasheet Rev-04 | Bell | Selectable Tone | 1 tone |
|  | Datasheet Rev-04 | Bell | IP54 | IP33 |
|  | Datasheet Rev-04 | Addressable Heat Detector-Discovery | Aluminum body material | polycarbonate |