## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2748 |  |  | Transmital Date: 8/18/2024
Document Title: Electrical Typical Schematic Diagrams For MV panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0305-EL-TR-2748 |  |  | Transmital Date: 8/19/2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DG-0001_D07 |  |  | CRS Status: | C1
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Voltage and current sample for capacitor bank shall be shown. |  | BK-SUR-ENG-ELE-00-02786 | 2022-01-23 | به مانند مدرک دیاگرام تک خطی این نوت اضافه گردید |  |  | Noted and Closed.
2 | Voltage level of voltage sample for transducer shall be modified on page 4 (10V shall be modified to 110V). |  | BK-SUR-ENG-ELE-00-02786 | 2022-01-23 | به ولتاژ 110 ولت تغییر پیدا کرد |  |  | Noted and Closed.
3 | 86 lock out relay in protection unit shall be deleted on page 5. (Separeted lock out relay has been considered) |  | BK-SUR-ENG-ELE-00-02786 | 2022-01-23 | اعمال گردید |  |  | Noted and Closed.
4 | ESD Trip have not been shown. It shall be clarified. |  | BK-SUR-ENG-ELE-00-02786 | 2022-01-23 | این تریپ نیز نشان داده شد. |  |  | Noted and Closed.
5 | No Comments. |  | BK-SUR-ENG-ELE-00-03606 | 2022-03-15
6 | No Comments. NOTE: Control circuit correct functionality is not correct and shall be rechecked and modified in the Manufacturer drawings |  | BK-SUR-ENG-ELE-01-04237 | 2022-05-11 | بعد از نهایی سازی قرارداد تابلو، سازنده موظف به تعیین عملکرد صحیح مدارات می باشد که در آن زمان مورد بررسی قرار خواهد گرفت. |  |  | Noted and Closed.
7 | According to our meeting date 1401.05.04 and NISOC comment, the feeder type F5 shall be modified base on motor type feeder and all require protection for fire water motor shall be considered in protection relay base on electrical design criteria. |  | BK-SUR-ENG-ELE-01-05282 | 2022-07-30 | مطابق با صورتجلسه در دفتر کارفرمای محترم (ذینفع اصلی پروژه)، کامنتها اعمال گردید. |  |  | Noted and Closed.
8 | Schematic and SLD shall be matched to each other for example 94 has not been shown in schematic or protection relay for fire water pump shall be considered base on above mentioned comment, etc. |  | BK-SUR-ENG-ELE-01-05282 | 2022-07-30 | مطابق با صورتجلسه در دفتر کارفرمای محترم (ذینفع اصلی پروژه)، کامنتها اعمال گردید. |  |  | Noted and Closed.
9 | Circuit breaker status shall be visible from RCP, therefor circuit breakers status shall be sent to both DCS and RCP. |  | BK-SUR-ENG-ELE-01-05282 | 2022-07-30 | مطابق با صورتجلسه در دفتر کارفرمای محترم (ذینفع اصلی پروژه)، کامنتها اعمال گردید. |  |  | See below item 13.
10 | Location of motor differential protection CTs at the motor side is not correct. Shall be modified based on SLD. |  | BK-SUR-ENG-ELE-01-05282 | 2022-07-30 | مطابق با صورتجلسه در دفتر کارفرمای محترم (ذینفع اصلی پروژه)، کامنتها اعمال گردید. |  |  | Noted and Closed.
11 | Re. Note 5, one voltmeter has been requested for 3.3kV but in the schematic diagram type C5, there is no PT and voltmeter. |  | BK-SUR-ENG-ELE-01-05282 | 2022-07-30 | مطابق با صورتجلسه در دفتر کارفرمای محترم (ذینفع اصلی پروژه)، کامنتها اعمال گردید. |  |  | Noted and Closed.
12 | Capacitive voltage indicator to be considered for MV feeders. |  | BK-SUR-ENG-ELE-01-05282 | 2022-07-30 | مطابق با صورتجلسه در دفتر کارفرمای محترم (ذینفع اصلی پروژه)، کامنتها اعمال گردید. |  |  | Noted and Closed.
13 | See above item 9: There is conflict between this document and latest revision of RCP wiring diagram from point of view Close/Open command between RCP and C5 type feeder (Fire water pump transformer). It shall be rechecked and modified and Matched with electrical I/O list |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | مدرک لیست سیگنال به روز گردیده است و با آخرین ویرایش مدرک تیپیکال یکسان شده است. |  |  | Noted and Closed.
14 | According to MOM date 1401/08/10&11 at NISOC office following items shall be rechecked and modified: |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31
14-1 | According to NISOC letter NO. 222997 date 1401/06/22, the protection of fire water transformer shall be considered base on IPS-E-EL-100 and electrical design criteria for example Function 64 shall be added. (Mom, Item 3) |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | استاندارد IPS-E-EL-100 مورد بازنگری قرار گرفت و حفاظت های مورد نیاز از جمله 64REF اضافه گردید. |  |  | Noted and Closed.
14-2 | RTD cable shall be modified to 12T1.5 instead of 2X18X1.5. (Mom, Item 7) |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | کابل RTD اصلاح گردید. |  |  | Noted and Closed.
14-3 | LCS for fire water electro pump shall be shown. (Mom, Item 7) |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | LCS اضافه گردید. |  |  | Noted and Closed.
14-4 | According to MOM, the F&G contact shall be added for start circuit as remote start. |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | اضافه گردید. |  |  | Noted and Closed.
15 | This document shall be matched to latest revision of electrical I/O list document form point of metering signals transfer method view. For example in this document the transfer mehode has been considered hardwire, but in electrical I/O list has been considered serial link. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | تمهیدات لازم به صورت لینک سریال در مدرک دیده شده است. |  |  | Noted and Closed.
16 | According to our telephone conversation UCP and IRP contact in open/close circuit of compressor outgoing type C3 feeder shall be rechecked and finalized base on Vendor I/O list. Meanwhile this document shall be matched to latest revision of electrical I/O list document form point of purpose signal view. For example in this document the the UCP and IRP contact has been shown in open/close circuit of motor compressor outgoing for feeder type C3 while in electrical I/O list has not been considered. |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | مدرک لیست سیگنال به روز گردیده است و با آخرین ویرایش مدرک تیپیکال یکسان شده است. |  |  | Noted and Closed.
17 | Heater has not been shown for Fire water electro pump. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | اضافه گردید. |  |  | Noted and Closed.
18 | Any changes shall be highlited by revision mark and cloud. |  | BK-SUR-ENG-ELE-01-06558 | 2022-12-31 | تمامی تغییرات به صورت ابرک نشان داده شده است. |  |  | Noted and Closed.
19 | No Comment. Note: A note as title "Protective relays and Measuring unit shall be equipped with RS 485 to send signals by serial link.", shall be added to document. |  | BK-SUR-ENG-ELE-02-07680 | 2023-05-23 | اعمال شده است.
20 | No Comment. |  | BK-SUR-ENG-ELE-02-08524 | 2023-10-02 | سپاسگزارم.
21 | No Comment. Note 1: 64RE for FIRE WATER PUMP transformer is not necessary and can be deleted during purchasing engineering. (Shall be matched with MV SLD) Note 2: Accuracy class of all CTs shall be based on related IPS standard durring Purchasing engineering. |  | BK-SUR-ENG-ELE-03-09465 | 2024-08-20 | مطابق درخواست NISOC در کامنت شیت TR2781-287305 برای فیدر FIRE WATER PUMP دو عدد ترانس جریان مطابق جریان NGR برای حفاظت 51G , 64REF در نظر گرفته شده است. همچنین کلاس CT مطابق استاندارد IPS می باشد..
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 20-Aug-24 |  |  |  |  | Date: