## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0003 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR ESD SYSTEMS نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | OCT.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | SEP.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708969
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0003 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X |  |  | X |  |  |  | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | X |  | X |  |  |  | 71
8 | X | X | X |  | X |  |  |  | 72
9 |  | X | X |  | X |  |  |  | 73
10 |  | X | X |  | X |  |  |  | 74
11 |  |  | X |  | X |  |  |  | 75
12 |  |  | X | [5 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0003 | D03
REFERENCES:
|  | Symbol & Legend For PFD and P&ID | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0001_D04
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0002_D07
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0003_D07
|  | P&ID - Slug Catcher System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0004_D07
|  | P&ID - Gas Compression Inlet Knock Out Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D07
|  | P&ID - 1st Stage Gas Compression Suction Drums | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D07
|  | P&ID - 1st Stage Gas Compression Compressors | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D07
|  | P&ID - 1st Stage Gas Compression Air Coolers | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0008_D07
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D07
|  | P&ID - 2nd Stage Gas Compression Compressors | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D06
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011_D07
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0012_D07
|  | P&ID - Gas Compression Dehydration Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0013_D07
|  | P&ID - Lean Glycol Storage Tank | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D07
|  | P&ID - Instrument & Plant Air System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D07
|  | P&ID - Nitrogen Generation System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0016_D07
|  | P&ID - Close Drain System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0017_D07
|  | P&ID - Corrosion Inhibitor Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0018_D07
|  | P&ID - Methanol Injection Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0019_D06
|  | P&ID - LP Flare System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0020_D07
|  | P&ID - Oily Water Sewer | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0021_D05
|  | P&ID - Fuel Gas System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0022_D07
|  | P&ID - Diesel Oil System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0023_D07
|  | P&ID - Potable Water System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0024_D06
|  | P&ID - Glycol Sump Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D07
|  | P&ID - Fire Water Network | [7 empty] | BK-GCS-PEDCO-120-SA-PI-0001_D04
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [7 empty] | BK-GCS-PEDCO-120-SA-PI-0002_D02
|  | P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [7 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D04
|  | Data Sheets For ESD Console/F&G Matrix Panel | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017_D00
|  | ESD Level Hierarchy | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003_D02
|  | Electrical I/O Signal List | [7 empty] | BK-GCS-PEDCO-120-EL-LI-0005-D03
NOTES:
| NOTE 1 : |  | ALL OF ANALOGE TRANSMITTER SHALL BE CONSIDERED INTRINSICALLY SAFE (EEXIA) & ALL OF DIGITAL TRANSMITTER ARE NON INTRINSICALLY SAFE (EEXD).
| NOTE 2 : |  | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".
| NOTE 3 : |  | ESD EQUIPMENT & ALL OF EQUIPMENT THAT IS ASSIGNED IN A CONTROL LOOP, ARE REDUNDANT.
| NOTE 4 : |  | ALL I/Os REQUIRED FOR ESD SHALL BE SHOWN IN DCS BY SERIAL LINK.
D03

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0003 | D03
ESD I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 59 | 72 | NOTES 1,2,3 | 70.8
| 2 |  | AI-IS-NR |  | IS | NR |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3 | 0
| 3 |  | AO-IS-R |  | IS | R |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3 | 0
| 4 |  | AO-IS-NR |  | IS | NR |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3 | 0
| 5 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 39 | 47 | NOTES 1,2,3 | 46.8
| 6 |  | DI-NIS-NR |  | NIS | NR |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3 | 0
| 7 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 89 | 107 | NOTES 1,2,3 | 106.8
| 8 |  | DO-NIS-NR |  | NIS | NR |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3 | 0
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
D03

## IO List for ESD System
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 |  | IN |  | LI |  | 0003 |  |  | D03
I/O List For ESD System
ITEM | ESD LEVEL | TAG | DESCRIPTION | SERVICE |  | P&ID |  |  | I/O TYPE |  | FROM |  | TO |  | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[15 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL | IND/STA | COM.
1 | 1 | ESOV-2101 | Solenoid Valve | To Inlet K.O. Drum (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
2 | 1 | ESOV-2102 | Solenoid Valve | To Slug Catcher (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
3 | 1 | PIT-2111 | Pressure Indicator Transmitter | Gas Transfer Pipe |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
4 | 1 , 3 | LIT-2112 | Level Indicator Transmitter | Slug Catcher Drum (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
5 | 3 | PIT-2115 | Pressure Indicator Transmitter | From P-2101A/B to BINAK Production Unit |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
6 | 3 | PIT-2114A | Pressure Indicator Transmitter | Slug Pump P-2101A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
7 | 3 | PIT-2114B | Pressure Indicator Transmitter | Slug Pump P-2101B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
8 | 3 | PIT-2116A | Pressure Indicator Transmitter | Slug Pump P-2101A Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
9 | 3 | PIT-2116B | Pressure Indicator Transmitter | Slug Pump P-2101B Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
10 | 3 | ESD-P-2111-A | Trip Command | Slug Pump (P-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
11 | 3 | ESD-P-2111-B | Trip Command | Slug Pump (P-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
12 | 3 | ESOV-2112 | Solenoid Valve | From P-2101A/B to BINAK Production Unit (After Slug Pumps) |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
13 | 3 | ESOV-2113 | Solenoid Valve | From V-2105 to Closed Drain header |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
14 | 1 | LIT-2117 | Level Indicator Transmitter | Inlet Knock Out Drum (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
15 | 3 | LIT-2118 | Level Indicator Transmitter | Inlet Knock Out Drum (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
16 | 1 | PIT-2116 | Pressure Indicator Transmitter | Slug Catcher Output |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
17 | 1A | BSOV-2110 | Solenoid Valve | Inlet K.O. Drum to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Added
18 | 2 | ESOV-2121A | Solenoid Valve | 1st Stage Gas Compression Suction Train A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
19 | 2 , 3 | LIT-2122A | Level Indicator Transmitter | 1st Stage Gas Compression Suction Drum Train #A (V-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
20 | 3 | ESOV-2122A | Solenoid Valve | Outlet Line of Suction Drum Train A 1st Stage |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
21 | 2 | ESOV-2121B | Solenoid Valve | 1st Stage Gas Compression Suction Train B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
22 | 2 , 3 | LIT-2122B | Level Indicator Transmitter | 1st Stage Gas Compression Suction Drum Train #B (V-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
23 | 3 | ESOV-2122B | Solenoid Valve | Outlet Line of Suction Drum Train B 1st Stage |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
24 | 2 | ESOV-2121C | Solenoid Valve | 1st Stage Gas Compression Suction Train C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
25 | 2 , 3 | LIT-2122C | Level Indicator Transmitter | 1st Stage Gas Compression Suction Drum Train #C (V-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
26 | 3 | ESOV-2122C | Solenoid Valve | Outlet Line of Suction Drum Train C 1st Stage |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
27 | 2 | PIT-2122A | Pressure Indicator Transmitter | Train A Pressure in Suction of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 Modified
28 | 2 | PIT-2125A | Pressure Indicator Transmitter | Train A Pressure in discharge of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
29 | 2 | TIT-2124A | Temperature Indicator Transmitter | Train A Temperature in discharge of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
30 | 2A | ESDR2A-C-2101-A | Trip Command | Compressor Train A (C-2101-A) Trip With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
31 | 2 | ESDR2-C-2101-A | Trip Command | Compressor Train A (C-2101-A) Trip Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
32 | 2A | ESD2A-C-2101-A | Trip Alarm (Request) | Compressor Train A (C-2101-A) Trip With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
33 | 2 | ESD2-C-2101-A | Trip Alarm (Request) | Compressor Train A (C-2101-A) Trip Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
34 | 2A | BSOV-2122A | Solenoid Valve | 1st Stage Gas Compressor (C-2101-A) Bypass Valve |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
35 | 2 | PIT-2122B | Pressure Indicator Transmitter | Train B Pressure in Suction of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 Modified
36 | 2 | PIT-2125B | Pressure Indicator Transmitter | Train B Pressure in discharge of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
37 | 2 | TIT-2124B | Temperature Indicator Transmitter | Train B Temperature in discharge of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
38 | 2A | ESDR2A-C-2101-B | Trip Command | Compressor Train B (C-2101-B) Trip With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
39 | 2 | ESDR2-C-2101-B | Trip Command | Compressor Train B (C-2101-B) Trip Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
40 | 2A | ESD2A-C-2101-B | Trip Alarm (Request) | Compressor Train B (C-2101-B) Trip With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
41 | 2 | ESD2-C-2101-B | Trip Alarm (Request) | Compressor Train B (C-2101-A) Trip Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
42 | 2A | BSOV-2122B | Solenoid Valve | 1st Stage Gas Compressor (C-2101-B) Bypass Valve |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
43 | 2 | PIT-2122C | Pressure Indicator Transmitter | Train C Pressure in Suction of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 Modified
44 | 2 | PIT-2125C | Pressure Indicator Transmitter | Train C Pressure in discharge of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
45 | 2 | TIT-2124C | Temperature Indicator Transmitter | Train C Temperature in discharge of 1st Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
46 | 2A | ESDR2A-C-2101-C | Trip Command | Compressor Train C (C-2101-C) Trip With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
47 | 2 | ESDR2-C-2101-C | Trip Command | Compressor Train C (C-2101-C) Trip Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
48 | 2A | ESD2A-C-2101-C | Trip Alarm (Request) | Compressor Train C (C-2101-C) Trip With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
49 | 2 | ESD2-C-2101-C | Trip Alarm (Request) | Compressor Train C (C-2101-C) Trip Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
50 | 2A | BSOV-2122C | Solenoid Valve | 1st Stage Gas Compressor (C-2101-C) Bypass Valve |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
51 | 3 | VSHH-2121A | Vibration Switch | From 1st Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
52 | 3 | VSHH-2122A | Vibration Switch | From 1st Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
53 | 3 | ESD-AE-2101-A-1 | Trip Command | From 1st Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
54 | 3 | ESD-AE-2101-A-2 | Trip Command | From 1st Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
55 | 2 | TIT-2125A | Temperature Indicator Transmitter | Train A Temperature after 1st Stage Gas Compressor Air Cooler |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
56 | 3 | VSHH-2121B | Vibration Switch | From 1st Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
57 | 3 | VSHH-2122B | Vibration Switch | From 1st Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
58 | 3 | ESD-AE-2101-B-1 | Trip Command | From 1st Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
59 | 3 | ESD-AE-2101-B-2 | Trip Command | From 1st Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
60 | 2 | TIT-2125B | Temperature Indicator Transmitter | Train B Temperature after 1st Stage Gas Compressor Air Cooler |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
61 | 3 | VSHH-2121C | Vibration Switch | From 1st Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
62 | 3 | VSHH-2122C | Vibration Switch | From 1st Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
63 | 3 | ESD-AE-2101-C-1 | Trip Command | From 1st Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
64 | 3 | ESD-AE-2101-C-2 | Trip Command | From 1st Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
65 | 2 | TIT-2125C | Temperature Indicator Transmitter | Train C Temperature after 1st Stage Gas Compressor Air Cooler |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
66 | 2 , 3 | LIT-2132A | Level Indicator Transmitter | 2nd Stage Gas Compressor Suction Drum Train #A (V-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X | X |  | X | X |  |  | D03 Modified
67 | 2A | BSOV-2134A | Solenoid Valve | From V-2102-A to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
68 | 3 | ESOV-2131A | Solenoid Valve | From V-2102-A to Closed Drain header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
69 | 2 , 3 | LIT-2132B | Level Indicator Transmitter | 2nd Stage Gas Compressor Suction Drum Train #A (V-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X | X |  | X | X |  |  | D03 Modified
70 | 2A | BSOV-2134B | Solenoid Valve | From V-2102-B to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
71 | 3 | ESOV-2131B | Solenoid Valve | From V-2102-B to Closed Drain header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
72 | 2 , 3 | LIT-2132C | Level Indicator Transmitter | 2nd Stage Gas Compressor Suction Drum Train #A (V-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X | X |  | X | X |  |  | D03 Modified
73 | 2A | BSOV-2134C | Solenoid Valve | From V-2102-C to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
74 | 3 | ESOV-2131C | Solenoid Valve | From V-2102-C to Closed Drain header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
75 | 2 | PIT-2131A | Pressure Indicator Transmitter | Train A Pressure in Suction of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
76 | 2 | PIT-2134A | Pressure Indicator Transmitter | Train A Pressure in discharge of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
77 | 2 | TIT-2134A | Temperature Indicator Transmitter | Train A Temperature in discharge of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
78 | 2 | PIT-2131B | Pressure Indicator Transmitter | Train B Pressure in Suction of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
79 | 2 | PIT-2134B | Pressure Indicator Transmitter | Train B Pressure in discharge of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
80 | 2 | TIT-2134B | Temperature Indicator Transmitter | Train B Temperature in discharge of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
81 | 2 | PIT-2131C | Pressure Indicator Transmitter | Train C Pressure in Suction of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
82 | 2 | PIT-2134C | Pressure Indicator Transmitter | Train C Pressure in discharge of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
83 | 2 | TIT-2134C | Temperature Indicator Transmitter | Train C Temperature in discharge of 2nd Stage of Compressor |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
84 | 3 | ESD-AE-2102-A-1 | Trip Command | From 2nd Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
85 | 3 | ESD-AE-2102-A-2 | Trip Command | From 2nd Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
86 | 3 | VSHH-2131A | Vibration Switch | From 2nd Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
87 | 3 | VSHH-2132A | Vibration Switch | From 2nd Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
88 | 2 | TIT-2136A | Temperature Indicator Transmitter | Train A Temperature after 2nd Stage Gas Compressor Air Cooler |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
89 | 2A | BSOV-2132A | Solenoid Valve | From AE-2102-A to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
90 | 2 | ESOV-2133A | Solenoid Valve | From AE-2102-A to Gas Compression Dicharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
91 | 3 | ESD-AE-2102-B-1 | Trip Command | From 2nd Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
92 | 3 | ESD-AE-2102-B-2 | Trip Command | From 2nd Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
93 | 3 | VSHH-2131B | Vibration Switch | From 2nd Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
94 | 3 | VSHH-2132B | Vibration Switch | From 2nd Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
95 | 2 | TIT-2136B | Temperature Indicator Transmitter | Train B Temperature after 2nd Stage Gas Compressor Air Cooler |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
96 | 2A | BSOV-2132B | Solenoid Valve | From AE-2102-B to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
97 | 2 | ESOV-2133B | Solenoid Valve | From AE-2102-B to Gs Compression Dicharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
98 | 3 | ESD-AE-2102-C-1 | Trip Command | From 2nd Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
99 | 3 | ESD-AE-2102-C-2 | Trip Command | From 2nd Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
100 | 3 | VSHH-2131C | Vibration Switch | From 2nd Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
101 | 3 | VSHH-2132C | Vibration Switch | From 2nd Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
102 | 2 | TIT-2136C | Temperature Indicator Transmitter | Train C Temperature after 2nd Stage Gas Compressor Air Cooler |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 Modified
103 | 2A | BSOV-2132C | Solenoid Valve | From AE-2102-C to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
104 | 2 | ESOV-2133C | Solenoid Valve | From AE-2102-B to Gs Compression Dicharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
105 | 1A | BSOV-2141 | Solenoid Valve | From Methanol header to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
106 | 1 | ESOV-2142 | Solenoid Valve | From V-2103 to Dehdration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
107 | 1 | ESOV-2143 | Solenoid Valve | From V-2103 to Dehdration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
108 | 1 , 3 | LIT-2142 | Level Indicator Transmitter | Gas Compression discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
109 | 3 | ESOV-2144 | Solenoid Valve | From V-2103 to Closed Drain header |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
110 | 1A | BSOV-2151 | Solenoid Valve | Dehydration Package (PK-2101) to LP Flare header |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
111 | 3 | ESD-PK-2101 | Trip Command | Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | BMS-DH-2150 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
112 | 3 | ESD3-PK-2101 | Trip Alarm (Request) | Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | DI-NIS-R |  | BMS-DH-2150 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
113 | 3 | LIT-2161 | Level Indicator Transmitter | Lean Glycol Storage Tank (TK-2102) |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
114 | 3 | ESD-P-2161-A | Trip Command | Glycol transfer Pump (P-2103A) |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
115 | 3 | ESD-P-2161-B | Trip Command | Glycol transfer Pump (P-2103B) |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
116 | 3 | PIT-2202 | Pressure Indicator Transmitter | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER Package (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
117 | 3 | ESOV-2201 | Solenoid Valve | INSTRUMENT & PLANT AIR SYSTEM header (PK-C-2203A/B , PK-DR-2203A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
118 | 3 | ESD-PK-C-2203 A | Trip Command | Air Compressor Package (PK-C-2203 A) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | PK-AC-2203-A |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
119 | 3 | ESD-PK-C-2203 B | Trip Command | Air Compressor Package (PK-C-2203 B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | PK-AC-2203-B |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
120 | 1A | PIT-2201A | Pressure Indicator Transmitter | From Air Drayer Package (PK-DR-2203) to Instrument Header |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
121 | 1A | PIT-2201B | Pressure Indicator Transmitter | From Air Drayer Package (PK-DR-2203) to Instrument Header |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
122 | 1A | PIT-2201C | Pressure Indicator Transmitter | From Air Drayer Package (PK-DR-2203) to Instrument Header |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
123 | 1 | PIT-2211 | Pressure Indicator Transmitter | Nitrogen Reciever Output |  | BK-GCS-PEDCO-120-PR-PI-0016 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
124 | 3 | PIT-2222A | Pressure Indicator Transmitter | Closed Drain Drum Pump P-2202A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
125 | 3 | PIT-2222B | Pressure Indicator Transmitter | Closed Drain Drum Pump P-2202B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
126 | 3 | ESD-P-2221-A | Trip Command | Closed Drain Drum Pump (P-2202-A) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
127 | 3 | ESD-P-2221-B | Trip Command | Closed Drain Drum Pump (P-2202-B) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
128 | 1A | ESD-P-2222-A | Trip Command | Sump Pump (P-2203-A) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
129 | 1A | ESD-P-2222-B | Trip Command | Sump Pump (P-2203-B) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
130 | 1 | ESD-PK-2207 | Trip Command | Corrosion Inhibitor Package (PK-2207A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 |  |  | DO-NIS-R |  | ESD |  | PK-2207 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
131 | 3 | ESD-P-2251A | Trip Command | LP Flare K.O. Drum Pump (P-2201 A) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
132 | 3 | ESD-P-2251B | Trip Command | LP Flare K.O. Drum Pump (P-2201 B) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
133 | 1 | LIT-2252A | Level Indicator Transmitter | LP Flare K.O. Drum (V-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
134 | 1 | LIT-2252B | Level Indicator Transmitter | LP Flare K.O. Drum (V-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
135 | 1 | LIT-2252C | Level Indicator Transmitter | LP Flare K.O. Drum (V-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
136 | 3 | PIT-2251A | Pressure Indicator Transmitter | LP Flare K.O. Drum Pump (P-2201 A) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
137 | 3 | PIT-2251B | Pressure Indicator Transmitter | LP Flare K.O. Drum Pump (P-2201 B) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
138 | 3 | LIT-2253 | Level Indicator Transmitter | LP Flare K.O. Drum (V-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
139 | 1A | FST-2201 | Start Command | LP Flare Stack Package (Air Blower) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | LOCAL MCC OR PDP IS IN VENDOR SCOPE OF WORK |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
140 | 3 | ESOV-2272 | Solenoid Valve | From Inlet K.O. Drum (V-2105) to V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
141 | 3 | LIT-2272 | Level Indicator Transmitter | Fuel Gas K.O. Drum (V-2205) |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
142 | 3 | ESOV-2271 | Solenoid Valve | From Inlet K.O. Drum (V-2105) to Closed Drain header |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
143 | 1A | ESD-P-2293 | Trip Command | Glycol Drain Pump (P-2104) |  | BK-GCS-PEDCO-120-PR-PI-0025 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
144 | 1 | ESOV-3201 | Solenoid Valve | PIPELINE: From Dehydration (PK-2101) to PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
145 | 1 | PIT-3201A | Pressure Indicator Transmitter | PIPELINE: From Dehydration (PK-2101) to PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
146 | 1 | PIT-3201B | Pressure Indicator Transmitter | PIPELINE: From Dehydration (PK-2101) to PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
147 | 1 | PIT-3201C | Pressure Indicator Transmitter | PIPELINE: From Dehydration (PK-2101) to PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 Modified
148 | 0 | ESD R0-UPS-A | Trip Alarm (Request) | 110V AC UPS, CH01 Fault Status |  | __ |  |  | DI-NIS-R |  | ELECTRICAL (UPS CHARGER) |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
149 | 0 | ESD R0-UPS-B | Trip Alarm (Request) | 110V AC UPS, CH02 Fault Status |  | __ |  |  | DI-NIS-R |  | ELECTRICAL (UPS CHARGER) |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
150 | 0 | ESDR 0-F&G | Trip Alarm (Request) | Confirmed Flammable Gas in HVAC Intake (Command From F&G) |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
151 | 0 | ESD 0-EL1A | Isolation Command | 11/0.4 KV SWGR-Transformer Feeder-Q2 (1) (Emergency + Normal Power Isolation) |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL MV SWG (IRP) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
152 | 0 | ESD 0-EL1B | Isolation Command | 11/0.4 KV SWGR-Transformer Feeder-Q2 (2) (Emergency + Normal Power Isolation) |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL MV SWG (IRP) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
153 | 0 | ESD 0-EL2A | Isolation Command | 110V AC UPS, CH01 Isolation Command |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (UPS CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
154 | 0 | ESD 0-EL2B | Isolation Command | 110V AC UPS, CH02 Isolation Command |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (UPS CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
155 | 1A | ESDR 1A-F&G | Trip Alarm (Request) | Confirmed Flammable/ Toxic Gas in Process Area (Command From F&G) |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
156 | 1 | ESDR 1-DC | Trip Alarm (Request) | DC Charger Failure |  | __ |  |  | DI-NIS-R |  | ELECTRICAL (UPS CHARGER) |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
157 | 1 | ESDR 1-PCS | Trip Alarm (Request) | PCS Failure |  | __ |  |  | DI-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
158 | 1 | ESDR 1-FLR | Trip Alarm (Request) | Flare Ignition Failure |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
159 | 1A | ESD 1A-F&G | Trip Alarm (Request) | Confirmed Fire in Fire Zone (Process) Area (Command From F&G) |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
160 | 0 | ESD0-LAMP | Signal Lamp | Total Plant Shut Down With Automatic Depressurizing (ESD0) |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
161 | 1A | ESD1A-LAMP | Signal Lamp | Process Emergency Shut Down With Depressurizing (ESD1A) |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
162 | 2A | ESD2A-A-LAMP | Signal Lamp | Train A Shut Down With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
163 | 2A | ESD2A-B-LAMP | Signal Lamp | Train B Shut Down With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
164 | 2A | ESD2A-C-LAMP | Signal Lamp | Train C Shut Down With Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
165 | --- | LAMP-ESD-INH | Signal Lamp | ESD INHIBIT LAMP |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
166 | --- | LAMP-ESD-RST | Signal Lamp | ESD RESET LAMP |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
167 | 1 | ESD1-LAMP | Signal Lamp | Process Emergency Shut Down Without Depressurizing (ESD1) |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
168 | 2 | ESD2-A-LAMP | Signal Lamp | Train A Shut Down Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
169 | 2 | ESD2-B-LAMP | Signal Lamp | Train B Shut Down Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
170 | 2 | ESD2-C-LAMP | Signal Lamp | Train C Shut Down Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
171 | 0 | ESD0-PB | Emergency Stop Push Button | Total Plant Shut Down With Automatic Depressurizing (ESD0) P.B. |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
172 | 1A | ESD1A-PB | Emergency Stop Push Button | Process Emergency Shut Down With Depressurizing (ESD1A) P.B. |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
173 | 2A | ESD2A-A-PB | Emergency Stop Push Button | Train A Shut Down With Depressurizing (ESD2A-A) P.B. |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
174 | 2A | ESD2A-B-PB | Emergency Stop Push Button | Train B Shut Down With Depressurizing (ESD2A-B) P.B. |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
175 | 2A | ESD2A-C-PB | Emergency Stop Push Button | Train C Shut Down With Depressurizing (ESD2A-C) P.B. |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
176 | --- | ESD-INH-SEL | Selector Switch With key | ESD INHIBIT SELECTOR SWITCH |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
177 | --- | ESD-RST-PB | Momentary Yellow Push Button | Alarm and Causes Reset Push Button |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
178 | 1 | ESD1-PB | Emergency Stop Push Button | Process Emergency Shut Down Without Depressurizing (ESD1) P.B. |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
179 | 2 | ESD2-A-PB | Emergency Stop Push Button | ESD CONSOL (Train A Shut Down PB Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
180 | 2 | ESD2-B-PB | Emergency Stop Push Button | ESD CONSOL (Train B Shut Down PB Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
181 | 2 | ESD2-C-PB | Emergency Stop Push Button | ESD CONSOL (Train C Shut Down PB Without Depressurizing |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
182 | - | ESDI 0-EX | Trip Alarm (Request) | ESD 0 STATUS from Existing System |  | __ |  |  | DI-NIS-R |  | EXISTING SYSTEM |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 Modified
183 | - | ESDI 0- NEW | Trip Command | ESD 0 to Existing System (Just Status) |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
| 1 | ESDI 1- NEW | Trip Command | ESD 1 Command to Existing System |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 Deleted
| 1A | ESDI 1A- NEW | Trip Command | ESD 1A Command to Existing System |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 Deleted
186 | 0 | ESD 0-EL3A | Isolation Command | 24 V DC UPS-002-CH01 Isolation Command |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
187 | 0 | ESD 0-EL3B | Isolation Command | 24 V DC UPS-002-CH02 Isolation Command |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
188 | 0 | ESD 0-EL4A | Isolation Command | 110V DC Charger-001-CH01 Isolation Command |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
189 | 0 | ESD 0-EL4B | Isolation Command | 110V DC Charger-001-CH02 Isolation Command |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 Modified
;
D03