## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL SYSTEM
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0002 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR CONTROL SYSTEM نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  | OCT.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D03 |  | DEC.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | SEP.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number:'F0Z-708968
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL SYSTEM
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0002 |  | D04
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 65
2 | X | X | X |  | X |  | X |  | 66
3 | X | X | X |  | X |  | X |  | 67
4 | X | X | X |  | X |  | X |  | 68
5 | X | X | X |  | X |  | X |  | 69
6 | X | X | X |  | X |  | X |  | 70
7 | X | X | X |  | X |  | X |  | 71
8 | X | X | X |  | X |  | X |  | 72
9 | X | X | X |  | X |  |  |  | 73
10 | X | X | X |  | X |  |  |  | 74
11 | X | X | X |  | X |  |  |  | 75
12 | X | X | X |  | X |  | X |  | 76
13 |  | X | X |  | X |  | X |  | 77
14 |  | X | X |  | X |  | X |  | 78
15 |  | X | X |  | X |  | X |  | 79
16 |  | X | X |  | X |  | X |  | 80
17 |  | X | X |  | X |  | X |  | 81
18 |  | X | X |  | X |  | X |  | 82
19 |  | X | X |  | X |  | X |  | 83
20 |  | X | X |  |  |  | X |  | 84
21 |  |  | X |  |  |  | X |  | 85
22 |  |  | X |  |  |  | X |  | 86
23 |  |  | X |  |  |  | X |  | 87
24 |  |  | X |  | X |  | X |  | 88
25 |  |  |  |  | X |  |  |  | 89
26 | [8 empty] | 90
27 | [6 empty] | X |  | 91
28 | [6 empty] | X |  | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL SYSTEM
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0002 | D04
REFERENCES:
|  | Symbol & Legend For PFD and P&ID | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0001_D04
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0002_D07
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0003_D07
|  | P&ID - Slug Catcher System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0004_D07
|  | P&ID - Gas Compression Inlet Knock Out Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D07
|  | P&ID - 1st Stage Gas Compression Suction Drums | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D07
|  | P&ID - 1st Stage Gas Compression Compressors | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D07
|  | P&ID - 1st Stage Gas Compression Air Coolers | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0008_D07
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D07
|  | P&ID - 2nd Stage Gas Compression Compressors | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D06
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011_D07
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0012_D07
|  | P&ID - Gas Compression Dehydration Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0013_D07
|  | P&ID - Lean Glycol Storage Tank | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D07
|  | P&ID - Instrument & Plant Air System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D07
|  | P&ID - Nitrogen Generation System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0016_D07
|  | P&ID - Close Drain System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0017_D07
|  | P&ID - Corrosion Inhibitor Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0018_D07
|  | P&ID - Methanol Injection Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0019_D06
|  | P&ID - LP Flare System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0020_D07
|  | P&ID - Oily Water Sewer | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0021_D05
|  | P&ID - Fuel Gas System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0022_D07
|  | P&ID - Diesel Oil System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0023_D07
|  | P&ID - Potable Water System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0024_D06
|  | P&ID - Glycol Sump Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D07
|  | P&ID - Fire Water Network | [7 empty] | BK-GCS-PEDCO-120-SA-PI-0001_D04
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [7 empty] | BK-GCS-PEDCO-120-SA-PI-0002_D02
|  | P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [7 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D04
|  | Data Sheets For ESD Console/F&G Matrix Panel | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017_D00
|  | ESD Level Hierarchy | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003_D02
|  | Electrical I/O Signal List | [7 empty] | BK-GCS-PEDCO-120-EL-LI-0005-D03
NOTES:
| NOTE 1 : |  | ALL OF ANALOUGE TRANSMITTERS SHALL BE CONSIDERED INTRINSICALLY SAFE (EEXIA) & ALL OF DIGITAL TRANSMITTERS ARE NON INTRINSICALLY SAFE (EEXD).
| NOTE 2 : |  | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".
| NOTE 3 : |  | ALL I/Os REQUIRED FOR DEHYDRATION PACKAGE (PK-2101) WILL BE ADDED TO THIS SUMMARY AS PER VENDOR DATA LATER.
| NOTE 4 : |  | AS MNIMUM 4 MODBUS COMMUNICATION CARDS WITH STORAGE CAPACITY OF 253 BYTES (+20 % SPARE) IN THIS SYSTEM SHALL BE USED (THIS CAPACITY SHALL BE FINILIZED BY PACKAGE VENDOR). A LIST OF MODBUS DATA WILL BE PROVIDED IN THIS DOCOMENT AFTAR OBTAINING FROM THE PACKAGE MANUFACTURERS. IN ADDITION TO COMMUNICATION BETWEEN ESD AND F&G WITH THE DCS SYSTEM SHALL BE THROUGH PROFIBUS SYSTEM THAT REQUIREMENTS BY DCS VENDOR WITH USABILITY FOR ESD AND F&G SYSTEMS MUST BE CONSIDERED.
| NOTE 5: |  | THIS TABLE IS SHOWN SIGNALS BETWEEN FIELD (OUT OF PACKAGE BATTERY LIMIT) AND UCP. OTHER SIGNALS THAT ARE RELATED TO INSIDE PACKAGE DEVICES/MOTORS, SHALL BE CONPLETED BY PACKAGE MANUFACTURER AS PER VENDOR P&ID THAT SHALL BE FINALIZED BY COMPRESSOR MANUFACTURE.
| NOTE 6 : |  | ALL ESD I/Os SHALL BE TRANSMITTED TO THE DCS SYSTEM BY SOFTWARE DATA-LINK.
| NOTE 7 : |  | ALL SERIAL DATA LINK OF THE PACKAGES WILL BE FINILIZED AFTER VENDOR DATA.
D04

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL SYSTEM
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0002 | D04
DCS I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 47 | 57 | NOTES 1,2,3 | 56.4
| 2 |  | AI-IS-NR |  | IS | NR |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 33 | 41 | NOTES 1,2,3 | 39.6
| 3 |  | AO-IS-R |  | IS | R |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 23 | 26 | NOTES 1,2,3 | 27.6
| 4 |  | AO-IS-NR |  | IS | NR |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3
| 5 |  | DI-NIS-NR |  | NIS | NR |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 182 | 219 | NOTES 1,2,3 | 218.4
| 6 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 2 | 3 | NOTES 1,2,3 | 2.4
| 6 |  | DO-NIS-NR |  | NIS | NR |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 73 | 88 | NOTES 1,2,3 | 87.6
NOTE 8 : The estimated I/O (No.100) for DEHYDRATION package shall be added to above DCS I/O summary.(refer to note 3).
UCP I/O SUMMERY COUNT (NOTE 5)
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 39 | 47 | NOTES 1,2,3 | 46.8
| 2 |  | AI-IS-NR |  | IS | NR |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3 | 0
| 3 |  | AO-IS-R |  | IS | R |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 3 | 4 | NOTES 1,2,3 | 3.6
| 4 |  | AO-IS-NR |  | IS | NR |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3 | 0
| 5 |  | DI-NIS-NR |  | NIS | NR |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 38 | 46 | NOTES 1,2,3 | 45.6
| 6 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 0 | 0 | NOTES 1,2,3 | 0
| 6 |  | DO-NIS-NR |  | NIS | NR |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 16 | 20 | NOTES 1,2,3 | 19.2
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
D04

## IO List for Control System
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL SYSTEM
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN |  | LI |  | 0002 |  |  | D04
I/O List For Control System
ITEM | TAG | DESCRIPTION | SERVICE |  | P&ID |  |  | I/O TYPE |  | FROM |  | TO |  | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[14 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL | IND/STA | COM.
1 | FCV-2101 | Flow Control Valve | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
2 | FIT-2101 | Flow Transmitter | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
3 | TIT-2102 | Flow Transmitter | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
4 | PIT-2102 | Pressure Transmitter | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X
5 | EZSC-2101 | ESDV Limit Switch Close | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
6 | EZSO-2101 | ESDV Limit Switch Open | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
7 | FCV-2102 | Flow Control Valve | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
8 | FIT-2102 | Flow Transmitter | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
9 | TIT-2104 | Temperature Transmitter | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
10 | PIT-2104 | Pressure Transmitter | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X
11 | EZSC-2102 | ESDV Limit Switch Close | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
12 | EZSO-2102 | ESDV Limit Switch Open | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
13 | ZA-2004A | PIG Signaller | TO PR-2002 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
14 | ZA-2004B | PIG Signaller | TO PR-2002 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
15 | ZA-2102B | PIG Signaller | TO PR-2002 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
16 | HSL-2003 | Hand Switch Local/Remot (MOV-2003) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
17 | XF-2003 | Fault Feedback (MOV-2003) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
18 | MZTO-2003 | Torque Limit Switch Open (MOV-2003) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
19 | MZTC-2003 | Torque Limit Switch Close (MOV-2003) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
20 | MZIO-2003 | Limit Switch Open (MOV-2003) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
21 | MZIC-2003 | Limit Switch Close (MOV-2003) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
22 | MSO-2003 | Valve Open Command (MOV-2003) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
23 | MSC-2003 | Valve Close Command (MOV-2003) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
24 | HSL-2004 | Hand Switch Local/Remot (MOV-2004) | GAS FROM GOLKHARI/TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
25 | XF-2004 | Fault Feedback (MOV-2004) | GAS FROM GOLKHARI/TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
26 | MZTO-2004 | Torque Limit Switch Open (MOV-2004) | GAS FROM GOLKHARI/TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
27 | MZTC-2004 | Torque Limit Switch Close (MOV-2004) | GAS FROM GOLKHARI/TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
28 | MZIO-2004 | Limit Switch Open Status (MOV-2004) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
29 | MZIC-2004 | Limit Switch Close Status (MOV-2004) | TO PR-2102 |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
30 | MSO-2004 | Valve Open Command (MOV-2004) | GAS FROM GOLKHARI/TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
31 | MSC-2004 | Valve Close Command (MOV-2004) | GAS FROM GOLKHARI/TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
32 | PIT-2112 | Pressure Indicator Transmitter | V-2104 |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
33 | PDIT-2111 | Diff. Pressure Indicator Transmitter | V-2104 |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
34 | LIT-2111 | Level Indicator Transmitter (DP) | V-2104 |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
35 | EZSO-2112 | Limit Switch Open | From P-2101A/B TO Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
36 | EZSC-2112 | Limit Switch Close | From P-2101A/B TO Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
37 | FIT-2111 | Flow Indicator Transmitter | From P-2101A/B TO Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
38 | FCV-2111 | Flow Control Valve | From P-2101A/B TO Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
39 | PIT-2114 | Pressure Indicator Transmitter | From P-2101A/B TO Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
40 | XL-2111A | Local / Remote Status | P-2101A |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
41 | XR-2111A | Running/Stop Status | P-2101A |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
42 | XF-2111A | Fault Status | P-2101A |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
43 | XSP-2111A | STOP Command | P-2101A |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
44 | XL-2111B | Local / Remote Status | P-2101B |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
45 | XR-2111B | Running/Stop Status | P-2101B |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
46 | XF-2111B | Fault Status | P-2101B |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
47 | XSP-2111B | STOP Command | P-2101B |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
48 | TIT-2112 | Temperature Indicator Transmitter | FROM SLUG CATCHER DRUM (V-2104) /Inlet Knock Out Drum (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
49 | PIT-2117 | Pressure Indicator Transmitter | Knock Out Drum (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
50 | PDIT-2112 | Diff. Pressure Indicator Transmitter | Knock Out Drum (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
51 | EZSO-2113 | Limit Switch Open | Outlet (V-2105) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
52 | EZSC-2113 | Limit Switch Close | Outlet (V-2105) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
| XZSO-2110 | Limit Switch Open | Outlet (V-2105) / To LP FLARE HEADER |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| XZSC-2110 | Limit Switch Close | Outlet (V-2105) / To LP FLARE HEADER |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| PSOV-2110 | Solenoid Valve | Outlet (V-2105) / To LP FLARE HEADER |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Deleted
53 | LIT-2119 | Level Indicator Transmitter | V-2105 |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
54 | LCV-2114 | Level Control Valve | Outlet (V-2105) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
55 | PIT-2121A | Pressure Indicator Transmitter | Outlet V-2101-A /to 1st Stage Compressore (C-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X
56 | PI-2121A | Pressure Control Valve | Outlet V-2101-A /to 1st Stage Compressore (C-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AO-IS-R |  | DCS |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
57 | PDIT-2121A | Diff. Pressure Indicator Transmitter | V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
58 | LIT-2121A | Level Indicator Transmitter | V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
59 | PSOV-2122A | Solenoid Valve | Outlet (V-2101-A) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
60 | XZSC-2122A | Limit Switch Close | Outlet (V-2101-A) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
61 | XZSO-2122A | Limit Switch Open | Outlet (V-2101-A) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
62 | PIT-2121B | Pressure Indicator Transmitter | Outlet V-2101-B /to 1st Stage Compressore (C-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X
63 | PI-2121B | Pressure Control Valve | Outlet V-2101-A /to 1st Stage Compressore (C-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AO-IS-R |  | DCS |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
64 | PDIT-2121B | Diff. Pressure Indicator Transmitter | V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
65 | LIT-2121B | Level Indicator Transmitter | V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
66 | PSOV-2122B | Solenoid Valve | Outlet (V-2101-B) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
67 | XZSC-2122B | Limit Switch Close | Outlet (V-2101-B) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
68 | XZSO-2122B | Limit Switch Open | Outlet (V-2101-B) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
69 | PIT-2121C | Pressure Indicator Transmitter | Outlet V-2101-C /to 1st Stage Compressore (C-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X
70 | PI-2121C | Pressure Control Valve | Outlet V-2101-A /to 1st Stage Compressore (C-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AO-IS-R |  | DCS |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
71 | PDIT-2121C | Diff. Pressure Indicator Transmitter | V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
72 | LIT-2121C | Level Indicator Transmitter | V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
73 | PSOV-2122C | Solenoid Valve | Outlet (V-2101-C) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
74 | XZSC-2122C | Limit Switch Close | Outlet (V-2101-C) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
75 | XZSO-2122C | Limit Switch Open | Outlet (V-2101-C) /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
76 | TIT-2121A | Temperature Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101A) /To C-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
77 | XSS-2124A | Start Permission | 1ST Gas Compressore Train#A (C-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-NR |  | UCP-GC-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
78 | XSS-2123A | Start Command | 1ST Gas Compressore Train#A (C-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
79 | XSP-2123A | Stop Command | 1ST Gas Compressore Train#A (C-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
80 | BZSO-2122A | Limit Switch Open | C-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
81 | BZSC-2122A | Limit Switch Close | C-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
82 | TIT-2121B | Temperature Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101B) /To C-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
83 | XSS-2124B | Start Permission | 1ST Gas Compressore Train#B (C-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-NR |  | UCP-GC-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
84 | XSS-2123B | Start Command | 1ST Gas Compressore Train#B (C-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
85 | XSP-2123B | Stop Command | 1ST Gas Compressore Train#B (C-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
86 | BZSO-2122B | Limit Switch Open | C-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
87 | BZSC-2122B | Limit Switch Close | C-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
88 | TIT-2121C | Temperature Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101C) /To C-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
89 | XSS-2124C | Start Permission | 1ST Gas Compressore Train#C (C-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-NR |  | UCP-GC-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
90 | XSS-2123C | Start Command | 1ST Gas Compressore Train#C (C-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
91 | XSP-2123C | Stop Command | 1ST Gas Compressore Train#C (C-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
92 | BZSO-2122C | Limit Switch Open | C-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
93 | BZSC-2122C | Limit Switch Close | C-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
94 | XF-2121A | Fault Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2121A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
95 | XR-2121A | Running/Stop Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2121A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
96 | XL-2121A | Local / Remote Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2121A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
97 | XSP-2121A | Stop Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2121A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
98 | XSS-2121A | Start Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2121A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
99 | XF-2122A | Fault Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2122A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
100 | XR-2122A | Running/Stop Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2122A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
101 | XL-2122A | Local / Remote Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2122A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
102 | XSP-2122A | Stop Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2122A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
103 | XSS-2122A | Start Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) /(AC-2122A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
104 | TIT-2126A | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
105 | TY-2122A | Cooler Actuator Positioner | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
106 | XF-2121B | Fault Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2121B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
107 | XR-2121B | Running/Stop Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2121B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
108 | XL-2121B | Local / Remote Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2121B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
109 | XSP-2121B | Stop Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2121B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
110 | XSS-2121B | Start Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2121B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
111 | XF-2122B | Fault Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2122B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
112 | XR-2122B | Running/Stop Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2122B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
113 | XL-2122B | Local / Remote Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2122B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
114 | XSP-2122B | Stop Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2122B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
115 | XSS-2122B | Start Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) /(AC-2122B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
116 | TIT-2126B | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
117 | TY-2122B | Cooler Actuator Positioner | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
118 | XF-2121C | Fault Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2121C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
119 | XR-2121C | Running/Stop Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2121C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
120 | XL-2121C | Local / Remote Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2121C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
121 | XSP-2121C | Stop Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2121C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
122 | XSS-2121C | Start Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2121C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
123 | XF-2122C | Fault Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2122C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
124 | XR-2122C | Running/Stop Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2122C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
125 | XL-2122C | Local / Remote Status | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2122C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
126 | XSP-2122C | Stop Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2122C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
127 | XSS-2122C | Start Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) /(AC-2122C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
128 | TIT-2126C | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
129 | TY-2122C | Cooler Actuator Positioner | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
130 | PDIT-2131A | Diff. Pressure Indicator Transmitter | V-2102-A |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
131 | LIT-2131A | Level Indicator Transmitter | V-2102-A |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
132 | PSOV-2131A | Solenoid Valve | FROM V-2102-A / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
133 | XZSC-2131A | Limit Switch Close | FROM V-2102-A / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
134 | XZSO-2131A | Limit Switch Open | FROM V-2102-A / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
135 | PDIT-2131B | Diff. Pressure Indicator Transmitter | V-2102-B |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
136 | LIT-2131B | Level Indicator Transmitter | V-2102-B |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
137 | PSOV-2131B | Solenoid Valve | FROM V-2102-B / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
138 | XZSC-2131B | Limit Switch Close | FROM V-2102-B / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
139 | XZSO-2131B | Limit Switch Open | FROM V-2102-B / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
140 | PDIT-2131C | Diff. Pressure Indicator Transmitter | V-2102-C |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
141 | LIT-2131C | Level Indicator Transmitter | V-2102-C |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
142 | PSOV-2131C | Solenoid Valve | FROM V-2102-C / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
143 | XZSC-2131C | Limit Switch Close | FROM V-2102-C / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
144 | XZSO-2131C | Limit Switch Open | FROM V-2102-C / To Close Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
145 | TIT-2131A | Temperature Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102A) /To C-2102-A |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
146 | TIT-2131B | Temperature Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102A) /To C-2102-A |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
147 | TIT-2131C | Temperature Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102A) /To C-2102-A |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
148 | XF-2131A | Fault Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2131A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
149 | XR-2131A | Running/Stop Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2131A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
150 | XL-2131A | Local / Remote Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2131A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
151 | XSP-2131A | Stop Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2131A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
152 | XSS-2131A | Start Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2131A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
153 | XF-2132A | Fault Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2132A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
154 | XR-2132A | Running/Stop Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2132A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
155 | XL-2132A | Local / Remote Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2132A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
156 | XSP-2132A | Stop Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2132A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
157 | XSS-2132A | Start Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A)/(AC-2132A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
158 | TIT-2135A | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
159 | TY-2132A | Cooler Actuator Positioner | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
160 | PIT-2135A | Pressure Indicator Transmitter | From AE-2102-A /TO GAS COMPRESSION DISCHARGE DRUM (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
161 | PCV-2135A | Pressure Control Valve | From AE-2102-A /TO GAS COMPRESSION DISCHARGE DRUM (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
162 | XF-2131B | Fault Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2131B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
163 | XR-2131B | Running/Stop Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2131B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
164 | XL-2131B | Local / Remote Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2131B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
165 | XSP-2131B | Stop Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2131B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
166 | XSS-2131B | Start Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2131B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
167 | XF-2132B | Fault Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2132B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
168 | XR-2132B | Running/Stop Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2132B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
169 | XL-2132B | Local / Remote Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2132B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
170 | XSP-2132B | Stop Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2132B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
171 | XSS-2132B | Start Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B)/(AC-2132B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
172 | TIT-2135B | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
173 | TY-2132B | Cooler Actuator Positioner | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
174 | PIT-2135B | Pressure Indicator Transmitter | From AE-2102-B /TO GAS COMPRESSION DISCHARGE DRUM (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
175 | PCV-2135B | Pressure Control Valve | From AE-2102-B /TO GAS COMPRESSION DISCHARGE DRUM (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
176 | XF-2131C | Fault Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2131C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
177 | XR-2131C | Running/Stop Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2131C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
178 | XL-2131C | Local / Remote Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2131C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
179 | XSP-2131C | Stop Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2131C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
180 | XSS-2131C | Start Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2131C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
181 | XF-2132C | Fault Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2132C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
182 | XR-2132C | Running/Stop Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2132C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
183 | XL-2132C | Local / Remote Status | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2132C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
184 | XSP-2132C | Stop Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2132C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
185 | XSS-2132C | Start Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C)/(AC-2132C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
186 | TIT-2135C | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
187 | TY-2132C | Cooler Actuator Positioner | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
188 | PIT-2135C | Pressure Indicator Transmitter | From AE-2102-C /TO GAS COMPRESSION DISCHARGE DRUM (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
189 | PCV-2135C | Pressure Control Valve | From AE-2102-C /TO GAS COMPRESSION DISCHARGE DRUM (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
190 | PDIT-2141 | Diff. Pressure Indicator Transmitter | V-2103 |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X |  |  | D04 Modified
191 | LIT-2141 | Level Indicator Transmitter | V-2103 |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
192 | PSOV-2144 | Solenoid Valve | From V-2103/ To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
193 | XZSC-2144 | Limit Switch Close | From V-2103/ To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
194 | XZSO-2144 | Limit Switch Open | From V-2103/ To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
195 | BZSC-2141 | Blowdown Limit Switch Close | From V-2103/ To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
196 | BZSO-2141 | Blowdown Limit Switch Open | From V-2103/ To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
197 | PSOV-2142 | Solenoid Valve | From V-2103/ To Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
198 | XZSC-2142 | Limit Switch Close | From V-2103/ To Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
199 | XZSO-2142 | Limit Switch Open | From V-2103/ To Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
200 | PSOV-2143 | Solenoid Valve | From V-2103/ To Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
201 | XZSC-2143 | Limit Switch Close | From V-2103/ To Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
202 | XZSO-2143 | Limit Switch Open | From V-2103/ To Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
203 | PDIT-2143 | Diff. Pressure Indicator Transmitter | From V-2103/ To Dehydration Package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
204 | BZSC-2151 | Blowdown Limit Switch Close | From PK-2101 /To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
205 | BZSO-2151 | Blowdown Limit Switch Open | From PK-2101 /To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
206 | PIT-2151 | Pressure Indicator Transmitter | From PK-2101 / To PL-3101 |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
207 | PCV-2151 | Pressure Control Vavle | From PK-2101 / To PL-3101 |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
208 | PCV-2152 | Pressure Control Vavle | From PK-2101 /To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
209 | LIT-2162 | Level Indicator Transmitter | TK-2102 |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
210 | PIT-2161 | Pressure Indicator Transmitter | TK-2102 |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
211 | XF-2161A | Fault Status | P-2103A |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
212 | XR-2161A | Running/Stop Status | P-2103A |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
213 | XL-2161A | Local / Remote Status | P-2103A |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
214 | XSP-2161A | Stop Command | P-2103A |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
| XSS-2161A | Start Command | P-2103A |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Deleted
215 | XF-2161B | Fault Status | P-2103B |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
216 | XR-2161B | Running/Stop Status | P-2103B |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
217 | XL-2161B | Local / Remote Status | P-2103B |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
218 | XSP-2161B | Stop Command | P-2103B |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
| XSS-2161B | Start Command | P-2103B |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Deleted
219 | XSP-2201A | Stop Command | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-NR |  | DCS |  | PK-C-2203 A |  | * | * | * | * | * | * | * | * | [5 empty] | X
220 | XSS-2201A | Start Command | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-NR |  | DCS |  | PK-C-2203 A |  | * | * | * | * | * | * | * | * | [5 empty] | X
| PDI-2201 | Dif. Pressure Indicator Transmitter | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| PDI-2202 | Dif. Pressure Indicator Transmitter | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| AIA-2201 | Humidity Analyzer | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X |  |  | D04 Deleted
| XR-2201 | Running/Stop Status | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| XF-2201 | Command Fault Alarm | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
221 | XSP-2201B | Stop Command | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-NR |  | DCS |  | PK-C-2203 B |  | * | * | * | * | * | * | * | * | [5 empty] | X
222 | XSS-2201B | Start Command | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-NR |  | DCS |  | PK-C-2203 B |  | * | * | * | * | * | * | * | * | [5 empty] | X
223 | PIT-2201 | Pressure Indicator Transmitter | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
224 | PCV-2201 | Pressure Control Valve | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
225 | PIT-2203A | Pressure Indicator Transmitter | From V-2203/ TO AIR COMPRESSOR PACKAGE (PK-C-2203A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X |  |  | D04 Modified
226 | PIT-2203B | Pressure Indicator Transmitter | From V-2203/ TO AIR COMPRESSOR PACKAGE (PK-C-2203A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X |  |  | D04 Added
227 | PI-2203A | Pressure Indicator | Air Compressor Package (PK-C-2203 A/B) / CAPACITY CONTROL SIGNAL / COMPRESSOR LOAD/UNLOAD |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AO-IS-R |  | DCS |  | PK-C-2203A |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
228 | PI-2203B | Pressure Indicator | Air Compressor Package (PK-C-2203 A/B) / CAPACITY CONTROL SIGNAL / COMPRESSOR LOAD/UNLOAD |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AO-IS-R |  | DCS |  | PK-C-2203B |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
229 | XSP-2211 | STOP Command | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | DO-NIS-NR |  | DCS |  | PK-G-2204 |  | * | * | * | * | * | * | * | * | [5 empty] | X
230 | XSS-2211 | START Command | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | DO-NIS-NR |  | DCS |  | PK-G-2204 |  | * | * | * | * | * | * | * | * | [5 empty] | X
231 | PIT-2213 | Pressure Indicator Transmitter | From V-2204 |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
232 | PCV-2211 | Pressure Control Valve | From V-2204 |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
233 | FIT-2211 | Flow Indicator Transmitter | From V-2204 |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
234 | TT-2211 | Temperature Transmitter | From V-2204 |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
235 | PIT-2214 | Pressure Indicator Transmitter | From V-2204 |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
236 | LIT-2221 | Level Indicator Transmitter | V-2202 |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
237 | LIT-2223 | Level Indicator Transmitter | LP Flare K.O. Drum and Closed Drum (SU-2201) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
238 | XF-2221A | Fault Status | P-2202-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
239 | XR-2221A | Running/Stop Status | P-2202-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
240 | XL-2221A | Local / Remote Status | P-2202-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
241 | XST-2221A | Start Command | P-2202-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
242 | XSP-2221A | Stop Command | P-2202-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
243 | XF-2221B | Fault Status | P-2202-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
244 | XR-2221B | Running/Stop Status | P-2202-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
245 | XL-2221B | Local / Remote Status | P-2202-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
246 | XST-2221B | Start Command | P-2202-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
247 | XSP-2221B | Stop Command | P-2202-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
248 | XF-2222A | Fault Status | P-2203-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
249 | XR-2222A | Running/Stop Status | P-2203-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
250 | XL-2222A | Local / Remote Status | P-2203-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
251 | XST-2222A | Start Command | P-2203-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
252 | XSP-2222A | Stop Command | P-2203-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
253 | XF-2222B | Fault Status | P-2203-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
254 | XR-2222B | Running/Stop Status | P-2203-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
255 | XL-2222B | Local / Remote Status | P-2203-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
256 | XST-2222B | Start Command | P-2203-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
257 | XSP-2222B | Stop Command | P-2203-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
258 | XSP-2231 | Stop Command | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DO-NIS-NR |  | DCS |  | PK-G-2207 |  | * | * | * | * | * | * | * | * | [5 empty] | X
259 | LSLL-2231 | Level Switch Low Low | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D04 Modified
260 | XF-2231A | Fault Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
261 | XF-2231B | Fault Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
262 | XF-2231C | Fault Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
263 | XF-2231D | Fault Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
264 | XF-2231F | Fault Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
265 | XR-2231A | Running/Stop Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
266 | XR-2231B | Running/Stop Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
267 | XR-2231C | Running/Stop Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
268 | XR-2231D | Running/Stop Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
269 | XR-2231F | Running/Stop Status | Corrosion Inhibitor Package (PK-TK-2207) /CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 (1 of 1) |  |  | DI-NIS-NR |  | PK-G-2207 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
270 | LIT-2251 | Level Indicator Transmitter | V-2201 |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
271 | XF-2251A | Fault Status | P-2201 A |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
272 | XR-2251A | Running/Stop Status | P-2201 A |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
273 | XL-2251A | Local / Remote Status | P-2201 A |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
274 | XST-2251A | Start Command | P-2201 A |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
275 | XSP-2251A | Stop Command | P-2201 A |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
276 | XF-2251B | Fault Status | P-2201 B |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
277 | XR-2251B | Running/Stop Status | P-2201 B |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
278 | XL-2251B | Local / Remote Status | P-2201 B |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
279 | XST-2251B | Start Command | P-2201 B |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
280 | XSP-2251B | Start Command | P-2201 B |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
281 | PIT-2252 | Pressure Indicator Transmitter | From V-2201 to LP Flare Stack |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
282 | XR-2261 | LPG Bottle Inservuce | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
283 | XR-2261A | Pilot 1 Status | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
284 | XR-2261B | Pilot 2 Status | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
285 | XR-2261C | Pilot 3 Status | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
286 | XA-2261 | Common Fault Alarm | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
287 | XF-2261 | Auto Ignition Failure | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
288 | XA-2262 | Burn Back Alarm | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
289 | TI-2261A | Temperature Indicator | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | AI-IS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
290 | TI-2261B | Temperature Indicator | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | AI-IS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
291 | TI-2261C | Temperature Indicator | (Ignition Control Panel IG-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | AI-IS-NR |  | IG-2201-LCP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
292 | XR-2281 | Running/Stop Status | P-2281 |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
293 | XF-2281 | Fault Status | P-2281 |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
294 | LIT-2273 | Level Indicator Transmitter | Oily Water Sump (SU-2202) |  | BK-GCS-PEDCO-120-PR-PI-0021 (1 of 1) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
295 | EZSC-2272 | Limit Switch Close | From Inlet K.O. Drum (V-2105) /TO V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
296 | EZSO-2272 | Limit Switch Open | From Inlet K.O. Drum (V-2105) /TO V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
297 | PIT-2272 | Pressure Indicator Transmitter | From Inlet K.O. Drum (V-2105) /TO V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
298 | PCV-2272 | Pressure Control Valve | From Inlet K.O. Drum (V-2105) /TO V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AO-IS-R |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
299 | LIT-2271 | Level Indicator Transmitter | V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
300 | PSOV-2271 | Solenoid Valve | From V-2205/ To Closed Drum |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
301 | XZSC-2271 | Limit Switch Close | From V-2205/ To Closed Drum |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
302 | XZSO-2271 | Limit Switch Open | From V-2205/ To Closed Drum |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
303 | TIT-2271 | Temperature Indicator Transmitter | FROM CORROSION INHIBITOR PUMPS (P-2207A/B) /To V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
304 | FIT-2271 | Flow Indicator Transmitter | FROM CORROSION INHIBITOR PUMPS (P-2207A/B) /To V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
305 | PIT-2271 | Pressure Indicator Transmitter | FROM CORROSION INHIBITOR PUMPS (P-2207A/B) /To V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
306 | LIT-2281 | Level Indicator Transmitter | V-2206 |  | BK-GCS-PEDCO-120-PR-PI-0023 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
307 | XF-2281 | Fault status | P-2206 |  | BK-GCS-PEDCO-120-PR-PI-0023 |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
308 | XR-2281 | Running/Stop Status | P-2206 |  | BK-GCS-PEDCO-120-PR-PI-0023 |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
309 | XSP-2281 | Stop Command | P-2206 |  | BK-GCS-PEDCO-120-PR-PI-0023 |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
310 | LIT-2291 | Level Indicator Transmitter | TK-2209 |  | BK-GCS-PEDCO-120-PR-PI-0024 |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
311 | XF-2291 | Fault Status | P-2209 |  | BK-GCS-PEDCO-120-PR-PI-0024 |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
312 | XR-2291 | Running/Stop Status | P-2209 |  | BK-GCS-PEDCO-120-PR-PI-0024 |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
313 | XL-2291 | Local / Remote Status | P-2209 |  | BK-GCS-PEDCO-120-PR-PI-0024 |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
314 | XSP-2291 | Stop Command | P-2209 |  | BK-GCS-PEDCO-120-PR-PI-0024 |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
315 | LIT-2293 | Level Indicator Transmitter | V-2107 |  | BK-GCS-PEDCO-120-PR-PI-0025 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X
316 | PIT-2291 | Level Indicator Transmitter | V-2107 |  | BK-GCS-PEDCO-120-PR-PI-0025 |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
317 | XF-2293 | Fault Status | P-2104 |  | BK-GCS-PEDCO-120-PR-PI-0025 |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
318 | XR-2293 | Running/Stop Status | P-2104 |  | BK-GCS-PEDCO-120-PR-PI-0025 |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
319 | XL-2293 | Local / Remote Status | P-2104 |  | BK-GCS-PEDCO-120-PR-PI-0025 |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
320 | XSP-2293 | Stop Command | P-2104 |  | BK-GCS-PEDCO-120-PR-PI-0025 |  |  | DO-NIS-NR |  | DCS |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
321 | LIT-2301A | Level Indicator Transmitter | TK-2301A |  | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | X | X | X |  | X |  |  | D04 Modified
322 | LIT-2302B | Level Indicator Transmitter | TK-2301B |  | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | X | X | X |  | X |  |  | D04 Modified
323 | ZSC-2301 | Limit Switch Close | FROM EXISTING PLANT T.P-09/ to Fire Water Storage Tank |  | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
324 | ZSO-2301 | Limit Switch Open | FROM EXISTING PLANT T.P-09/ to Fire Water Storage Tank |  | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
325 | PSOV-2301 | Solenoid Valve | FROM EXISTING PLANT T.P-09/ to Fire Water Storage Tank |  | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
326 | EZSC-3201 | Limit Switch Close | From Dehydration (PK-2101) To Pig Receiver (PR-3201) - Near Pig Launcher |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
327 | EZSO-3201 | Limit Switch Open | From Dehydration (PK-2101) To Pig Receiver (PR-3201) - Near Pig Launcher |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
328 | PSOV-3201 | Solenoid Valve | From Dehydration (PK-2101) To Pig Receiver (PR-3201) - Near Pig Launcher |  | BK-PPL-PEDCO-320-PR-PI-0001 (1 of 3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
| PT-2301 | Pressure Transmitter | To Fire Water Network |  | BK-PPL-PEDCO-320-PR-PI-0001 (2 of 2) |  |  | AI-IS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D04 Deleted
329 | EZSC-3202 | Limit Switch Close | From Pig Launcher (PR-3201) To Inlet Header (Near Pig Receiver) |  | BK-PPL-PEDCO-320-PR-PI-0001 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
330 | EZSO-3202 | Limit Switch Open | From Pig Launcher (PR-3201) To Inlet Header (Near Pig Receiver) |  | BK-PPL-PEDCO-320-PR-PI-0001 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
331 | PSOV-3202 | Solenoid Valve | From Pig Launcher (PR-3201) To Inlet Header (Near Pig Receiver) |  | BK-PPL-PEDCO-320-PR-PI-0001 (3 of 3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
332 | ESDR 1-PCS | PCS FAILURE | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
333 | ESDR 1-FLR | FLARE IGNITION FAILURE | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
334 | XOC-LV-Q0A | Open/Close Status (SWGR-Incoming A-Q0A) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
335 | XF-LV-Q0A | Fault Status (SWGR-Incoming A-Q0A) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
336 | XF-TR-001 | Fault Status (Transformer-001) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
337 | XOC-LV-Q0B | Open/Close Status (SWGR-Incoming B-Q0B) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
338 | XF-LV-Q0B | Fault Status(SWGR-Incoming B-Q0B) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
339 | XF-TR-002 | Fault Status (Transformer-002) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
340 | XOC-LV-Q0C | Open/Close Status (SWGR-Bus Tie C-Q0C) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
341 | XF-LV-Q0C | Fault Status (SWGR-Bus Tie C-Q0C) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
342 | XOC-LV-Q0E | Open/Close Status (SWGR-DG C.B-Q0E) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
343 | XF-LV-Q0E | Fault Status (SWGR-DG C.B-Q0E) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
344 | XOC-LV-Q0D | Open/Close Status (SWGR-DG Bus Tie-Q0D) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
345 | XF-LV-Q0D | Fault Status (SWGR-DG Bus Tie-Q0D) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (LV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
346 | XF-UPS-001-CH01 | Fault Status ( 110V AC UPS-001 (CH01)) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
347 | XF-UPS-001-CH02 | Fault Status ( 110V AC UPS-001 (CH02)) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
348 | XOC-MV-001A-Q2 | Open/Close Status (SWGR-Transformer feeder-Q2) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
349 | XF-MV-001A-Q2 | Fault Status(SWGR-Transformer feeder-Q2) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
| XOC-MV-001A-Q3 | Open/Close Status (SWGR-Gas Compressor-A-2101A-Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| XF-MV-001A-Q3 | Fault Status (SWGR-Gas Compressor-A-2101A-Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| XOC-MV-001A-Q4 | Open/Close Status (SWGR-Gas Compressor-C-2101C-Q4) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| XF-MV-001A-Q4 | Fault Status(SWGR-Gas Compressor-C-2101C-Q4) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
354 | XOC-MV-001A-Q5 | Open/Close Status (SWGR-Spare -Q5) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
355 | XF-MV-001A-Q5 | Fault Status (SWGR-Spare -Q5) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
356 | XOC-MV-001B-Q2 | Open/Close Status (SWGR-Transformer feeder-Q2) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
357 | XF-MV-001B-Q2 | Fault Status (SWGR-Transformer feeder-Q2) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
| XOC-MV-001B-Q3 | Open/Close Status (SWGR-Gas Compressor-C-2101B-Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| XF-MV-001B-Q3 | Fault Status (SWGR-Gas Compressor-C-2101B-Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
1 | XOC-MV-001B-Q4 | Open/Close Status (SWGR-Transformer feeder-Q4) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
361 | XF-MV-001B-Q4 | Fault Status (SWGR-Transformer feeder-Q4) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
362 | XOC-MV-001B-Q5 | Open/Close Status (SWGR-Spare -Q5) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
363 | XF-MV-001B-Q5 | Fault Status (SWGR-Spare -Q5) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
364 | XOC-MV-001C-Q3 | Open/Close Status (SWGR-Fire Pump -Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
365 | XF-MV-001C-Q3 | Fault Status (SWGR-Fire Pump -Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
366 | XL-ATS | Auto/Manual Status | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 modified
367 | XM-LV-IN1 | Multifunction Meter | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
368 | XM-LV-IN2 | Multifunction Meter | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Deleted
| ESDI 0-DCS | ESD 0 status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 1-DCS | ESD 1 status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 1A-DCS | ESD 1A status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 2-A-DCS | ESD 2 status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 2-B-DCS | ESD 2 status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 2-C-DCS | ESD 2 status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 2A-A-DCS | ESD 2A status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 2A-B-DCS | ESD 2A status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 2A-C-DCS | ESD 2A status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 3-A-DCS | ESD 3 status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 3-B-DCS | ESD 3 status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 3-C-DCS | ESD 3 status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 3A-A-DCS | ESD 3A status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 3A-B-DCS | ESD 3A status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
| ESDI 3A-C-DCS | ESD 3A status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D04 Deleted
D04

## IO List for UCP-C-2101
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL SYSTEM
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN |  | LI |  | 0002 |  |  | D04
I/O List For UCP-C-2101
ITEM | TAG | DESCRIPTION | SERVICE |  | P&ID |  |  | I/O TYPE |  | FROM |  | TO |  | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[14 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL | IND/STA | COM.
1 | PSOV-2110 | Solenoid Valve | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DO-NIS-NR |  | UCP (Note 2) |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
2 | BZSC-2110 | Limit Switch Close | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DI-NIS-NR |  | FIELD |  | UCP (Note 2) |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
3 | BZSO-2110 | Limit Switch Open | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DI-NIS-NR |  | FIELD |  | UCP (Note 2) |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
4 | PSOV-2121A | Solenoid Valve | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101A |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
5 | XZSC-2121A | Limit Switch Close | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
6 | XZSO-2121A | Limit Switch Open | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
7 | PSOV-2123A | Solenoid Valve | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-NR |  | UCD (Note 1) |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
8 | XZSC-2123A | Limit Switch Close | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
9 | XZSO-2123A | Limit Switch Open | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
10 | PI-2121A | Pressure Indicator | Outlet V-2101-A /to 1st Stage Compressore (C-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AI-IS-R |  | DCS |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
11 | PCV-2123A | Pressure Control Valve | Outlet V-2101-A /to 1st Stage Compressore (C-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AO-IS-R |  | UCP-GC-2101A |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
12 | FIT-2121A | Flow Indicator Transmitter | 1st Stage Gas Compressor Train A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
13 | TIT-2122A | Temperature Indicator Transmitter | 1st Stage Gas Compressor Train A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
14 | PDIT-2122A | Differential Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
15 | PIT-2123A | Pressure Indicator Transmitter | 1st Stage Gas Compressor Train A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
16 | TIT-2123A | Temperature Indicator Transmitter | 1st Stage Gas Compressor Train A Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
17 | PIT-2124A | Pressure Indicator Transmitter | 1st Stage Gas Compressor Train A Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
18 | PSOV-2134A | Solenoid Valve | From 1ST Stage Air Cooler (AE-2101A) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101A |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
19 | BZSC-2134A | Blowdown Limit Switch Close | From 1ST Stage Air Cooler (AE-2101A) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
20 | BZSO-2134A | Blowdown Limit Switch Open | From 1ST Stage Air Cooler (AE-2101A) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
21 | FIT-2131A | Flow Indicator Transmitter | 2nd Stage Gas Compressor Train A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
22 | TIT-2132A | Temperature Indicator Transmitter | 2nd Stage Gas Compressor Train A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
23 | PDIT-2132A | Differential Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
24 | PIT-2132A | Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train A Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
25 | TIT-2133A | Temperature Indicator Transmitter | 2nd Stage Gas Compressor Train A Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
26 | PIT-2133A | Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train A Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
27 | PSOV-2132A | Solenoid Valve | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101A |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
28 | BZSC-2132A | Blowdown Limit Switch Close | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
29 | BZSO-2132A | Blowdown Limit Switch Open | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
30 | PSOV-2133A | Solenoid Valve | From AE-2102-A /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101A |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
31 | BZSC-2133A | Blowdown Limit Switch Close | From AE-2102-A /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
32 | BZSO-2133A | Blowdown Limit Switch Open | From AE-2102-A /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
33 | XOC-MV-001A-Q3 | Open/Close Status (SWGR-Gas Compressor-A-2101A-Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
34 | XF-MV-001A-Q3 | Fault Status (SWGR-Gas Compressor-A-2101A-Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | UCP-GC-2101A |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
35 | PSOV-2121B | Solenoid Valve | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101B |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
36 | XZSC-2121B | Limit Switch Close | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
37 | XZSO-2121B | Limit Switch Open | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
38 | PSOV-2123B | Solenoid Valve | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-NR |  | UCD (Note 1) |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
39 | XZSC-2123B | Limit Switch Close | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
40 | XZSO-2123B | Limit Switch Open | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
41 | PI-2121B | Pressure Indicator | Outlet V-2101-A /to 1st Stage Compressore (C-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AI-IS-R |  | DCS |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
42 | PCV-2123B | Pressure Control Valve | Outlet V-2101-A /to 1st Stage Compressore (C-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AO-IS-R |  | UCP-GC-2101B |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
43 | FIT-2121B | Flow Indicator Transmitter | 1st Stage Gas Compressor Train B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
44 | TIT-2122B | Temperature Indicator Transmitter | 1st Stage Gas Compressor Train B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
45 | PDIT-2122B | Differential Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
46 | PIT-2123B | Pressure Indicator Transmitter | 1st Stage Gas Compressor Train B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
47 | TIT-2123B | Temperature Indicator Transmitter | 1st Stage Gas Compressor Train B Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
48 | PIT-2124B | Pressure Indicator Transmitter | 1st Stage Gas Compressor Train B Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
49 | PSOV-2134B | Solenoid Valve | From 1ST Stage Air Cooler (AE-2101B) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101B |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
50 | BZSC-2134B | Blowdown Limit Switch Close | From 1ST Stage Air Cooler (AE-2101B) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
51 | BZSO-2134B | Blowdown Limit Switch Open | From 1ST Stage Air Cooler (AE-2101B) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
52 | FIT-2131B | Flow Indicator Transmitter | 2nd Stage Gas Compressor Train B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
53 | TIT-2132B | Temperature Indicator Transmitter | 2nd Stage Gas Compressor Train B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
54 | PDIT-2132B | Differential Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
55 | PIT-2132B | Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train B Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
56 | TIT-2133B | Temperature Indicator Transmitter | 2nd Stage Gas Compressor Train B Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
57 | PIT-2133B | Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train B Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
58 | PSOV-2132B | Solenoid Valve | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101B |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
59 | BZSC-2132B | Blowdown Limit Switch Close | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
60 | BZSO-2132B | Blowdown Limit Switch Open | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
61 | PSOV-2133B | Solenoid Valve | From AE-2102-B /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101B |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
62 | BZSC-2133B | Blowdown Limit Switch Close | From AE-2102-B /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
63 | BZSO-2133B | Blowdown Limit Switch Open | From AE-2102-B /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
64 | XOC-MV-001A-Q4 | Open/Close Status (SWGR-Gas Compressor-C-2101C-Q4) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
65 | XF-MV-001A-Q4 | Fault Status(SWGR-Gas Compressor-C-2101C-Q4) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | UCP-GC-2101B |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
66 | PSOV-2121C | Solenoid Valve | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101C |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
67 | XZSC-2121C | Limit Switch Close | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
68 | XZSO-2121C | Limit Switch Open | FROM 1ST STAGE RECYCLING VALVE LINE To V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
69 | PSOV-2123C | Solenoid Valve | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-NR |  | UCD (Note 1) |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
70 | XZSC-2123C | Limit Switch Close | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
71 | XZSO-2123C | Limit Switch Open | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD /To V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
72 | PI-2121C | Pressure Indicator | Outlet V-2101-A /to 1st Stage Compressore (C-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AI-IS-R |  | DCS |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
73 | PCV-2123C | Pressure Control Valve | Outlet V-2101-A /to 1st Stage Compressore (C-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AO-IS-R |  | UCP-GC-2101C |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Added
74 | FIT-2121C | Flow Indicator Transmitter | 1st Stage Gas Compressor Train C Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
75 | TIT-2122C | Temperature Indicator Transmitter | 1st Stage Gas Compressor Train C Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
76 | PDIT-2122C | Differential Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train C Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
77 | PIT-2123C | Pressure Indicator Transmitter | 1st Stage Gas Compressor Train C Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
78 | TIT-2123C | Temperature Indicator Transmitter | 1st Stage Gas Compressor Train C Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
79 | PIT-2124C | Pressure Indicator Transmitter | 1st Stage Gas Compressor Train C Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
80 | PSOV-2134C | Solenoid Valve | From 1ST Stage Air Cooler (AE-2101C) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101C |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
81 | BZSC-2134C | Blowdown Limit Switch Close | From 1ST Stage Air Cooler (AE-2101C) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
82 | BZSO-2134C | Blowdown Limit Switch Open | From 1ST Stage Air Cooler (AE-2101C) To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
83 | FIT-2131C | Flow Indicator Transmitter | 2nd Stage Gas Compressor Train C Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
84 | TIT-2132C | Temperature Indicator Transmitter | 2nd Stage Gas Compressor Train C Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
85 | PDIT-2132C | Differential Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train C Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
86 | PIT-2132C | Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train C Suction Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
87 | TIT-2133C | Temperature Indicator Transmitter | 2nd Stage Gas Compressor Train C Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
88 | PIT-2133C | Pressure Indicator Transmitter | 2nd Stage Gas Compressor Train C Discharge Line |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
89 | PSOV-2132C | Solenoid Valve | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101C |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
90 | BZSC-2132C | Blowdown Limit Switch Close | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
91 | BZSO-2132C | Blowdown Limit Switch Open | From Methanol Header To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
92 | PSOV-2133C | Solenoid Valve | From AE-2102-C /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-NR |  | UCP-GC-2101C |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D04 Modified
93 | BZSC-2133C | Blowdown Limit Switch Close | From AE-2102-C /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
94 | BZSO-2133C | Blowdown Limit Switch Open | From AE-2102-C /To Gas Compression Discharge Drum (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-NR |  | FIELD |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
95 | XOC-MV-001B-Q3 | Open/Close Status (SWGR-Gas Compressor-C-2101B-Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
96 | XF-MV-001B-Q3 | Fault Status (SWGR-Gas Compressor-C-2101B-Q3) | CONTROL ROOM |  | __ |  |  | DI-NIS-NR |  | IRP (MV SWG) |  | UCP-GC-2101C |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Added
Note 1: Gas Compressor Unit ESD System
D04

## DATA-LINK SOFTWARE
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL SYSTEM
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN |  | LI |  | 0002 |  |  | D04
SOFTWARE DATA-LINK LIST FOR UCP
ITEM | TAG | DESCRIPTION | SERVICE |  | P&ID |  |  | I/O TYPE |  | FROM |  | TO |  | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[14 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL | IND/STA | COM.
UCP-C-2101 (NOTE 7)
1 | XF-2121A | Fault Status | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
2 | XR-2121A | Running/Stop Status | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
3 | FIA-2121A | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
4 | PIA-2123A | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
5 | TIA-2122A | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
6 | PIA-2124A | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
7 | TIA-2123A | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
8 | FIA-2131A | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
9 | PIA-2132A | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
10 | TIA-2132A | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
11 | PIA-2132A | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
12 | TIA-2133A | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | Data-Link Software |  | UCP-C-2101A |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
13 | XF-2121B | Fault Status | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
14 | XR-2121B | Running/Stop Status | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
15 | FIA-2121B | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
16 | PIA-2123B | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
17 | TIA-2122B | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
18 | PIA-2124B | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
19 | TIA-2123B | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
20 | FIA-2131B | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
21 | PIA-2132B | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
22 | TIA-2132B | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
23 | PIA-2132B | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
24 | TIA-2133B | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | Data-Link Software |  | UCP-C-2101B |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
25 | XR-2121C | Running/Stop Status | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D04 Modified
26 | FIA-2121C | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
27 | PIA-2123C | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
28 | TIA-2122C | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
29 | PIA-2124C | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
30 | TIA-2123C | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
31 | FIA-2131C | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
32 | PIA-2132C | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
33 | TIA-2132C | Suction | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
34 | PIA-2132C | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
35 | TIA-2133C | Discharge | UCP-C-2101 |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | Data-Link Software |  | UCP-C-2101C |  | DCS |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D04 Modified
PK-C-2203 A (NOTE 7)
36 | XR-2201A | Running/Stop Status | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 A |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
37 | XF-2201A | Fault Status | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 A |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
38 | XA-2201A | Availibility | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 A |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
39 | XD-2201A | Duty/Standby Status | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 A |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
40 | TAH-2201A | Temperature High Alarm | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 A |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
41 | PAL-2201A | Pressure Low Alarm | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 A |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X
42 | PAH-2201A | Pressure Low Alarm | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 A |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
43 | HSD-2201A | Duty/Standby Command | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | DCS |  | PK-C-2203 A |  | * | * | * | * | * | * | * | * |  |  |  |  | X
PK-C-2203 B (NOTE 7)
44 | XR-2201B | Running/Stop Status | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 B |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
45 | XF-2201B | Fault Status | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 B |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
46 | XA-2201B | Availibility | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 B |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
47 | XD-2201B | Duty/Standby Status | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 B |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
48 | TAH-2201B | Temperature High Alarm | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 B |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
49 | PAL-2201B | Pressure Low Alarm | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 B |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X
50 | PAH-2201B | Pressure Low Alarm | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | PK-C-2203 B |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
51 | HSD-2201B | Duty/Standby Command | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | Data-Link Software |  | DCS |  | PK-C-2203 B |  | * | * | * | * | * | * | * | * |  |  |  |  | X
PK-G-2204 (NOTE 7)
52 | XR-2211 | Running/Stop Status | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
53 | XF-2211 | Fault Status | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
54 | XA-2211 | Availibility | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
55 | TAH-2211 | Temperature High Alarm | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
56 | PAL-2211 | Pressure Low Alarm | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  |  | X |  | X
57 | PAH-2211 | Pressure Low Alarm | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
58 | PDIA-2211 | Dif. Pressure Indicator Transmitter | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
59 | XR-2212 | Running/Stop Status | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
60 | XF-2212 | Fault Status | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X
61 | PDIA-2212 | Dif. Pressure Indicator Transmitter | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
62 | AIA-2212 | Humidity Analyzer | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | PK-G-2204 |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
63 | AIA-2213 | Humidity Analyzer | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | Data-Link Software |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  | X |  |  | X
110V AC UPS-001 (CH01)
64 | XO-UPS-001-CH01 | On/Off Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
65 | XC-UPS-001-CH01 | Current Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
66 | XV-UPS-001-CH01 | Voltage Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
110V AC UPS-001 (CH02)
67 | XO-UPS-001-CH02 | On/Off Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
68 | XC-UPS-001-CH02 | Current Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
69 | XV-UPS-001-CH02 | Voltage Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
24V DC UPS-002 (CH01)
70 | XO-UPS-002-CH01 | On/Off Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
71 | XC-UPS-002-CH01 | Current Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
72 | XV-UPS-002-CH01 | Voltage Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
73 | XF-UPS-002-CH01 | Fault Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
24V DC UPS-002 (CH02)
74 | XO-UPS-002-CH02 | On/Off Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
75 | XC-UPS-002-CH02 | Current Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
76 | XV-UPS-002-CH02 | Voltage Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
77 | XF-UPS-002-CH02 | Fault Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
110V DC CHARGER-001 (CH01)
78 | XO-CHG-001-CH01 | On/Off Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
79 | XC-CHG-001-CH01 | Current Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
80 | XV-CHG-001-CH01 | Voltage Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
81 | XF-CHG-001-CH01 | Fault Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
110V DC CHARGER-001 (CH02)
82 | XO-CHG-001-CH02 | On/Off Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
83 | XC-CHG-001-CH02 | Current Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
84 | XV-CHG-001-CH02 | Voltage Sample | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
85 | XF-CHG-001-CH02 | Fault Status | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | UPS Charger |  | DCS |  | * | * | * | * | * | * | * | * | [7 empty] | D03 ADDED
400 V SWGR-INCOMING
86 | XM-LV-IN1 | Multifunction Meter | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 ADDED
87 | XM-LV-IN2 | Multifunction Meter | CONTROL ROOM |  | __ |  |  | Data-Link Software |  | IRP |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 ADDED
88
89
90
91
92
93
94
95
96
D04