## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2056 |  |  | Transmital Date: 5/1/2023
Document Title: Data Sheets For LV Switchgear |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2056 |  |  | Transmital Date: 5/1/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0005_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | A separate section for MCCB and switch fuse shall be added and some items such as manufacturer/Country, type of design., NO. of poles, rated voltage, rated current, etc shall be added and specified. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | سطرهای مجزا برای MCCB و Switch-Fuse در نظر گرفته شد. |  |  | Noted and Closed
2 | Page 7, item 10: Measuring device such as Ammeters, Voltmeters and Multi Meters shall be added and manufacturer, operating range, accuracy class, etc shall be added and specified. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | در آیتم 12 موارد اضافه گردید. |  |  | Noted and Closed
3 | Following note shall be added: According to IPS-M-EL-143(3), the rated ultimate short circuit breaking capacity (Icu) and rated service short circuit breaking capacity (Ics) shall be equal. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | نوت شماره دو در انتهای جدول با این موضوع اضافه گردید. |  |  | Noted and Closed
4 | Rated insulation voltage system shall be added and specified. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | ولتاژ عایقی برای کلید ها و فیوز منظور شده است. |  |  | Noted and Closed
5 | Page 3, item 1.5: Latest revision of IPS-M-EL-143 (Revision 3) shall be replaced. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | بند 1.5 بر این اساس اصلاح گردید. |  |  | Noted and Closed
6 | Page 3, item 1.13: Impulse withstand voltage shall be rechecked and modified. (If required) |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | مطابق با استاندارد بروزرسانی گردید. |  |  | Noted and Closed
7 | Page 4, item 3: Neutral bus bar cross section shall be added as new row. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | بند 3.8 اضافه گردید. |  |  | Noted and Closed
8 | Page 5, item 4.6: Reference document shall be modified to single line diagram for LV switchgear, not load list. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | مدرک تیپیکال جایگزین مدرک لیست بار گردید. |  |  | Noted and Closed
9 | Page 7, item 10: Manufacturer and model NO. for transducer shall be added. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | اعمال گردید. |  |  | Noted and Closed
10 | No Comment |  | BK-SUR-ENG-ELE-01-04499 | 2022-05-31 | _
11 | No Comment |  | BK-SUR-ENG-ELE-01-05269 | 2022-07-30 | _
12 | No Comment |  | BK-SUR-ENG-ELE-02-07520 | 2023-05-01 | _
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: