## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0006_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1192 |  |  | Transmital Date: 25-Jul-2022
Document Title: Electrical Cable Route & Section Layout For Building & Shelter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1192 |  |  | Transmital Date: 25-Jul-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-PY-0006_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Tag کابل ها بر اساس نامه شماره 172867 مورخ 1401/05/20 اصلاح گردد. |  | 01-2294-183486 | 1401/05/27 | اصلاح گردید.
2 | تعداد Sleeve pipe یدکی PVC در کاندویت های بین اتاق ها،با توجه به تعداد کابل های عبوری در نظر گرفته شود. |  | 01-2294-183486 | 1401/05/27 | اصلاح گردید.
3 | با توجه به محل قرار گیری ترانس سوم بر روی ترانشه کابل های اتاق کنترل موجود ،چه تمهیداتی برای این موضوع دیده شده است؟ |  | 01-2294-183486 | 1401/05/27 | فنداسیون ترانس مزبور ، زیر ترنچ موجود اجرا خواهد شد و اشکالی متوجه کابلهای موجود نخواهد بود.
4 | محل عبور کابل های روشنایی اتاق کپسول های CO2 در نقشه مشخص گردد. |  | 01-2294-183486 | 1401/05/27 | روشنایی اتاق کپسول CO2 از طریق کاندویت توسط تابلو GCS-400-EDP-SW تغذیه خواهد شد و در مدرک مرتبط لحاظ خواهد شد.
5 | جهت جابه جایی بانک های خازنی موجود تمهیدات لازم،شامل تعیین مسیر،سطح مقطع کابل و یا مفصل های احتمالی لحاط و در مدرک نمایش داده شود. |  | 01-2294-183486 | 1401/05/27 | در مدرک مرتبط تمهیدات لازم انجام خواهد پذیرفت.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 02-Aug-22 |  |  |  |  | Date: