## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0006_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1192 |  |  | Transmital Date: 25-Jul-2022
Document Title: Electrical Cable Route & Section Layout For Building & Shelter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1192 |  |  | Transmital Date: 25-Jul-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-PY-0006_D00 |  |  | CRS Status: | C3
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be issued as AFC after finalizing or minor comments on prerequisite documents such as electrical equipment arrangement layout for building, cable list and architectural detail drawing for buildings and shelters. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
2 | According to our telephone conversation, there is conflict between this document and electrical equipment arrangement layout from the equipment arrangement point of view and the cabling on tray/ladder shall be base on equipment arrangement for example for diesel generator shall be modified. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
3 | According to our telephone conversation, Instrument decipline of consultant shall be checked this document before submitting next revison and instrument cables location on tray or sleeves shall be shown in common route by cloud (Especially cables between IRP and DCS/ESD). |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
4 | The crossing between new cable route and existing cable route shall be chekced base on existing cable route document (See attahced file) and if it is possible to use existing cable route, it shall be shown in document. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | تلاش گردید تا در حد امکان جلوگیری از برخورد کابل ها به یکدیگر مرتفع گردد.همانگونه کهخود نیز مستحضرید شرایط نهایی در سایت بازنگری خواهد شد.
5 | According to our telephone conversation, Section detail for MV capacitor room and transfromer rooms has not been shown. It shall be added. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
6 | According to our telephone conversation, NO. of sleeves shall be rechecked and modified if required. For example for SLEEVES-07. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
7 | The arrangement of single core cable on tray/ladder shall be rechecked and modified base on IEC 60034-5-52, Annex H. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
8 | Cable route for following location shall be shown in this document: -Diesel generator shelter -Fire water Pump House -Utility shelter -Chemical Injection Packages & Storage Shelter -Air coolers -Flare K.O. drum/Closed drain/Sump Pumps |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
9 | Incoming and outgoing Trench/openings/Sleeves shall be specified base on Overall cable route layout. (It will be checked later after finalizing or minor comments on overall cable route layout.) |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
10 | The cable route for following items shall be added and specified (New or existing): -New MV panels in left side of MV switchgear. -Between DC UPS panels and LV switchgear. -Between DC UPS panels and Fuse box. -Between fuse box and battery bank. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | بروز رسانی گردید.
11 | Dimension of cable support (especially height) shall be specified in order to facilitate in purchasing stage. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | در مدرک مرتبط تمهیدات لازم انجام خواهد پذیرفت.
12 | Tray/ladder support under LV swithcgear panels can be common in such away tray/ladder installaed on both side of support. Meanwhile support shall be shown on layout. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | اعمال گردید.
13 | Required duct bank (Or conduit) for earthing and lighting cables shall be shown according to related drawing. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | اعمال گردید.
14 | Type of conduit shall be rechecked and modified base on electrical desing criteria. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | اعمال گردید.
15 | Following note shall be added: For exact location of cables trench see relevant civil drawing. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | اعمال گردید.
16 | Following documents shall be added as reference document: -Architectural drawing for buildings -Overall cable route -Electrical equipment arrangement. -Typical Installation Details & Notes For Power System |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | اعمال گردید.
17 | See attached file for Civil comments. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | اعمال گردید.
18 | Complementary comments will be submitted after receiving prerequisit and revised document. |  | BK-SUR-ENG-ELE-01-05335 | 2022-08-02 | در صورت هرگونه تغییر در مدارک مرتبط این مدرک نیز بروزرسانی خواهد گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 02-Aug-22 |  |  |  |  | Date: