## TBE for TG
'نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE For Temperature Gauge
|  |  | Project Code |  | Package | Company code |  | Scope | Disc Code | Doc. Code | Sequence No. | Rev. Code
|  |  | BK |  | GCS | PEDCO |  | 120 | IN | TB | 0013 | D00
REQ. NAME : |  | PMR for Temperature Gauge |  | BIDDER: |  |  | EFSACO
REQ. NO. : |  | BK-GCS-PEDCO-120-IN-TB-0013 |  | NAME: |  |  | Tajhizat Fara Sanat Arman
REQ. REV. : |  | D03 |  | QUOTATION NO.: |  |  | 137ف1403 (REV 01)
EQUIPMENT TYPE : |  | Temperature Gauge |  | QUOTATION DATE: |  |  | 1403/02/09
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED
A | Scope of Work And Supply
1 | Tag Number | [5 empty] | Confirmed
2 | Scope of Work And Supply |  |  | Temperature Gauge |  |  | Confirmed
3 | Delivary Date |  |  | B.V. |  |  | 150 working days
4 | Delivary Place |  |  | Ex.Work |  |  | DDP
5 | Bid Validity Period |  |  | B.V. |  |  | 2 weeks
6 | GUARANTEE |  |  | Requisition eighteen (18) months from the date of the Installation and Commissioning or twenty-four (24) months after the date of delivery of materials (whichever comes earlier) |  |  | Confirmed
7 | MANUFACTURER (VENDOR LIST) |  |  | AVL |  |  | EFSACO is on AVL
8 | SPARE PARTS |  |  | 5% complete set (at least 1 set per type) |  |  | Confirmed
B | Technical Requirements
1 | Environmental / Process Condition |  |  | According to data sheet |  |  | Confirmed
2 | Thermometer Type |  |  | Bimetal / Filled type (As requested) |  |  | Confirmed
3 | Calibrated Range |  |  | As requested |  |  | Confirmed
4 | Dial Size |  |  | 150 mm |  |  | Confirmed
5 | Dial Color |  |  | White with black Letter |  |  | Confirmed
6 | Case Material |  |  | Stainless Steel 304 |  |  | Confirmed
7 | Process Connection Size/ rating |  |  | 1 1/2 RTJ,/ API 3000 |  |  | Process Connection Size/ rating according to Data sheet (2" or 1 1/2" Class 300 and Class 600)
8 | Eng. Unit |  |  | °C/ °F |  |  | Confirmed
9 | Accuracy |  |  | Better than ± 1% of full span |  |  | According to EN13190 Min Accuracy of TGs are ± 1% of full span
10 | Pointer Color / Material |  |  | Black / Metallic |  |  | Confirmed
11 | Stem Type / Material |  |  | Threaded / 316 SS |  |  | Confirmed
12 | Stem Diameter |  |  | 6 mm |  |  | Confirmed
13 | Ingress Protection |  |  | IP65 |  |  | Confirmed
14 | Window Material |  |  | Shatterproof Glass |  |  | Confirmed
15 | Zero Adjustment |  |  | Pointer |  |  | Confirmed
16 | Over range Protection |  |  | 1.5 times the maximum scale. |  |  | Confirmed
17 | Connection |  |  | Every Angle |  |  | Confirmed
18 | External Calibration Adjustment |  |  | Required |  |  | Confirmed
19 | Head Type |  |  | Oriantable Head |  |  | Confirmed
20 | Thermowell |  |  | Tapered Drilled Bar Stock |  |  | Confirmed
21 | Well conn. & Flange Material |  |  | As requested & Stainless Steel 316 |  |  | Confirmed
22 | Thermowell Connection to thermometer |  |  | 1/2" NPTF |  |  | Confirmed
23 | In Complaince with Nace Standard |  |  | As requested |  |  | Confirmed
24 | Insertion Length (U) mm |  |  | As requested |  |  | Confirmed
25 | SS Name Plate |  |  | As requested |  |  | Confirmed
26 | Accessories for installation for remote type |  |  | As requested |  |  | Confirmed
C | Test and Inspection
1 | Test and Inspection |  |  | Project IDS, Requisition |  |  | Confirmed
D | Document Requirements
1 | Country Of Origin |  |  | Contract |  |  | Iran
2 | Wake Frequency Calculaton |  |  | Requisition |  |  | Wake Frequency Calculaton will be done
3 | Material Test / Calibration Certificate |  |  | Requisition |  |  | Confirmed
4 | Level of Similar Experience in past 10 years |  |  | Vendor 's Quotation |  |  | Confirmed
F | Deviations / Alternatives
1 | Deviations (if any) |  |  | signed and stamped |  |  | There is no deviation. The form will be signed accordingly
2 | Manufacturer's Location |  |  | - |  |  | Iran - Isfahan
H | PROPOSAL DOCUMENTATION
1 | Quality plan / ITP |  |  | shall be submitted |  |  | Confirmed
2 | Standard certificates |  |  | shall be submitted |  |  | Confirmed
3 | Filled TBE |  |  | shall be submitted |  |  | Confirmed
4 | Summary sheets |  |  | shall be submitted |  |  | Confirmed
5 | Subvendor list (if any) |  |  | shall be submitted |  |  | There are no subvendors
6 | Reference list |  |  | shall be submitted |  |  | submitted before
7 | Catalouges |  |  | shall be submitted |  |  | Confirmed
8 | Datasheet/ Drawing |  |  | shall be submitted |  |  | Confirmed
9 | Order code (Part No.) |  |  | shall be submitted |  |  | Confirmed
GENERAL ACCEPTANCE FOR QUOTATION:
Notes:
A : ACCEPTABLE (TECHNICALLY MEETS REQUIREMENT)
NA: NOT ACCEPTABLE (TECHNICALLY DOES NOT MEET REQUIREMENT)
CA: CONDITIONALLY ACCEPTED
INA: INFORMATION NOT AVAILABLE
N/A: NOT APPLICABLE