| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CALCULATION NOTE FOR TANK FOUNDATION (TK-2301 A/B) نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D04 |  | DEC. 2024 | AFD | R.Berlouie | M.Fakharian | M.Sadeghian |  |
| D03 |  | MAY. 2024 | AFD | R.Berlouie | M.Fakharian | M.Sadeghian |  |
| D02 |  | FEB. 2024 | IFA | R.Berlouie | M.Fakharian | S.Faramarzpour |  |
| D01 |  | OCT. 2023 | IFA | R.Berlouie | M.Fakharian | S.Faramarzpour |  |
| D00 |  | SEP. 2023 | IFC | R.Berlouie | M.Fakharian | A.M.Mohseni |  |
| Rev. |  | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class:2 |  |  | COMPANY Doc. Number: F0Z-709122 |  |  |  |  |
| Status: |  | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X | X | X |  | 66 |  |  |  |  |  |
| 2 | X | X | X | X | X |  | 67 |  |  |  |  |  |
| 3 | X | X |  |  |  |  | 68 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 70 |  |  |  |  |  |
| 6 | X |  | X |  | X |  | 71 |  |  |  |  |  |
| 7 | X |  |  |  | X |  | 72 |  |  |  |  |  |
| 8 | X |  |  |  | X |  | 73 |  |  |  |  |  |
| 9 | X |  | X |  | X |  | 74 |  |  |  |  |  |
| 10 | X |  | X |  | X |  | 75 |  |  |  |  |  |
| 11 | X |  | X |  | X |  | 76 |  |  |  |  |  |
| 12 | X |  | X |  | X |  | 77 |  |  |  |  |  |
| 13 | X |  | X |  | X |  | 78 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 79 |  |  |  |  |  |
| 15 | X |  |  |  | X |  | 80 |  |  |  |  |  |
| 16 | X |  | X |  | X |  | 81 |  |  |  |  |  |
| 17 | X |  | X |  | X |  | 82 |  |  |  |  |  |
| 18 | X |  |  |  | X |  | 83 |  |  |  |  |  |
| 19 | X |  |  |  | X |  | 84 |  |  |  |  |  |
| 20 | X |  |  |  | X |  | 85 |  |  |  |  |  |
| 21 | X |  |  |  | X |  | 86 |  |  |  |  |  |
| 22 | X |  | X |  | X |  | 87 |  |  |  |  |  |
| 23 | X |  |  |  | X |  | 88 |  |  |  |  |  |
| 24 | X |  |  |  | X |  | 89 |  |  |  |  |  |
| 25 |  | X |  |  | X |  | 90 |  |  |  |  |  |
| 26 |  | X |  |  | X |  | 91 |  |  |  |  |  |
| 27 |  | X |  |  | X |  | 92 |  |  |  |  |  |
| 28 |  |  |  |  | X |  | 93 |  |  |  |  |  |
| 29 |  |  |  |  | X |  | 94 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 100 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 101 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 102 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 103 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 104 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 105 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 106 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 107 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 108 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 109 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 110 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 111 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 112 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 113 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 114 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 115 |  |  |  |  |  |
| 51 |  |  |  |  |  |  | 116 |  |  |  |  |  |
| 52 |  |  |  |  |  |  | 117 |  |  |  |  |  |
| 53 |  |  |  |  |  |  | 118 |  |  |  |  |  |
| 54 |  |  |  |  |  |  | 119 |  |  |  |  |  |
| 55 |  |  |  |  |  |  | 120 |  |  |  |  |  |
| 56 |  |  |  |  |  |  | 121 |  |  |  |  |  |
| 57 |  |  |  |  |  |  | 122 |  |  |  |  |  |
| 58 |  |  |  |  |  |  | 123 |  |  |  |  |  |
| 59 |  |  |  |  |  |  | 124 |  |  |  |  |  |
| 60 |  |  |  |  |  |  | 125 |  |  |  |  |  |
| 61 |  |  |  |  |  |  | 126 |  |  |  |  |  |
| 62 |  |  |  |  |  |  | 127 |  |  |  |  |  |
| 63 |  |  |  |  |  |  | 128 |  |  |  |  |  |
| 64 |  |  |  |  |  |  | 129 |  |  |  |  |  |
| 65 |  |  |  |  |  |  | 130 |  |  |  |  |  |

CONTENTS

1.0	Scope	4

2.0	NORMATIVE REFERENCE	4

3.0	Material properties	5

4.0	Computer software	5

5.0	Geometry	6

6.0	DESIGN LOAD	7

7.0	Design Load Combinations	12

8.0	Tank ANALYSIS AND DESIGN	15

9.0	Reinforcing	21

10.0	ATTACHMENTS	27

INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

- Scope

This report covers design of Fire Water Storage Tanks (TK-2301A/B). The calculation of foundation is performed using “SAP” software.

- NORMATIVE REFERENCE

  - Local Codes and Standards

- INBC Part 6 “Iranian National Building Code

- INBC Part 7 “Iranian National Building Code

- INBC Part 9 “Iranian National Building Code

- INBC Part 10 “Iranian National Building Code

- Iranian Seismic Design Code for Petroleum Facilities(3rd edition)

  - International Codes and Standards

- ASCE 7-10 “Minimum Design Loads and Associated Criteria for Buildings and Other Structures-American Society of Civil Engineers”.

- ACI 318. “Building Code Requirements for Reinforced Concrete”, American Concrete Institute.

- AISC 358 “Prequalified Connections for Special and Intermediate Steel Moment Frames for Seismic Applications.” American Institute of Steel Construction, Inc.

- AISC 360 - “Specification for Structural Steel Buildings”. American Institute of Steel Construction, Inc.

  - The Project Documents

- BK-GNRAL-PEDCO-000-ST-SP-0001 SPECIFICATION FOR CONCRETE WORK

- BK-GNRAL-PEDCO-000-ST-DC-0001 Structural Design Criteria

- BK-GNRAL-PEDCO-000-CV-SP-0004 Specification For Earth Work

- BK-GCS-PEDCO-120-GT-RT-0001 Geotechnical Investigation Report for Compressor Station

- Material properties

Material properties are delivered in the following table.

| Material properties |  |
| --- | --- |
| Structure and Foundation concrete | F’c=300kg/cm²(28 days cylindrical sample) |
| Long. Reinforcement | Fy=4000 kg/cm² (AIII) |
| Trans. Reinforcement | Fy=4000 kg/cm² (AIII) |

- Computer software

Computer’s Software, which is used in structure and foundation analysis and design, are defined in the following table.

| Computer software |  |
| --- | --- |
| analysis and design of structure and foundation | SAP 20.1.0 |

- Geometry

D04

- foundation and pedestal plan for TK-2301-A

- foundation and pedestal plan for TK-2301-B

D04

DESIGN LOAD

  - Load case for tank foundation design

The loads that apply on the foundation, according to tank design report (annex I), are as following:

| Anchor Bolt data |  |  |  |  |
| --- | --- | --- | --- | --- |
| anchor bolt dia. | M30 |  |  |  |
| No. of anchor bolt | 24 |  |  |  |
| BCD | 13250 | mm |  |  |
| foundation load data |  |  |  |  |
| Seismic | Shear (N) |  | 1,963,990 | N |
|  | Moment (N.m) | Ring wall | 6,929,589 | N.m |
|  |  | Slab | 10,790,497 | N.m |
| wind | Shear (N) |  | 456,771 | N |
|  | Moment (N.m) |  | 2,682,225 | N.m |
| Weight | Empty |  | 50,485 | Kg |
|  | Operating |  | 1,090,485 | Kg |
|  | Hydrotest |  | 1,310,485 | Kg |

  - Ds (Total Dead Load of Structure and Foundation & Soil overburden)

Soil overburden:

Soil Pressure on Ring wall:

Ds = 0.5 × 1.85 × (1.5) = 1.40 ton/m²

- area surface pressure for ring wall (face top)

  - F (Normal Fluid Load)

Normal Fluid Load on ring foundation:

F = (Ope load / area of ring foundation) → area of ring foundation: (𝜋 × 13.25²)/4=137.88

1090485/137.88=7.90 ton/m²

Soil Pressure Due to Normal Fluid Load on Ring wall:

F = 7.90× (Kₒ = 0.5) = 3.954 t/m²

- Area uniform F load on the inside ring foundation

- Area uniform F load on the ring wall

  - HT (Test Fluid Load)

Test Load on ring foundation:

HT = Hydro test load / area of ring foundation → area of ring foundation: (𝜋 × 13.25²)/4=137.88 m2 → 1310485/ 137.88 = 9.50 ton/m²

Soil Pressure Due to Test Fluid Load on Ring wall:

HT = 9.50 × (Kₒ = 0.5) = 4.75 t/m²

- area uniform HT load on the inside ring foundation

- area uniform HT load on the ring wall

  - E (Earthquake Load)

Shear load = 1963990 N (based on Mechanical Data Sheet for fire water storage Tanks (TK-2301 A/B).

This shear is based on the datasheet, but we used API650 with ASD behavior coefficient so its value is multiplied by 1.4 → 1963990  1.4 = 2749586 N

Moment = 6929589 N.m (based on Mechanical Data Sheet for fire water storage Tanks (TK-2301 A/B).

This moment is based on the datasheet, but we used API650 with ASD behavior coefficient so its value is multiplied by 1.4 → 6929589  1.4 = 9701424 N.m

- Earthquake Load (EX)

  - W (Wind Load)

Shear load = 456771 N (based on Mechanical Data Sheet for fire water storage Tanks (TK-2301 A/B).

This shear is based on the datasheet, but we used API650 with ASD behavior coefficient so its value is multiplied by 1.4 → 456771  1.4 = 639479 N

Moment = 2682225 N.m (based on Mechanical Data Sheet for fire water storage Tanks (TK-2301 A/B).

This moment is based on the datasheet, but we used API650 with ASD behavior coefficient so its value is multiplied by 1.4 → 2682225  1.4 = 3755115 N.m

- Wind load (WX)

- Design Load Combinations

| Load Assignments |  |  |  |
| --- | --- | --- | --- |
| Case | LoadType | LoadName | LoadSF |
| Text | Text | Text | Unitless |
| A.A.O.1-NL | Load pattern | DE | 1 |
|  | Load pattern | DL | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | F | 1 |
| A.A.O.2-NL | Load pattern | DE | 1 |
|  | Load pattern | DL | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | F | 1 |
|  | Load pattern | WX | 1 |
| A.B.T.1-NL | Load pattern | DL | 1 |
|  | Load pattern | DE | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | HT | 1 |
|  | Load pattern | WX | 0.25 |
| A.B.T.2-NL | Load pattern | DL | 0.6 |
|  | Load pattern | DE | 0.6 |
|  | Load pattern | DS | 0.6 |
|  | Load pattern | HT | 0.6 |
|  | Load pattern | WX | 0.25 |
| A.C.E.1-NL | Load pattern | DL | 1 |
|  | Load pattern | DE | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | WX | 1 |
| A.C.E.2-NL | Load pattern | DL | 0.6 |
|  | Load pattern | DE | 0.6 |
|  | Load pattern | DS | 0.6 |
|  | Load pattern | WX | 1 |
| A.D.E.1-NL | Load pattern | DL | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | DE | 1 |
|  | Load pattern | F | 1 |
|  | Load pattern | EX | 0.7 |
| A.D.E.2-NL | Load pattern | DL | 0.6 |
|  | Load pattern | DS | 0.6 |
|  | Load pattern | DE | 0.6 |
|  | Load pattern | F | 0.6 |
|  | Load pattern | EX | 0.7 |
| S.A.O.1-NL | Load pattern | DL | 1.4 |
|  | Load pattern | DS | 1.4 |
|  | Load pattern | DE | 1.4 |
|  | Load pattern | F | 1.4 |
| S.A.O.2-NL | Load pattern | DL | 1.2 |
|  | Load pattern | DS | 1.2 |
|  | Load pattern | DE | 1.2 |
|  | Load pattern | F | 1.2 |
|  | Load pattern | WX | 1 |
| S.A.O.3-NL | Load pattern | DL | 0.9 |
|  | Load pattern | DS | 0.9 |
|  | Load pattern | DE | 0.9 |
|  | Load pattern | F | 0.9 |
|  | Load pattern | WX | 1 |
| S.B.T.1-NL | Load pattern | DL | 1.2 |
|  | Load pattern | DE | 1.2 |
|  | Load pattern | DS | 1.2 |
|  | Load pattern | HT | 1.2 |
|  | Load pattern | WX | 0.25 |
| S.B.T.2-NL | Load pattern | DL | 0.9 |
|  | Load pattern | DE | 0.9 |
|  | Load pattern | DS | 0.9 |
|  | Load pattern | HT | 0.9 |
|  | Load pattern | WX | 0.25 |
| S.C.E.1-NL | Load pattern | DE | 1.2 |
|  | Load pattern | DL | 1.2 |
|  | Load pattern | DS | 1.2 |
|  | Load pattern | WX | 1 |
| S.C.E.2-NL | Load pattern | DE | 0.9 |
|  | Load pattern | DL | 0.9 |
|  | Load pattern | DS | 0.9 |
|  | Load pattern | WX | 1 |
| S.D.E.1-NL | Load pattern | DE | 1.2 |
|  | Load pattern | DL | 1.2 |
|  | Load pattern | DS | 1.2 |
|  | Load pattern | F | 1.2 |
|  | Load pattern | EX | 1 |
| S.D.E.2-NL | Load pattern | DE | 0.9 |
|  | Load pattern | DL | 0.9 |
|  | Load pattern | DS | 0.9 |
|  | Load pattern | F | 0.9 |
|  | Load pattern | EX | 1 |

- Tank ANALYSIS AND DESIGN

  - Tank geometry

As noted before, the structure has modelled and analysed by SAP2000. This figure shows a 3D view of the model in software.

- 3D model

  - Tank Design Results

    - Soil Pressure Control

Soil pressures in different service load combinations should be checked by allowable value. The following figure is extracted from “SAP” model.

According to Geotechnical report Ks = 0.73 Kg/cm³ ,allowable settlement = 2.5 cm and  Max soil pressure for this foundation is 2.00 Kg/cm², in this foundation maximum existing settlement is 1.76 cm and maximum existing stress is about 1.50 Kg/cm² .

- Soil pressure

According to Geotechnical report allowable soil pressure in mat foundation (middle of tank) is 0.60 Kg/cm²

In this foundation maximum soil pressure is:

Qliquid<Qall(Circular Mat)

(Operation load / tank area) 1074765/ 1330000 =0.808 Kg/cm²  < 0.88 Kg/cm²

    - Displacement check

Based on SAP2000 output the maximum deflection in foundation is 0.41 cm and the maximum drift is 1.64 cm.

| TABLE: Joint Displacements |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Joint | OutputCase | CaseType | StepType | U1 | U2 | U3 |
| Text | Text | Text | Text | cm | cm | cm |
| 256 | ENV A | Combination | Min | 0 | 0 | -1.553913 |
| 257 | ENV A | Combination | Min | 0 | 0 | -1.539193 |
| 258 | ENV A | Combination | Min | 0 | 0 | -1.496036 |
| 259 | ENV A | Combination | Max | 0 | 0 | -0.487966 |
| 259 | ENV A | Combination | Min | 0 | 0 | -1.427384 |
| 260 | ENV A | Combination | Min | 0 | 0 | -1.337915 |
| 261 | ENV A | Combination | Min | 0 | 0 | -1.233726 |
| 262 | ENV A | Combination | Min | 0 | 0 | -1.210166 |
| 263 | ENV A | Combination | Max | 0 | 0 | -0.310527 |
| 263 | ENV A | Combination | Min | 0 | 0 | -1.198277 |
| 264 | ENV A | Combination | Min | 0 | 0 | -1.187199 |
| 270 | ENV A | Combination | Min | 0 | 0 | -1.170385 |
| 271 | ENV A | Combination | Min | 0 | 0 | -1.177685 |
| 272 | ENV A | Combination | Min | 0 | 0 | -1.187199 |
| 273 | ENV A | Combination | Min | 0 | 0 | -1.198277 |
| 274 | ENV A | Combination | Min | 0 | 0 | -1.210166 |
| 275 | ENV A | Combination | Min | 0 | 0 | -1.233726 |
| 276 | ENV A | Combination | Min | 0 | 0 | -1.337915 |
| 277 | ENV A | Combination | Min | 0 | 0 | -1.427384 |
| 278 | ENV A | Combination | Min | 0 | 0 | -1.496036 |
| 279 | ENV A | Combination | Min | 0 | 0 | -1.539193 |
| 280 | ENV A | Combination | Min | 0 | 0 | -1.660392 |
| 281 | ENV A | Combination | Min | 0 | 0 | -1.641737 |
| 282 | ENV A | Combination | Min | 0 | 0 | -1.587041 |
| 283 | ENV A | Combination | Min | 0 | 0 | -1.500033 |
| 284 | ENV A | Combination | Min | 0 | 0 | -1.386641 |
| 285 | ENV A | Combination | Min | 0 | 0 | -1.254594 |
| 286 | ENV A | Combination | Min | 0 | 0 | -1.199891 |
| 287 | ENV A | Combination | Min | 0 | 0 | -1.18515 |
| 288 | ENV A | Combination | Min | 0 | 0 | -1.171413 |
| 289 | ENV A | Combination | Min | 0 | 0 | -1.159617 |
| 290 | ENV A | Combination | Min | 0 | 0 | -1.150565 |
| 291 | ENV A | Combination | Min | 0 | 0 | -1.144874 |
| 292 | ENV A | Combination | Min | 0 | 0 | -1.142933 |
| 293 | ENV A | Combination | Min | 0 | 0 | -1.144874 |
| 294 | ENV A | Combination | Min | 0 | 0 | -1.150565 |
| 295 | ENV A | Combination | Min | 0 | 0 | -1.159617 |
| 296 | ENV A | Combination | Min | 0 | 0 | -1.171413 |
| 297 | ENV A | Combination | Min | 0 | 0 | -1.18515 |
| 298 | ENV A | Combination | Min | 0 | 0 | -1.199891 |
| 299 | ENV A | Combination | Min | 0 | 0 | -1.254594 |
| 300 | ENV A | Combination | Min | 0 | 0 | -1.386641 |
| 301 | ENV A | Combination | Min | 0 | 0 | -1.500033 |
| 302 | ENV A | Combination | Min | 0 | 0 | -1.587041 |
| 303 | ENV A | Combination | Min | 0 | 0 | -1.641737 |
| 304 | ENV A | Combination | Min | 0 | 0 | -1.762392 |
| 305 | ENV A | Combination | Min | 0 | 0 | -1.739941 |
| 306 | ENV A | Combination | Min | 0 | 0 | -1.674118 |
| 307 | ENV A | Combination | Min | 0 | 0 | -1.569408 |
| 308 | ENV A | Combination | Max | 0 | 0 | -0.491536 |
| 308 | ENV A | Combination | Min | 0 | 0 | -1.432948 |
| 309 | ENV A | Combination | Min | 0 | 0 | -1.274037 |
| 310 | ENV A | Combination | Min | 0 | 0 | -1.189318 |
| 311 | ENV A | Combination | Min | 0 | 0 | -1.171832 |
| 312 | ENV A | Combination | Min | 0 | 0 | -1.155537 |
| 313 | ENV A | Combination | Min | 0 | 0 | -1.141544 |
| 314 | ENV A | Combination | Min | 0 | 0 | -1.130806 |
| 315 | ENV A | Combination | Min | 0 | 0 | -1.124056 |
| 316 | ENV A | Combination | Min | 0 | 0 | -1.121754 |
| 317 | ENV A | Combination | Min | 0 | 0 | -1.124056 |
| 318 | ENV A | Combination | Min | 0 | 0 | -1.130806 |
| 319 | ENV A | Combination | Min | 0 | 0 | -1.141544 |
| 320 | ENV A | Combination | Min | 0 | 0 | -1.155537 |
| 321 | ENV A | Combination | Min | 0 | 0 | -1.171832 |
| 322 | ENV A | Combination | Min | 0 | 0 | -1.189318 |
| 323 | ENV A | Combination | Min | 0 | 0 | -1.274037 |
| 324 | ENV A | Combination | Min | 0 | 0 | -1.432948 |
| 325 | ENV A | Combination | Min | 0 | 0 | -1.569408 |
| 326 | ENV A | Combination | Min | 0 | 0 | -1.674118 |
| 327 | ENV A | Combination | Min | 0 | 0 | -1.739941 |
|  |  |  |  |  | MAX | -1.762392 |

- Reinforcing

  - Hoop tension control

Ph=k0hQliquid+0.5k0Ɣh2=0.5*2.1*7.90+0.5*0.5*1.85*2.12=10.33  T/m

T HOOP=PHD/2=10.33*13.25=77.99 T

T HOOP=As Fy= As= THOOP /Fy =77990/4000=19.49 cm

Use 10T16                            As=20  OK

  - Dowel reinforcement of ring wall

AS≥(0.75FuA)anchorφFyrein.=0.75*4000*3.1415*3*340.9*4000=5.89

Use T16@200                             As=20.00     OK

  - Foundation reinforcement

According to ACI-318-08:

AS,min=0.0018×60×100=10.8cm2 for top and bottom 
→ If use Φ 12@200 → A = 5.65cm² → 5.65 cm² ≤ 10.8/2 = 5.4 cm² → ok

- Foundation reinforcement plan

fc=300  kg/cm²

fy=4000  kg/cm²

φ=0.9

As used=T12@200=5.6cm²

cover=75mm

h=600 mm

a=Asfy0.85bfc'=5.6*40000.85*100*300=0.9cm

Mn=0.9×5.6×4000×50.1=10.1 ton.m

- M11 Max

- M11 Min

- M22 Max

- M22 Min

- V3-3 EX

- V3-3 WX

- ATTACHMENTS

  - SOWFTWARE FILE

“SAP” software file is attached.

  - MECHANICAL DATA SHEET

Mechanical data sheet is attached.

  - VENDOR LOAD DATA

Vendor load data is attached.