## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-TB-0010 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2807 |  |  | Transmital Date: 23 Oct 2024
Document Title: TBE For Differential Pressure/Pressure Gauge |  |  |  |  | NISOC Tr. No.: |  |  | Transmital Date:
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-TB-0010_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | برای تمامی سازندگان نوع Connection از نوع screwed مورد پذیرش می باشد و خارج از آن قابل پذیرش نمی باشد. |  | 03/2294/329220 | 1403/08/20 | مورد ذکر شده به سازندگان اعلام گردید ، مدارک اصلاح شده سازندگان به ضمیمه TBE ارسال گردید.
2 | Deviation List باید دارای مهر و امضا سازنده باشد. در حال حاضر Deviation List شرکت سنگان صنعت مورد پذیرش نمی باشد. |  | 03/2294/329220 | 1403/08/20 | مورد ذکر شده به سازندگان اعلام گردید ، مدارک اصلاح شده سازندگان به ضمیمه TBE ارسال گردید.
3 | برای تمامی سازندگان دقت اندازه گیری تا 1% قابل پذیرش می باشد، بیشتر از آن غیر قابل قبول می باشد. |  | 03/2294/329220 | 1403/08/20 | مورد ذکر شده به سازندگان اعلام گردید ، مدارک اصلاح شده سازندگان به ضمیمه TBE ارسال گردید.
4 | درمورد Deviation List شرکت پارس جهد آیتم های 5و1و3 مورد پذیرش نمی باشد و آیتم های 4 مطابق بند 3 عمل گردد. |  | 03/2294/329220 | 1403/08/20 | موارد ذکر شده به سازنده مربوطه اعلام گردید ، پاسخ سازنده در TCL مربوطه به همراه مدارک اصلاح شده سازنده ضمیمه TBE ارسال گردید.
5 | . در موردDeviation List شرکت سنگان صنعت نظرات ارائه شده از جانب شرکت هیرگان انرژی مورد تایید کارفرما می باشد. |  | 03/2294/329220 | 1403/08/20 | -
6 | در سایر موارد نظرات مطرح شده در TCL ها کفایت امر می نمایند و لازم است مدرک پس از تعیین تکلیف موارد مطرح شده و باز در TCL ها مجددا برای بررسی ارسال گردد. |  | 03/2294/329220 | 1403/08/20 | مدارک اصلاح شده سازندگان به همراه TCLهای اصلاح شده به ضمیمه TBE ارسال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 6 Nov 2024 |  |  |  |  | Date: