| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| HVAC CALCULATION NOTE FOR CCTV CONTROL ROOM (DU,PU,GCS) نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D01 |  | DEC. 2024 | IFA | K.Ahmadi | M.Fakharian | S.Faramarzpour |  |
| D00 |  | APR. 2024 | IFC | K.Ahmadi | M.Fakharian | S.Faramarzpour |  |
| Rev. |  | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class: 2 |  |  | CLIENT Doc. Number: F0Z-709533 |  |  |  |  |
| Status: |  | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X |  |  |  |  | 58 |  |  |  |  |  |
| 2 | X | X |  |  |  |  | 59 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 60 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 61 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 62 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 63 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 64 |  |  |  |  |  |
| 8 | X | X |  |  |  |  | 65 |  |  |  |  |  |
| 9 | X | X |  |  |  |  | 66 |  |  |  |  |  |
| 10 | X |  |  |  |  |  | 67 |  |  |  |  |  |
| 11 | X | X |  |  |  |  | 68 |  |  |  |  |  |
| 12 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 13 | X | X |  |  |  |  | 70 |  |  |  |  |  |
| 14 | X | X |  |  |  |  | 71 |  |  |  |  |  |
| 15 | X | X |  |  |  |  | 72 |  |  |  |  |  |
| 16 | X | X |  |  |  |  | 73 |  |  |  |  |  |
| 17 | X | X |  |  |  |  | 74 |  |  |  |  |  |
| 18 | X | X |  |  |  |  | 75 |  |  |  |  |  |
| 19 | X | X |  |  |  |  | 76 |  |  |  |  |  |
| 20 | X | X |  |  |  |  | 77 |  |  |  |  |  |
| 21 | X | X |  |  |  |  | 78 |  |  |  |  |  |
| 22 | X | X |  |  |  |  | 79 |  |  |  |  |  |
| 23 | X |  |  |  |  |  | 80 |  |  |  |  |  |
| 24 | X |  |  |  |  |  | 81 |  |  |  |  |  |
| 25 | X | X |  |  |  |  | 82 |  |  |  |  |  |
| 26 | X | X |  |  |  |  | 83 |  |  |  |  |  |
| 27 | X | X |  |  |  |  | 84 |  |  |  |  |  |
| 28 | X | X |  |  |  |  | 85 |  |  |  |  |  |
| 29 | X | X |  |  |  |  | 86 |  |  |  |  |  |
| 30 | X | X |  |  |  |  | 87 |  |  |  |  |  |
| 31 | X | X |  |  |  |  | 88 |  |  |  |  |  |
| 32 | X | X |  |  |  |  | 89 |  |  |  |  |  |
| 33 | X | X |  |  |  |  | 90 |  |  |  |  |  |
| 34 | X | X |  |  |  |  | 91 |  |  |  |  |  |
| 35 | X | X |  |  |  |  | 92 |  |  |  |  |  |
| 36 |  | X |  |  |  |  | 93 |  |  |  |  |  |
| 37 |  | X |  |  |  |  | 94 |  |  |  |  |  |
| 38 |  | X |  |  |  |  | 95 |  |  |  |  |  |
| 39 |  | X |  |  |  |  | 96 |  |  |  |  |  |
| 40 |  | X |  |  |  |  | 97 |  |  |  |  |  |
| 41 |  | X |  |  |  |  | 98 |  |  |  |  |  |
| 42 |  | X |  |  |  |  | 99 |  |  |  |  |  |
| 43 |  | X |  |  |  |  | 100 |  |  |  |  |  |
| 44 |  | X |  |  |  |  | 101 |  |  |  |  |  |
| 45 |  | X |  |  |  |  | 102 |  |  |  |  |  |
| 46 |  | X |  |  |  |  | 103 |  |  |  |  |  |
| 47 |  | X |  |  |  |  | 104 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 105 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 106 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 107 |  |  |  |  |  |
| 51 |  |  |  |  |  |  | 108 |  |  |  |  |  |
| 52 |  |  |  |  |  |  | 109 |  |  |  |  |  |
| 53 |  |  |  |  |  |  | 110 |  |  |  |  |  |
| 54 |  |  |  |  |  |  | 111 |  |  |  |  |  |
| 55 |  |  |  |  |  |  | 112 |  |  |  |  |  |
| 56 |  |  |  |  |  |  | 113 |  |  |  |  |  |
| 57 |  |  |  |  |  |  | 114 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	4

3.0	NORMATIVE REFERENCES	5

3.1	Local Codes and Standards	5

3.2	International Codes and Standards	5

3.3	ENVIRONMENTAL DATA	5

4.0	HVAC CALCULATION	6

4.1	Design weather Parameters:	6

4.2	CONSTRUCTIONS U-VALUE:	8

4.3	SPACE INPUT DATA:	13

4.4	SYSTEM INPUT DATA:	23

4.5	AIR SYSTEM SIZING SUMMARY:	25

4.6	ventilation sizing summary	28

4.7	air system design load summary:	29

4.8	ZONE DESIGN LOAD SUMMARY:	32

4.9	SPACE DESIGN LOAD SUMMARY:	35

5.0	Equipment Selection	45

5.1	Air Conditioning Unit	45

5.2	Exhaust fan selection	48

CCTV CONTROL ROOM - BINAK GCS & DU	48

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO).Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – General Facilities |
| GENERAL CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of :Hirgan Energy – Design & Inspection(D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR (GC) and approved by CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR |
| MAY: | Is used where a provision is completely discretionary. |

- Scope

The main purpose of this document is to define the HVAC system load calculation has been carried out by computer program (HAP software) as per ASHRAE method in order to evaluate cooling load (summer) and heating load (winter) and also to select HVAC equipment for the calculated cooling and heating load.

- NORMATIVE REFERENCES

## Local Codes and Standards

- IPS                                                Iranian petroleum standards

- INBC                                             Iranian National Building Code

## International Codes and Standards

- ASTM	American Society for Testing Materials Relevant Parts

- API 610	Centrifugal Pumps for General Refinery Service, 10th Edition

- ISO 15156	Petroleum and Natural Gas Industries. Materials for use in H2S Containing Environments in Oil and Gas

Production

- AMCA 	Air Movement and Control Association

- ANSI 	American National Standards Institute.

- ASHRAE 	American Society of Heating, Refrigeration and Air-conditioning Engineer

- ASTM 	American Society for Testing and Material

- BOCA 	Building Officials and Code Administrators international

- BS 	British Standards

- CIBSE 	Chartered Institute of Building Services Engineers.

- NFPA 	National fire protection association

- SBCCI	Southern Building Code Congress International

- SMACNA                               Sheet Metal and Air Conditioning Contractors’ National Association

- AWWA                                          American Water Works Association

- ASME                                          The American Society of Mechanical Engineers

Note: The latest issued or revised edition of all above mentioned codes and standards shall be considered as reference.

## ENVIRONMENTAL DATA

Refer to "Process Basis of Design; Doc. No BK-GNRAL-PEDCO-000-PR-DB-0001.

- HVAC CALCULATION

## Design weather Parameters:

Design Parameters:

City Name 	 Binak

Location 	 IRAN

Latitude 	 29.7	Deg.

Longitude 	 -50.4	Deg.

Elevation 	 26.2	m

Summer Design Dry-Bulb 	 41.0	°C

Summer Coincident Wet-Bulb 	 32.0	°C

Summer Daily Range 	 16.7	°K

Winter Design Dry-Bulb 	 6.0	°C

Winter Design Wet-Bulb 	 6.0	°C

Atmospheric Clearness Number 	 1.00

Average Ground Reflectance 	 0.20

Soil Conductivity 	 1.385	W/ (m-°K)

Local Time Zone (GMT +/- N hours) 	 -3.5	hours

Consider Daylight Savings Time 	 No

Simulation Weather Data 	 noneN/A

Current Data is 	 User Modified

Design Cooling Months 	                                                                   January to December

Design Day Maximum Solar Heat Gains

(The MSHG values are expressed in W/m²)

| Month | N | NNE | NE | ENE | E | ESE | SE | SSE | S |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| January | 77.5 | 77.5 | 95.1 | 360.4 | 561.2 | 730.9 | 794.1 | 786.3 | 762.3 |
| February | 89.1 | 89.1 | 206.7 | 484.1 | 668.9 | 760.8 | 782.0 | 718.9 | 671.9 |
| March | 101.4 | 120.5 | 367.4 | 576.2 | 723.5 | 759.6 | 702.5 | 590.8 | 520.1 |
| April | 113.0 | 252.7 | 487.2 | 636.6 | 705.1 | 688.3 | 568.6 | 408.7 | 322.0 |
| May | 124.3 | 351.1 | 551.9 | 666.3 | 679.9 | 619.4 | 469.6 | 279.8 | 199.5 |
| June | 161.0 | 389.1 | 570.0 | 664.8 | 662.8 | 586.8 | 421.4 | 228.9 | 165.7 |
| July | 128.9 | 355.9 | 541.6 | 644.7 | 671.3 | 606.9 | 452.1 | 270.2 | 196.1 |
| August | 118.3 | 256.1 | 470.7 | 606.2 | 686.0 | 663.8 | 546.8 | 395.4 | 311.9 |
| September | 104.3 | 109.2 | 354.3 | 538.8 | 681.8 | 728.9 | 670.0 | 569.4 | 503.5 |
| October | 91.2 | 91.2 | 226.5 | 441.2 | 642.7 | 746.9 | 748.8 | 692.4 | 650.8 |
| November | 78.1 | 78.1 | 103.7 | 341.8 | 572.3 | 707.9 | 785.7 | 774.1 | 747.8 |
| December | 71.9 | 71.9 | 71.9 | 306.4 | 524.4 | 699.0 | 788.1 | 799.2 | 780.7 |
| Month | SSW | SW | WSW | W | WNW | NW | NNW | HOR | Mult |
| January | 779.8 | 791.7 | 733.2 | 577.4 | 337.4 | 108.2 | 77.5 | 591.4 | 1.00 |
| February | 716.3 | 777.2 | 772.2 | 650.4 | 482.8 | 225.6 | 89.1 | 714.5 | 1.00 |
| March | 590.5 | 703.8 | 755.6 | 713.7 | 589.1 | 369.6 | 114.3 | 816.8 | 1.00 |
| April | 413.5 | 574.6 | 682.6 | 707.6 | 645.8 | 485.9 | 241.4 | 863.3 | 1.00 |
| May | 282.1 | 471.6 | 614.4 | 688.4 | 669.7 | 550.4 | 343.5 | 875.1 | 1.00 |
| June | 233.1 | 424.2 | 577.0 | 674.2 | 670.6 | 567.0 | 376.4 | 872.9 | 1.00 |
| July | 274.2 | 458.7 | 596.0 | 677.5 | 657.5 | 539.9 | 345.0 | 865.3 | 1.00 |
| August | 398.9 | 554.0 | 657.3 | 682.8 | 624.7 | 473.1 | 240.3 | 846.4 | 1.00 |
| September | 569.0 | 669.3 | 728.9 | 681.0 | 540.4 | 354.6 | 108.6 | 783.8 | 1.00 |
| October | 697.0 | 755.4 | 737.2 | 647.9 | 457.7 | 216.5 | 91.2 | 696.8 | 1.00 |
| November | 775.6 | 786.0 | 708.0 | 568.2 | 351.0 | 91.0 | 78.1 | 582.8 | 1.00 |
| December | 798.2 | 790.7 | 685.6 | 536.9 | 295.2 | 71.9 | 71.9 | 533.5 | 1.00 |

Mult. = User-defined solar multiplier factor.

Design Temperature Profile

D01

CONSTRUCTIONS U-VALUE:

# CCTV CONTROL ROOM - BINAK GCS & DU

Wall (Ceramic tile)

Wall Details

Outside Surface Color 	 Medium

Absorptivity 	 0.675

Overall U-Value 	 0.541	W/(m²-°K)

Wall Layers Details (Inside to Outside)

|  | Thickness | Density | Specific Ht. | R-Value | Weight |
| --- | --- | --- | --- | --- | --- |
| Layers | mm | kg/m³ | kJ / (kg - °K) | (m²-°K)/W | kg/m² |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| Ceramic tile | 12.500 | 1000.0 | 0.34 | 0.03676 | 12.5 |
| Cement plaster | 20.000 | 1600.0 | 0.80 | 0.06667 | 32.0 |
| Wall brick | 200.000 | 2000.0 | 0.20 | 0.28000 | 400.0 |
| Rock wool | 50.000 | 25.0 | 0.05 | 1.19048 | 1.3 |
| Cement plaster | 20.000 | 1600.0 | 0.80 | 0.06667 | 32.0 |
| Face brick | 30.000 | 2000.0 | 0.03 | 0.03000 | 60.0 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| Totals | 332.500 | - |  | 1.84986 | 537.8 |

Wall (gypsum plaster)

Wall Details

Outside Surface Color 	 Medium

Absorptivity 	 0.675

Overall U-Value 	 0.495	W/(m²-°K)

Wall Layers Details (Inside to Outside)

|  | Thickness | Density | Specific Ht. | R-Value | Weight |
| --- | --- | --- | --- | --- | --- |
| Layers | mm | kg/m³ | kJ / (kg - °K) | (m²-°K)/W | kg/m² |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| Gypsum plaster | 20.000 | 1300.0 | 1.17 | 0.03571 | 26.0 |
| Wall brick | 200.000 | 2000.0 | 0.20 | 0.28000 | 400.0 |
| HDPU | 50.000 | 50.0 | 0.05 | 1.42857 | 2.5 |
| Cement plaster | 20.000 | 750.0 | 0.80 | 0.06667 | 15.0 |
| Face brick | 30.000 | 2000.0 | 0.03 | 0.03000 | 60.0 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| Totals | 320.000 | - |  | 2.02023 | 503.5 |

Wall (MDF)

Wall Details

Outside Surface Color 	 Medium

Absorptivity 	 0.675

Overall U-Value 	 0.452	W/(m²-°K)

Wall Layers Details (Inside to Outside)

|  | Thickness | Density | Specific Ht. | R-Value | Weight |
| --- | --- | --- | --- | --- | --- |
| Layers | mm | kg/m³ | kJ / (kg - °K) | (m²-°K)/W | kg/m² |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| MDF | 40.000 | 400.0 | 1.17 | 0.40000 | 16.0 |
| Cement plaster | 20.000 | 1600.0 | 0.80 | 0.06667 | 32.0 |
| Wall brick | 200.000 | 2000.0 | 0.20 | 0.28000 | 400.0 |
| Rock wool | 50.000 | 25.0 | 0.05 | 1.19048 | 1.3 |
| Cement plaster | 20.000 | 1600.0 | 0.80 | 0.06667 | 32.0 |
| Face brick | 30.000 | 2000.0 | 0.03 | 0.03000 | 60.0 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| Totals | 360.000 | - |  | 2.21310 | 541.3 |

Wall (Stone)-Rock Wool

D01

Wall Details

Outside Surface Color 	 Medium

Absorptivity 	 0.675

Overall U-Value 	 0.547	W/(m²-°K)

Wall Layers Details (Inside to Outside)

|  | Thickness | Density | Specific Ht. | R-Value | Weight |
| --- | --- | --- | --- | --- | --- |
| Layers | mm | kg/m³ | kJ / (kg - °K) | (m²-°K)/W | kg/m² |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| Marble stone | 50.000 | 2700.0 | 1.26 | 0.01429 | 135.0 |
| Cement plaster | 20.000 | 750.0 | 0.80 | 0.06667 | 15.0 |
| Wall brick | 200.000 | 2000.0 | 0.20 | 0.28000 | 400.0 |
| Rock wool | 50.000 | 80.0 | 0.05 | 1.19048 | 4.0 |
| Cement plaster | 20.000 | 750.0 | 0.80 | 0.06667 | 15.0 |
| Face brick | 30.000 | 2000.0 | 1.00 | 0.03000 | 60.0 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| Totals | 370.000 | - |  | 1.82739 | 629.0 |

Roof-HDPU

Roof Details

Outside Surface Color 	 Medium

Absorptivity 	 0.675

Overall U-Value 	 0.536	W/(m²-°K)

Roof Layers Details (Inside to Outside)

|  | Thickness | Density | Specific Ht. | R-Value | Weight |
| --- | --- | --- | --- | --- | --- |
| Layers | mm | kg/m³ | kJ / (kg - °K) | (m²-°K)/W | kg/m² |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| HW concrete | 200.000 | 2400.0 | 0.84 | 0.08000 | 480.0 |
| HDPU | 50.000 | 60.0 | 0.84 | 1.42857 | 3.0 |
| LW concrete | 100.000 | 2000.0 | 0.84 | 0.07407 | 200.0 |
| Waterproofing/isogume or similar | 4.000 | 1000.0 | 1.67 | 0.01739 | 4.0 |
| Cement plaster | 20.000 | 750.0 | 0.80 | 0.06666 | 15.0 |
| Terrazzo tile | 25.000 | 2000.0 | 0.84 | 0.01852 | 50.0 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| Totals | 399.000 | - |  | 1.86449 | 752.0 |

U.W.-1

Window Details:

Detailed Input 	 Yes

Height 	 1.20	m

Width 	 1.00	m

Frame Type 	 Vinyl

Internal Shade Type 	 None

Overall U-Value 	 2.819	W/(m²-°K)

Overall Shade Coefficient 	 0.700

Glass Details:

Gap Type 	 6mm Argon

| Glazing | Glass Type | Transmissivity | Reflectivity | Absorptivity |
| --- | --- | --- | --- | --- |
| Outer Glazing | 6mm clear | 0.792 | 0.079 | 0.129 |
| Glazing #2 | 6mm clear | 0.792 | 0.079 | 0.129 |
| Glazing #3 | not used | 1.000 | 0.000 | 0.000 |

M.D.-1

Door Details:

Gross Area 	 2.4	m²

Door U-Value 	 5.800	W/(m²-°K)

Glass Details:

Glass Area 	 0.0	m²

Glass U-Value 	 3.293	W/(m²-°K)

Glass Shade Coefficient 	 0.880

Glass Shaded All Day? 	 No

# CCTV CONTROL ROOM - BINAK pu

Wall (gypsum plaster)

Wall Details

D01

Outside Surface Color 	 Medium

Absorptivity 	 0.675

Overall U-Value 	 0.495	W/(m²-°K)

Wall Layers Details (Inside to Outside)

|  | Thickness | Density | Specific Ht. | R-Value | Weight |
| --- | --- | --- | --- | --- | --- |
| Layers | mm | kg/m³ | kJ / (kg - °K) | (m²-°K)/W | kg/m² |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| Gypsum plaster | 20.000 | 1300.0 | 1.17 | 0.03571 | 26.0 |
| Wall brick | 200.000 | 2000.0 | 0.20 | 0.28000 | 400.0 |
| HDPU | 50.000 | 50.0 | 0.05 | 1.42857 | 2.5 |
| Cement plaster | 20.000 | 750.0 | 0.80 | 0.06667 | 15.0 |
| Face brick | 30.000 | 2000.0 | 0.03 | 0.03000 | 60.0 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| Totals | 320.000 | - |  | 2.02023 | 503.5 |

Wall (marmarit stone)

Wall Details

Outside Surface Color 	 Medium

Absorptivity 	 0.675

Overall U-Value 	 0.484	W/(m²-°K)

Wall Layers Details (Inside to Outside)

|  | Thickness | Density | Specific Ht. | R-Value | Weight |
| --- | --- | --- | --- | --- | --- |
| Layers | mm | kg/m³ | kJ / (kg - °K) | (m²-°K)/W | kg/m² |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| Marmarit stone | 50.000 | 2700.0 | 1.26 | 0.01429 | 135.0 |
| Cement plaster | 20.000 | 750.0 | 0.80 | 0.06667 | 15.0 |
| Wall brick | 200.000 | 2000.0 | 0.20 | 0.28000 | 400.0 |
| HDPU | 50.000 | 40.0 | 0.05 | 1.42857 | 2.0 |
| Cement plaster | 20.000 | 750.0 | 0.80 | 0.06667 | 15.0 |
| Face brick | 30.000 | 2000.0 | 0.03 | 0.03000 | 60.0 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| Totals | 370.000 | - |  | 2.06548 | 627.0 |

Roof-HDPU

Roof Details

Outside Surface Color 	 Medium

Absorptivity 	 0.675

Overall U-Value 	 0.536	W/(m²-°K)

Roof Layers Details (Inside to Outside)

|  | Thickness | Density | Specific Ht. | R-Value | Weight |
| --- | --- | --- | --- | --- | --- |
| Layers | mm | kg/m³ | kJ / (kg - °K) | (m²-°K)/W | kg/m² |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| HW concrete | 200.000 | 2400.0 | 0.84 | 0.08000 | 480.0 |
| HDPU | 50.000 | 60.0 | 0.84 | 1.42857 | 3.0 |
| LW concrete | 100.000 | 2000.0 | 0.84 | 0.07407 | 200.0 |
| Waterproofing/isogume or similar | 4.000 | 1000.0 | 1.67 | 0.01739 | 4.0 |
| Cement plaster | 20.000 | 750.0 | 0.80 | 0.06666 | 15.0 |
| Terrazzo tile | 25.000 | 2000.0 | 0.84 | 0.01852 | 50.0 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| Totals | 399.000 | - |  | 1.86449 | 752.0 |

U.W.-1

Window Details:

Detailed Input 	 Yes

Height 	 1.20	m

Width 	 0.70	m

Frame Type 	 Vinyl

Internal Shade Type 	 None

Overall U-Value 	 2.819	W/(m²-°K)

Overall Shade Coefficient 	 0.700

Glass Details:

Gap Type 	 6mm Argon

| Glazing | Glass Type | Transmissivity | Reflectivity | Absorptivity |
| --- | --- | --- | --- | --- |
| Outer Glazing | 6mm clear | 0.792 | 0.079 | 0.129 |
| Glazing #2 | 6mm clear | 0.792 | 0.079 | 0.129 |
| Glazing #3 | not used | 1.000 | 0.000 | 0.000 |

U.W.-2

Window Details:

Detailed Input 	 Yes

Height 	 1.20	m

Width 	 1.50	m

Frame Type 	 Vinyl

Internal Shade Type 	 None

Overall U-Value 	 2.845	W/(m²-°K)

Overall Shade Coefficient 	 0.700

Glass Details:

Gap Type 	 6mm Argon

| Glazing | Glass Type | Transmissivity | Reflectivity | Absorptivity |
| --- | --- | --- | --- | --- |
| Outer Glazing | 6mm clear | 0.792 | 0.079 | 0.129 |
| Glazing #2 | 6mm clear | 0.792 | 0.079 | 0.129 |
| Glazing #3 | not used | 1.000 | 0.000 | 0.000 |

M.D.-1

Door Details:

Gross Area 	 2.2	m²

Door U-Value 	 5.800	W/(m²-°K)

Glass Details:

Glass Area 	 0.0	m²

Glass U-Value 	 3.293	W/(m²-°K)

Glass Shade Coefficient 	 0.880

Glass Shaded All Day? 	 No

D01

SPACE INPUT DATA:

# CCTV CONTROL ROOM - BINAK GCS

00-Control Room

1. General Details:

Floor Area 	 46.6	m²

Avg. Ceiling Height 	 3.2	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 11.90 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 500.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 5.0 People

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 People

2.5. Miscellaneous Loads:

Sensible 	 0 W

Schedule 	 None

Latent 	 0 W

Schedule 	 None

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| ENE | 18.9 | 0 | 0 | 0 |
| SSE | 24.6 | 0 | 0 | 0 |
| NNW | 24.6 | 0 | 0 | 0 |

3.1. Construction Types for Exposure NNW

Wall Type 	 Wall (MDF)

3.2. Construction Types for Exposure ENE

Wall Type 	 Wall (MDF)

3.3. Construction Types for Exposure WSW

Wall Type 	 Wall (MDF)

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 46.6 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	  Roof-HDPU

5. Infiltration:

Design Cooling 	 0.00	ACH

Design Heating 	 0.00	ACH

Energy Analysis 	 0.00	ACH

Infiltration occurs at all hours.

6. Floors:

Type 	 Slab Floor On Grade

Floor Area 	 46.6	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Exposed Perimeter 	 21.6	m

Edge Insulation R-Value 	 0.00	(m²-°K)/W

7. Partitions:

7.1. 1st Partition Details:

Partition Type 	 Wall Partition

Area 	 6.6	m²

U-Value 	 0.761	W/(m²-°K)

Uncondit. Space Max Temp 	 35.0	°C

Ambient at Space Max Temp 	 41.0	°C

Uncondit. Space Min Temp 	 12.5	°C

Ambient at Space Min Temp 	 6.0	°C

7.2. 2nd Partition Details:

(No partition data).

D01

01-Rack Room

1. General Details:

Floor Area 	 10.0	m²

Avg. Ceiling Height 	 3.2	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 10.20 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 2500.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 0.0 Person

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 None

2.5. Miscellaneous Loads:

Sensible 	 0 W

Schedule 	 None

Latent 	 0 W

Schedule 	 None

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| SSE | 12.6 | 0 | 0 | 0 |
| WSW | 7.9 | 0 | 0 | 0 |

3.1. Construction Types for Exposure ENE

Wall Type 	 Wall (Stone)-Rock Wool

3.2. Construction Types for Exposure SSE

Wall Type 	 Wall (Stone)-Rock Wool)

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 10.0 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	 Roof

5. Infiltration:

Design Cooling 	 0.00	ACH

Design Heating 	 0.00	ACH

Energy Analysis 	 0.00	ACH

Infiltration occurs at all hours.

6. Floors:

Type 	 Floor Above Unconditioned Space

Floor Area 	 10.0	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Unconditioned Space Max Temp. 	 35.0	°C

Ambient at Space Max Temp. 	 41.0	°C

Unconditioned Space Min Temp. 	 12.5	°C

Ambient at Space Min Temp. 	 6.0	°C

7. Partitions:

(No partition data).

02-Entrance

D01

1. General Details:

Floor Area 	 4.8	m²

Avg. Ceiling Height 	 3.2	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 7.00 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 500.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 0.0 Person

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 None

2.5. Miscellaneous Loads:

Sensible 	 0 W

Schedule 	 None

Latent 	 0 W

Schedule 	 None

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| WSW | 3.8 | 0 | 0 | 1 |

3.1. Construction Types for Exposure SSE

Wall Type 	  Wall (gypsum plaster)

Door Type 	 M.D.-1

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 4.8 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	 Roof-HDPU

5. Infiltration:

Design Cooling 	 74.33	L/s

Design Heating 	 74.33	L/s

Energy Analysis 	 74.33	L/s

Infiltration occurs at all hours.

6. Floors:

Type 	 Slab Floor On Grade

Floor Area 	 4.8	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Exposed Perimeter 	 1.2	m

Edge Insulation R-Value 	 0.00	(m²-°K)/W

7. Partitions:

7.1. 1st Partition Details:

Partition Type 	 Wall Partition

Area 	 6.0	m²

U-Value 	 0.761	W/(m²-°K)

Uncondit. Space Max Temp 	 35.0	°C

Ambient at Space Max Temp 	 41.0	°C

Uncondit. Space Min Temp 	 12.5	°C

Ambient at Space Min Temp 	 6.0	°C

7.2. 2nd Partition Details:

(No partition data).

D01

03-Pantry

1. General Details:

Floor Area 	 4.2	m²

Avg. Ceiling Height 	 3.2	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 10.70 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 600.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 0.0 Person

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 None

2.5. Miscellaneous Loads:

Sensible 	 1000 W

Schedule 	 Electrical Eq.

Latent 	 700 W

Schedule 	 Electrical Eq.

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| NNW | 6.3 | 1 | 0 | 0 |
| WSW | 6.6 | 0 | 0 | 0 |

3.1. Construction Types for Exposure WSW

Wall Type 	 Wall (Ceramic tile)

1st Window Type 	 U.W.-1

3.2. Construction Types for Exposure SSE

Wall Type 	 Wall (Ceramic tile)

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 4.2 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	 Roof-HDPU

5. Infiltration:

Design Cooling 	 21.83	L/s

Design Heating 	 21.83	L/s

Energy Analysis 	 21.83	L/s

Infiltration occurs at all hours.

6. Floors:

Type 	 Slab Floor On Grade

Floor Area 	 4.2	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Exposed Perimeter 	 4.1	m

Edge Insulation R-Value 	 0.00	(m²-°K)/W

7. Partitions:

7.1. 1st Partition Details:

Partition Type 	 Wall Partition

Area 	 6.6	m²

U-Value 	 0.761	W/(m²-°K)

Uncondit. Space Max Temp 	 35.0	°C

Ambient at Space Max Temp 	 41.0	°C

Uncondit. Space Min Temp 	 12.5	°C

Ambient at Space Min Temp 	 6.0	°C

7.2. 2nd Partition Details:

(No partition data).

D01

CCTV CONTROL ROOM - BINAK DU

00-Control Room

1. General Details:

Floor Area 	 46.6	m²

Avg. Ceiling Height 	 3.2	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 11.90 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 500.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 5.0 People

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 People

2.5. Miscellaneous Loads:

Sensible 	 0 W

Schedule 	 None

Latent 	 0 W

Schedule 	 None

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| ESE | 18.9 | 0 | 0 | 0 |
| NNE | 24.6 | 0 | 0 | 0 |
| SSW | 24.6 | 0 | 0 | 0 |

3.1. Construction Types for Exposure NNW

Wall Type 	 Wall (MDF)

3.2. Construction Types for Exposure ENE

Wall Type 	 Wall (MDF)

3.3. Construction Types for Exposure WSW

Wall Type 	 Wall (MDF)

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 46.6 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	  Roof-HDPU

5. Infiltration:

Design Cooling 	 0.00	ACH

Design Heating 	 0.00	ACH

Energy Analysis 	 0.00	ACH

Infiltration occurs at all hours.

6. Floors:

Type 	 Slab Floor On Grade

Floor Area 	 46.6	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Exposed Perimeter 	 21.6	m

Edge Insulation R-Value 	 0.00	(m²-°K)/W

7. Partitions:

7.1. 1st Partition Details:

Partition Type 	 Wall Partition

Area 	 6.6	m²

U-Value 	 0.761	W/(m²-°K)

Uncondit. Space Max Temp 	 35.0	°C

Ambient at Space Max Temp 	 41.0	°C

Uncondit. Space Min Temp 	 12.5	°C

Ambient at Space Min Temp 	 6.0	°C

7.2. 2nd Partition Details:

(No partition data).

01-Rack Room

1. General Details:

Floor Area 	 10.0	m²

D01

Avg. Ceiling Height 	 3.2	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 10.20 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 2500.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 0.0 Person

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 None

2.5. Miscellaneous Loads:

Sensible 	 0 W

Schedule 	 None

Latent 	 0 W

Schedule 	 None

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| SSW | 12.6 | 0 | 0 | 0 |
| WNW | 7.9 | 0 | 0 | 0 |

3.1. Construction Types for Exposure ENE

Wall Type 	 Wall (Stone)-Rock Wool

3.2. Construction Types for Exposure SSE

Wall Type 	 Wall (Stone)-Rock Wool)

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 10.0 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	 Roof

5. Infiltration:

Design Cooling 	 0.00	ACH

Design Heating 	 0.00	ACH

Energy Analysis 	 0.00	ACH

Infiltration occurs at all hours.

6. Floors:

Type 	 Floor Above Unconditioned Space

Floor Area 	 10.0	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Unconditioned Space Max Temp. 	 35.0	°C

Ambient at Space Max Temp. 	 41.0	°C

Unconditioned Space Min Temp. 	 12.5	°C

Ambient at Space Min Temp. 	 6.0	°C

7. Partitions:

(No partition data).

D01

02-Entrance

1. General Details:

Floor Area 	 4.8	m²

Avg. Ceiling Height 	 3.2	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 7.00 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 500.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 0.0 Person

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 None

2.5. Miscellaneous Loads:

Sensible 	 0 W

Schedule 	 None

Latent 	 0 W

Schedule 	 None

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| WNW | 3.8 | 0 | 0 | 1 |

3.1. Construction Types for Exposure SSE

Wall Type 	  Wall (gypsum plaster)

Door Type 	 M.D.-1

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 4.8 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	 Roof-HDPU

5. Infiltration:

Design Cooling 	 74.33	L/s

Design Heating 	 74.33	L/s

Energy Analysis 	 74.33	L/s

Infiltration occurs at all hours.

6. Floors:

Type 	 Slab Floor On Grade

Floor Area 	 4.8	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Exposed Perimeter 	 1.2	m

Edge Insulation R-Value 	 0.00	(m²-°K)/W

7. Partitions:

7.1. 1st Partition Details:

Partition Type 	 Wall Partition

Area 	 6.0	m²

U-Value 	 0.761	W/(m²-°K)

Uncondit. Space Max Temp 	 35.0	°C

Ambient at Space Max Temp 	 41.0	°C

Uncondit. Space Min Temp 	 12.5	°C

Ambient at Space Min Temp 	 6.0	°C

7.2. 2nd Partition Details:

(No partition data).

D01

03-Pantry

1. General Details:

Floor Area 	 4.2	m²

Avg. Ceiling Height 	 3.2	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 10.70 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 600.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 0.0 Person

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 None

2.5. Miscellaneous Loads:

Sensible 	 1000 W

Schedule 	 Electrical Eq.

Latent 	 700 W

Schedule 	 Electrical Eq.

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| NNE | 6.3 | 1 | 0 | 0 |
| WNW | 6.6 | 0 | 0 | 0 |

3.1. Construction Types for Exposure WSW

Wall Type 	 Wall (Ceramic tile)

1st Window Type 	 U.W.-1

3.2. Construction Types for Exposure SSE

Wall Type 	 Wall (Ceramic tile)

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 4.2 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	 Roof-HDPU

5. Infiltration:

Design Cooling 	 21.83	L/s

Design Heating 	 21.83	L/s

Energy Analysis 	 21.83	L/s

Infiltration occurs at all hours.

6. Floors:

Type 	 Slab Floor On Grade

Floor Area 	 4.2	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Exposed Perimeter 	 4.1	m

Edge Insulation R-Value 	 0.00	(m²-°K)/W

7. Partitions:

7.1. 1st Partition Details:

Partition Type 	 Wall Partition

Area 	 6.6	m²

U-Value 	 0.761	W/(m²-°K)

Uncondit. Space Max Temp 	 35.0	°C

Ambient at Space Max Temp 	 41.0	°C

Uncondit. Space Min Temp 	 12.5	°C

Ambient at Space Min Temp 	 6.0	°C

7.2. 2nd Partition Details:

(No partition data).

D01

CCTV CONTROL ROOM - BINAK pu

00-Guard House

1. General Details:

Floor Area 	 4.7	m²

Avg. Ceiling Height 	 2.8	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 11.90 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 100.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 2.0 People

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 People

2.5. Miscellaneous Loads:

Sensible 	 0 W

Schedule 	 None

Latent 	 0 W

Schedule 	 None

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| N | 5.7 | 1 | 0 | 1 |
| S | 5.7 | 1 | 0 | 0 |
| E | 6.4 | 1 | 0 | 0 |

3.1. Construction Types for Exposure N

Wall Type 	 Wall (gypsum plaster)

1st Window Type 	 U.W.-1

Door Type 	 M.D.-1

3.2. Construction Types for Exposure S

Wall Type 	 Wall (gypsum plaster)

1st Window Type 	 U.W.-2

3.3. Construction Types for Exposure E

Wall Type 	 Wall (gypsum plaster)

1st Window Type 	 U.W.-2

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 4.7 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	 Roof-HDPU

5. Infiltration:

Design Cooling 	 2.00	ACH

Design Heating 	 2.00	ACH

Energy Analysis 	 2.00	ACH

Infiltration occurs at all hours.

6. Floors:

Type 	 Slab Floor On Grade

Floor Area 	 4.7	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Exposed Perimeter 	 10.5	m

Edge Insulation R-Value 	 0.00	(m²-°K)/W

7. Partitions:

(No partition data).

D01

01-Rack Room

1. General Details:

Floor Area 	 2.6	m²

Avg. Ceiling Height 	 2.8	m

Building Weight 	 341.8	kg/m²

1.1. OA Ventilation Requirements:

Space Usage 	 User-Defined

OA Requirement 1 	 0.0	L/s/person

OA Requirement 2 	 0.00	L/(s-m²)

Space Usage Defaults 	 ASHRAE Standard 62.1-2010

2. Internals:

2.1. Overhead Lighting:

Fixture Type 	 Recessed (Unvented)

Wattage 	 10.20 W/m²

Ballast Multiplier 	 1.25

Schedule 	 Lighting

2.2. Task Lighting:

Wattage 	 0.00 W/m²

Schedule 	 None

2.3. Electrical Equipment:

Wattage 	 1000.0 Watts

Schedule 	 Electrical Eq.

2.4. People:

Occupancy 	 0.0 Person

Activity Level 	 Office Work

Sensible 	 71.8 W/person

Latent 	 60.1 W/person

Schedule 	 None

2.5. Miscellaneous Loads:

Sensible 	 0 W

Schedule 	 None

Latent 	 0 W

Schedule 	 None

3. Walls, Windows, Doors:

| Exp. | Wall Gross Area (m²) | Window 1 Qty. | Window 2 Qty. | Door 1 Qty. |
| --- | --- | --- | --- | --- |
| N | 3.2 | 0 | 0 | 0 |
| W | 6.4 | 0 | 0 | 1 |
| S | 3.2 | 0 | 0 | 0 |

3.1. Construction Types for Exposure N

Wall Type 	 Wall (marmarit stone)

3.2. Construction Types for Exposure W

Wall Type 	 Wall (marmarit stone)

Door Type 	 M.D.-1

3.3. Construction Types for Exposure S

Wall Type 	 Wall (marmarit stone)

4. Roofs, Skylights:

| Exp. | Roof Gross Area (m²) | Roof Slope (deg.) | Skylight Qty. |
| --- | --- | --- | --- |
| H | 2.6 | 0 | 0 |

4.1. Construction Types for Exposure H

Roof Type 	 Roof-HDPU

5. Infiltration:

Design Cooling 	 0.00	ACH

Design Heating 	 0.00	L/(s-m²)

Energy Analysis 	 0.00	L/s

Infiltration occurs at all hours.

6. Floors:

Type 	 Floor Above Unconditioned Space

Floor Area 	 2.6	m²

Total Floor U-Value 	 0.568	W/(m²-°K)

Unconditioned Space Max Temp. 	 35.0	°C

Ambient at Space Max Temp. 	 41.0	°C

Unconditioned Space Min Temp. 	 12.5	°C

Ambient at Space Min Temp. 	 6.0	°C

7. Partitions:

(No partition data).

## SYSTEM INPUT DATA:

# CCTV CONTROL ROOM - BINAK GCS & DU

1. General Details:

Air System Name 	 System

Equipment Type 	 Terminal Units

Air System Type 	 Split DX Fan Coil

Number of zones 	 2

Ventilation 	 Direct Ventilation

2. Ventilation System Components:

(Common Ventilation System not used: no inputs)

3. Zone Components:

Space Assignments:

| Zone 1: Zone 1 |  |
| --- | --- |
| 00-Control Room | x1 |
| 02-Entrance | x1 |
| 03-Pantry | x1 |
| Zone 2: Zone 2 |  |
| 01-Rack Room | x1 |

Thermostats and Zone Data:

| Zone | Cooling T-Stat Occ. | Cooling T-Stat Unocc. | Heating T-Stat Occ. | Heating T-Stat Unocc. | T-Stat Throttling Range |
| --- | --- | --- | --- | --- | --- |
|  | (°C) | (°C) | (°C) | (°C) | (°C) |
| 1 | 24.0 | 27.0 | 22.0 | 18.0 | 0.83 |
| 2 | 30.0 | 30.0 | 10.0 | 10.0 | 0.83 |

Thermostat Schedule 	 Fan

Unoccupied Cooling is 	 Available

Common Terminal Unit Data:

Cooling Coil:

Design Supply Temperature 	 14.4	°C

Coil Bypass Factor 	 0.100

Cooling Source 	 Air-Cooled DX

Schedule 	 JFMAMJJASOND

Heating Coil:

Design Supply Temperature 	 35.0	°C

Heating Source 	 Air Source Heat Pump

Schedule 	 JFMAMJJASOND

Fan Control 	 Fan On

Ventilation Sizing Method 	 Sum of Space OA Airflows

Terminal Units Data:

Zone 	 All

Terminal Type 	 Fan Coil

Minimum Airflow 	 0.00	L/s/person

Fan Performance 	 0	Pa

Fan Overall Efficiency 	 50	%

4. Sizing Data (Computer-Generated):

System Sizing Data:

Sizing Data:

Cooling Supply Temperature 	 14.4	°C

Heating Supply Temperature 	 35.0	°C

Hydronic Sizing Specifications:

Chilled Water Delta-T 	 5.6	°K

Hot Water Delta-T 	 11.1	°K

Safety Factors:

Cooling Sensible 	 10	%

Cooling Latent 	 10	%

Heating 	 10	%

# CCTV CONTROL ROOM - BINAK pu

1. General Details:

Air System Name 	 System

Equipment Type 	 Terminal Units

Air System Type 	 Split DX Fan Coil

Number of zones 	 2

Ventilation 	 Direct Ventilation

2. Ventilation System Components:

(Common Ventilation System not used: no inputs)

3. Zone Components:

Space Assignments:

| Zone 1: Zone 1 |  |
| --- | --- |
| 00-Guard House | x1 |
| Zone 2: Zone 2 |  |
| 01-Rack Room | x1 |

Thermostats and Zone Data:

| Zone | Cooling T-Stat Occ. | Cooling T-Stat Unocc. | Heating T-Stat Occ. | Heating T-Stat Unocc. | T-Stat Throttling Range |
| --- | --- | --- | --- | --- | --- |
|  | (°C) | (°C) | (°C) | (°C) | (°C) |
| 1 | 24.0 | 27.0 | 22.0 | 18.0 | 0.83 |
| 2 | 30.0 | 30.0 | 10.0 | 10.0 | 0.83 |

Thermostat Schedule 	 Fan

Unoccupied Cooling is 	 Available

Common Terminal Unit Data:

Cooling Coil:

Design Supply Temperature 	 14.4	°C

Coil Bypass Factor 	 0.100

Cooling Source 	 Air-Cooled DX

Schedule 	 JFMAMJJASOND

Heating Coil:

Design Supply Temperature 	 35.0	°C

Heating Source 	 Air Source Heat Pump

Schedule 	 JFMAMJJASOND

Fan Control 	 Fan On

Ventilation Sizing Method 	 Sum of Space OA Airflows

Terminal Units Data:

Zone 	 All

Terminal Type 	 Fan Coil

Minimum Airflow 	 0.00	L/s/person

Fan Performance 	 0	Pa

Fan Overall Efficiency 	 50	%

4. Sizing Data (Computer-Generated):

System Sizing Data:

Sizing Data:

Cooling Supply Temperature 	 14.4	°C

Heating Supply Temperature 	 35.0	°C

Hydronic Sizing Specifications:

Chilled Water Delta-T 	 5.6	°K

Hot Water Delta-T 	 11.1	°K

Safety Factors:

Cooling Sensible 	 10	%

Cooling Latent 	 10	%

Heating 	 10	%

D01

AIR SYSTEM SIZING SUMMARY:

# CCTV CONTROL ROOM - BINAK GCS

Air System Information

Air System Name 	 System

Equipment Class 	 TERM

Air System Type 	 SPLT-FC

Number of zones 	 2

Floor Area 	 65.6	m²

Location 	 Binak, IRAN

Sizing Calculation Information

Calculation Months 	 Jan to Dec

Sizing Data 	 Calculated	
Zone L/s Sizing 	 Sum of space airflow rates

Space L/s Sizing 	 Individual peak space loads

Zone Sizing Data

|  | Maximum |  |  |  | Maximum | Zone |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Cooling | Design | Minimum |  | Heating | Floor |  |
|  | Sensible | Airflow | Airflow | Time of | Load | Area | Zone |
| Zone Name | (kW) | (L/s) | (L/s) | Peak Load | (kW) | (m²) | L/(s-m²) |
| Zone 1 | 6.7 | 627 | 627 | Jul 1500 | 3.5 | 55.6 | 11.28 |
| Zone 2 | 2.9 | 155 | 155 | Jul 0800 | 0.0 | 10.0 | 15.51 |

Terminal Unit Sizing Data - Cooling

|  | Total | Sens | Coil | Coil | Water | Time |
| --- | --- | --- | --- | --- | --- | --- |
|  | Coil | Coil | Entering | Leaving | Flow | of |
|  | Load | Load | DB / WB | DB / WB | @ 5.6 °K | Peak |
| Zone Name | (kW) | (kW) | (°C) | (°C) | (L/s) | Load |
| Zone 1 | 11.4 | 6.8 | 24.5 / 20.3 | 15.7 / 15.3 | - | Jun 1600 |
| Zone 2 | 3.8 | 2.9 | 30.6 / 21.0 | 15.0 / 14.2 | - | Aug 2000 |

Terminal Unit Sizing Data - Heating, Fan, Ventilation

|  |  | Heating | Htg Coil |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Heating | Coil | Water | Fan |  |  | OA Vent |
|  | Coil | Ent/Lvg | Flow | Design | Fan | Fan | Design |
|  | Load | DB | @11.1 °K | Airflow | Motor | Motor | Airflow |
| Zone Name | (kW) | (°C) | (L/s) | (L/s) | (BHP) | (kW) | (L/s) |
| Zone 1 | 3.9 | 21.7 / 26.7 | - | 639 | 0.000 | 0.000 | 0 |
| Zone 2 | 0.3 | 21.4 / 23.1 | - | 157 | 0.000 | 0.000 | 0 |

Space Loads and Airflows

|  |  | Cooling | Time | Air | Heating | Floor |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Zone Name / |  | Sensible | of | Flow | Load | Area | Space |
| Space Name | Mult. | (kW) | Load | (L/s) | (kW) | (m²) | L/(s-m²) |
| Zone 1 |  |  |  |  |  |  |  |
| 00-Control Room | 1 | 2.2 | Jul 0800 | 192 | 1.2 | 46.6 | 4.12 |
| 02-Entrance | 1 | 2.5 | Jul 1500 | 221 | 1.9 | 4.8 | 45.99 |
| 03-Pantry | 1 | 2.6 | Jul 1600 | 227 | 0.7 | 4.2 | 53.93 |
| Zone 2 |  |  |  |  |  |  |  |
| 01-Rack Room | 1 | 2.9 | Aug 2100 | 157 | 0.1 | 10.0 | 15.73 |

D01

CCTV CONTROL ROOM - BINAK DU

Air System Information

Air System Name 	 System

Equipment Class 	 TERM

Air System Type 	 SPLT-FC

Number of zones 	 2

Floor Area 	 65.6	m²

Location 	 Binak, IRAN

Sizing Calculation Information

Calculation Months 	 Jan to Dec

Sizing Data 	 Calculated	
Zone L/s Sizing 	 Sum of space airflow rates

Space L/s Sizing 	 Individual peak space loads

Zone Sizing Data

|  | Maximum |  |  |  | Maximum | Zone |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Cooling | Design | Minimum |  | Heating | Floor |  |
|  | Sensible | Airflow | Airflow | Time of | Load | Area | Zone |
| Zone Name | (kW) | (L/s) | (L/s) | Peak Load | (kW) | (m²) | L/(s-m²) |
| Zone 1 | 7.0 | 637 | 637 | Jul 1500 | 3.9 | 55.6 | 11.45 |
| Zone 2 | 2.9 | 157 | 157 | Aug 2200 | 0.1 | 10.0 | 15.73 |

Terminal Unit Sizing Data - Cooling

|  | Total | Sens | Coil | Coil | Water | Time |
| --- | --- | --- | --- | --- | --- | --- |
|  | Coil | Coil | Entering | Leaving | Flow | of |
|  | Load | Load | DB / WB | DB / WB | @ 5.6 °K | Peak |
| Zone Name | (kW) | (kW) | (°C) | (°C) | (L/s) | Load |
| Zone 1 | 11.3 | 6.8 | 24.7 / 20.3 | 15.8 / 15.5 | - | Jul 1500 |
| Zone 2 | 3.8 | 2.9 | 30.6 / 21.0 | 15.1 / 14.2 | - | Jun 2100 |

Terminal Unit Sizing Data - Heating, Fan, Ventilation

|  |  | Heating | Htg Coil |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Heating | Coil | Water | Fan |  |  | OA Vent |
|  | Coil | Ent/Lvg | Flow | Design | Fan | Fan | Design |
|  | Load | DB | @11.1 °K | Airflow | Motor | Motor | Airflow |
| Zone Name | (kW) | (°C) | (L/s) | (L/s) | (BHP) | (kW) | (L/s) |
| Zone 1 | 3.9 | 21.7 / 26.7 | - | 637 | 0.000 | 0.000 | 0 |
| Zone 2 | 0.3 | 21.4 / 23.1 | - | 157 | 0.000 | 0.000 | 0 |

Space Loads and Airflows

|  |  | Cooling | Time | Air | Heating | Floor |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Zone Name / |  | Sensible | of | Flow | Load | Area | Space |
| Space Name | Mult. | (kW) | Load | (L/s) | (kW) | (m²) | L/(s-m²) |
| Zone 1 |  |  |  |  |  |  |  |
| 00-Control Room | 1 | 2.2 | Jul 0800 | 192 | 1.2 | 46.6 | 4.12 |
| 02-Entrance | 1 | 2.5 | Jul 1500 | 221 | 1.9 | 4.8 | 45.98 |
| 03-Pantry | 1 | 2.6 | Jul 1500 | 224 | 0.7 | 4.2 | 53.34 |
| Zone 2 |  |  |  |  |  |  |  |
| 01-Rack Room | 1 | 2.9 | Aug 2200 | 157 | 0.1 | 10.0 | 15.73 |

D01

CCTV CONTROL ROOM - BINAK pu

Air System Information

Air System Name 	 System

Equipment Class 	 TERM

Air System Type 	 SPLT-FC

Number of zones 	 2

Floor Area 	 7.3	m²

Location 	 Binak, IRAN

Sizing Calculation Information

Calculation Months 	 Jan to Dec

Sizing Data 	 Calculated	
Zone L/s Sizing 	 Sum of space airflow rates

Space L/s Sizing 	 Individual peak space loads

Zone Sizing Data

|  | Maximum |  |  |  | Maximum | Zone |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Cooling | Design | Minimum |  | Heating | Floor |  |
|  | Sensible | Airflow | Airflow | Time of | Load | Area | Zone |
| Zone Name | (kW) | (L/s) | (L/s) | Peak Load | (kW) | (m²) | L/(s-m²) |
| Zone 1 | 1.5 | 127 | 127 | Sep 1400 | 0.8 | 4.7 | 27.05 |
| Zone 2 | 1.3 | 67 | 67 | Jul 1600 | 0.1 | 2.6 | 25.93 |

Terminal Unit Sizing Data - Cooling

|  | Total | Sens | Coil | Coil | Water | Time |
| --- | --- | --- | --- | --- | --- | --- |
|  | Coil | Coil | Entering | Leaving | Flow | of |
|  | Load | Load | DB / WB | DB / WB | @ 5.6 °K | Peak |
| Zone Name | (kW) | (kW) | (°C) | (°C) | (L/s) | Load |
| Zone 1 | 1.8 | 1.4 | 24.6 / 18.6 | 15.2 / 14.6 | - | Sep 1400 |
| Zone 2 | 1.4 | 1.2 | 30.8 / 20.4 | 15.4 / 14.5 | - | Aug 1600 |

Terminal Unit Sizing Data - Heating, Fan, Ventilation

|  |  | Heating | Htg Coil |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Heating | Coil | Water | Fan |  |  | OA Vent |
|  | Coil | Ent/Lvg | Flow | Design | Fan | Fan | Design |
|  | Load | DB | @11.1 °K | Airflow | Motor | Motor | Airflow |
| Zone Name | (kW) | (°C) | (L/s) | (L/s) | (BHP) | (kW) | (L/s) |
| Zone 1 | 0.7 | 21.6 / 26.5 | - | 127 | 0.000 | 0.000 | 0 |
| Zone 2 | 0.3 | 19.5 / 22.9 | - | 67 | 0.000 | 0.000 | 0 |

Space Loads and Airflows

|  |  | Cooling | Time | Air | Heating | Floor |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Zone Name / |  | Sensible | of | Flow | Load | Area | Space |
| Space Name | Mult. | (kW) | Load | (L/s) | (kW) | (m²) | L/(s-m²) |
| Zone 1 |  |  |  |  |  |  |  |
| 00-Guard House | 1 | 1.5 | Sep 1400 | 127 | 0.8 | 4.7 | 27.05 |
| Zone 2 |  |  |  |  |  |  |  |
| 01-Rack Room | 1 | 1.3 | Jul 1600 | 67 | 0.1 | 2.6 | 25.93 |

D01

ventilation sizing summary

# CCTV CONTROL ROOM - BINAK GCS

1. Summary

Ventilation Sizing Method 	 Sum of Space OA Airflows

2. Space Ventilation Analysis Table

|  |  | Floor |  | Maximum | Required | Required | Required | Required | Uncorrected |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Area | Maximum | Supply Air | Outdoor Air | Outdoor Air | Outdoor Air | Outdoor Air | Outdoor Air |
| Zone Name / Space Name | Mult. | (m²) | Occupants | (L/s) | (L/s/person) | (L/(s-m²)) | (L/s) | (% of supply) | (L/s) |
| Zone 1 |  |  |  |  |  |  |  |  |  |
| 00-Control Room | 1 | 46.6 | 5.0 | 192.1 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| 02-Entrance | 1 | 4.8 | 0.0 | 220.7 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| 03-Pantry | 1 | 4.2 | 0.0 | 226.5 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| Zone 2 |  |  |  |  |  |  |  |  |  |
| 01-Rack Room | 1 | 10.0 | 0.0 | 157.3 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| Totals (incl. Space Multipliers) |  |  |  | 796.7 |  |  |  |  | 0.0 |

# CCTV CONTROL ROOM - BINAK DU

1. Summary

Ventilation Sizing Method 	 Sum of Space OA Airflows

2. Space Ventilation Analysis Table

|  |  | Floor |  | Maximum | Required | Required | Required | Required | Uncorrected |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Area | Maximum | Supply Air | Outdoor Air | Outdoor Air | Outdoor Air | Outdoor Air | Outdoor Air |
| Zone Name / Space Name | Mult. | (m²) | Occupants | (L/s) | (L/s/person) | (L/(s-m²)) | (L/s) | (% of supply) | (L/s) |
| Zone 1 |  |  |  |  |  |  |  |  |  |
| 00-Control Room | 1 | 46.6 | 5.0 | 191.9 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| 02-Entrance | 1 | 4.8 | 0.0 | 220.7 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| 03-Pantry | 1 | 4.2 | 0.0 | 224.0 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| Zone 2 |  |  |  |  |  |  |  |  |  |
| 01-Rack Room | 1 | 10.0 | 0.0 | 157.3 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| Totals (incl. Space Multipliers) |  |  |  | 793.9 |  |  |  |  | 0.0 |

# CCTV CONTROL ROOM - BINAK pu

1. Summary

Ventilation Sizing Method 	 Sum of Space OA Airflows

2. Space Ventilation Analysis Table

|  |  | Floor |  | Maximum | Required | Required | Required | Required | Uncorrected |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Area | Maximum | Supply Air | Outdoor Air | Outdoor Air | Outdoor Air | Outdoor Air | Outdoor Air |
| Zone Name / Space Name | Mult. | (m²) | Occupants | (L/s) | (L/s/person) | (L/(s-m²)) | (L/s) | (% of supply) | (L/s) |
| Zone 1 |  |  |  |  |  |  |  |  |  |
| 00-Guard House | 1 | 4.7 | 2.0 | 127.1 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| Zone 2 |  |  |  |  |  |  |  |  |  |
| 01-Rack Room | 1 | 2.6 | 0.0 | 67.4 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 |
| Totals (incl. Space Multipliers) |  |  |  | 194.6 |  |  |  |  | 0.0 |

D01

air system design load summary:

# CCTV CONTROL ROOM - BINAK GCS

|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Jul 1500 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 41.0 °C / 32.0 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 1 m² | 135 | - | 1 m² | - | - |
| Wall Transmission | 102 m² | 520 | - | 102 m² | 649 | - |
| Roof Transmission | 66 m² | 516 | - | 66 m² | 499 | - |
| Window Transmission | 1 m² | 45 | - | 1 m² | 54 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 185 | - | 2 m² | 223 | - |
| Floor Transmission | 66 m² | 15 | - | 66 m² | 220 | - |
| Partitions | 19 m² | 126 | - | 19 m² | 139 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 21 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 4100 W | 4100 | - | 0 | 0 | - |
| People | 5 | 359 | 300 | 0 | 0 | 0 |
| Infiltration | - | 1845 | 3917 | - | 1852 | 0 |
| Miscellaneous | - | 1000 | 700 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 887 | 492 | 10% | 364 | 0 |
| >> Total Zone Loads | - | 9752 | 5409 | - | 3999 | 0 |
| Zone Conditioning | - | 9632 | 5409 | - | 4200 | 0 |
| Plenum Wall Load | 0% | 0 | - | 0 | 0 | - |
| Plenum Roof Load | 0% | 0 | - | 0 | 0 | - |
| Plenum Lighting Load | 0% | 0 | - | 0 | 0 | - |
| Exhaust Fan Load | 0 L/s | 0 | - | 0 L/s | 0 | - |
| Ventilation Load | 0 L/s | 0 | 0 | 0 L/s | 0 | 0 |
| Ventilation Fan Load | 0 L/s | 0 | - | 0 L/s | 0 | - |
| Space Fan Coil Fans | - | 0 | - | - | 0 | - |
| Duct Heat Gain / Loss | 0% | 0 | - | 0% | 0 | - |
| >> Total System Loads | - | 9632 | 5409 | - | 4200 | 0 |
| Terminal Unit Cooling | - | 9632 | 5441 | - | 0 | 0 |
| Terminal Unit Heating | - | 0 | - | - | 4200 | - |
| >> Total Conditioning | - | 9632 | 5441 | - | 4200 | 0 |
| Key: | Positive values are clg loads |  |  | Positive values are htg loads |  |  |
|  | Negative values are htg loads |  |  | Negative values are clg loads |  |  |

# CCTV CONTROL ROOM - BINAK DU

|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Jul 1500 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 41.0 °C / 32.0 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 1 m² | 85 | - | 1 m² | - | - |
| Wall Transmission | 102 m² | 545 | - | 102 m² | 649 | - |
| Roof Transmission | 66 m² | 522 | - | 66 m² | 499 | - |
| Window Transmission | 1 m² | 47 | - | 1 m² | 54 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 193 | - | 2 m² | 223 | - |
| Floor Transmission | 66 m² | 17 | - | 66 m² | 220 | - |
| Partitions | 19 m² | 131 | - | 19 m² | 139 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 21 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 4100 W | 4100 | - | 0 | 0 | - |
| People | 5 | 359 | 300 | 0 | 0 | 0 |
| Infiltration | - | 1909 | 3831 | - | 1852 | 0 |
| Miscellaneous | - | 1000 | 700 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 893 | 483 | 10% | 364 | 0 |
| >> Total Zone Loads | - | 9822 | 5315 | - | 3999 | 0 |
| Zone Conditioning | - | 9656 | 5315 | - | 4186 | 0 |
| Plenum Wall Load | 0% | 0 | - | 0 | 0 | - |
| Plenum Roof Load | 0% | 0 | - | 0 | 0 | - |
| Plenum Lighting Load | 0% | 0 | - | 0 | 0 | - |
| Exhaust Fan Load | 0 L/s | 0 | - | 0 L/s | 0 | - |
| Ventilation Load | 0 L/s | 0 | 0 | 0 L/s | 0 | 0 |
| Ventilation Fan Load | 0 L/s | 0 | - | 0 L/s | 0 | - |
| Space Fan Coil Fans | - | 0 | - | - | 0 | - |
| Duct Heat Gain / Loss | 0% | 0 | - | 0% | 0 | - |
| >> Total System Loads | - | 9656 | 5315 | - | 4186 | 0 |
| Terminal Unit Cooling | - | 9656 | 5386 | - | 0 | 0 |
| Terminal Unit Heating | - | 0 | - | - | 4186 | - |
| >> Total Conditioning | - | 9656 | 5386 | - | 4186 | 0 |
| Key: | Positive values are clg loads |  |  | Positive values are htg loads |  |  |
|  | Negative values are htg loads |  |  | Negative values are clg loads |  |  |

D01

# CCTV CONTROL ROOM - BINAK pu

|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Aug 1400 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 40.5 °C / 31.9 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 4 m² | 436 | - | 4 m² | - | - |
| Wall Transmission | 22 m² | 99 | - | 22 m² | 107 | - |
| Roof Transmission | 7 m² | 48 | - | 7 m² | 46 | - |
| Window Transmission | 4 m² | 168 | - | 4 m² | 199 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 4 m² | 267 | - | 4 m² | 255 | - |
| Floor Transmission | 7 m² | 4 | - | 7 m² | 27 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 3 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 1100 W | 1100 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 145 | 334 | - | 141 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 241 | 45 | 10% | 78 | 0 |
| >> Total Zone Loads | - | 2655 | 500 | - | 853 | 0 |
| Zone Conditioning | - | 2616 | 500 | - | 1030 | 0 |
| Plenum Wall Load | 0% | 0 | - | 0 | 0 | - |
| Plenum Roof Load | 0% | 0 | - | 0 | 0 | - |
| Plenum Lighting Load | 0% | 0 | - | 0 | 0 | - |
| Exhaust Fan Load | 0 L/s | 0 | - | 0 L/s | 0 | - |
| Ventilation Load | 0 L/s | 0 | 0 | 0 L/s | 0 | 0 |
| Ventilation Fan Load | 0 L/s | 0 | - | 0 L/s | 0 | - |
| Space Fan Coil Fans | - | 0 | - | - | 0 | - |
| Duct Heat Gain / Loss | 0% | 0 | - | 0% | 0 | - |
| >> Total System Loads | - | 2616 | 500 | - | 1030 | 0 |
| Terminal Unit Cooling | - | 2616 | 504 | - | 0 | 0 |
| Terminal Unit Heating | - | 0 | - | - | 1030 | - |
| >> Total Conditioning | - | 2616 | 504 | - | 1030 | 0 |
| Key: | Positive values are clg loads |  |  | Positive values are htg loads |  |  |
|  | Negative values are htg loads |  |  | Negative values are clg loads |  |  |

D01

D01

ZONE DESIGN LOAD SUMMARY:

# CCTV CONTROL ROOM - BINAK GCS

| Zone 1 | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Jul 1500 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 41.0 °C / 32.0 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 1 m² | 99 | - | 1 m² | - | - |
| Wall Transmission | 81 m² | 457 | - | 81 m² | 605 | - |
| Roof Transmission | 56 m² | 462 | - | 56 m² | 477 | - |
| Window Transmission | 1 m² | 47 | - | 1 m² | 54 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 195 | - | 2 m² | 223 | - |
| Floor Transmission | 56 m² | 0 | - | 56 m² | 220 | - |
| Partitions | 19 m² | 133 | - | 19 m² | 139 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 19 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 1600 W | 1600 | - | 0 | 0 | - |
| People | 5 | 359 | 300 | 0 | 0 | 0 |
| Infiltration | - | 1967 | 3770 | - | 1852 | 0 |
| Miscellaneous | - | 1000 | 700 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 634 | 477 | 10% | 357 | 0 |
| >> Total Zone Loads | - | 6972 | 5247 | - | 3926 | 0 |

| Zone 2 | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Jul 0800 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 27.0 °C / 26.7 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 30.0 °C |  |  | OCCUPIED T-STAT 10.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 21 m² | 121 | - | 21 m² | 45 | - |
| Roof Transmission | 10 m² | 59 | - | 10 m² | 21 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 10 m² | -4 | - | 10 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 128 W | 2 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 2500 W | 2500 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 268 | 0 | 10% | 7 | 0 |
| >> Total Zone Loads | - | 2946 | 0 | - | 73 | 0 |

D01

CCTV CONTROL ROOM - BINAK DU

| Zone 1 | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Jul 1500 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 41.0 °C / 32.0 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 1 m² | 89 | - | 1 m² | - | - |
| Wall Transmission | 81 m² | 463 | - | 81 m² | 605 | - |
| Roof Transmission | 56 m² | 462 | - | 56 m² | 477 | - |
| Window Transmission | 1 m² | 47 | - | 1 m² | 54 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 195 | - | 2 m² | 223 | - |
| Floor Transmission | 56 m² | 0 | - | 56 m² | 220 | - |
| Partitions | 19 m² | 133 | - | 19 m² | 139 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 19 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 1600 W | 1600 | - | 0 | 0 | - |
| People | 5 | 359 | 300 | 0 | 0 | 0 |
| Infiltration | - | 1967 | 3834 | - | 1852 | 0 |
| Miscellaneous | - | 1000 | 700 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 633 | 483 | 10% | 357 | 0 |
| >> Total Zone Loads | - | 6967 | 5318 | - | 3926 | 0 |

| Zone 2 | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Jul 0800 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 27.0 °C / 26.7 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 30.0 °C |  |  | OCCUPIED T-STAT 10.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 21 m² | 122 | - | 21 m² | 45 | - |
| Roof Transmission | 10 m² | 61 | - | 10 m² | 21 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 10 m² | -9 | - | 10 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 128 W | 2 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 2500 W | 2500 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 268 | 0 | 10% | 7 | 0 |
| >> Total Zone Loads | - | 2944 | 0 | - | 73 | 0 |

D01

CCTV CONTROL ROOM - BINAK pu

| Zone 1 | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Sep 1400 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 39.4 °C / 31.4 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 4 m² | 530 | - | 4 m² | - | - |
| Wall Transmission | 11 m² | 77 | - | 11 m² | 87 | - |
| Roof Transmission | 5 m² | 30 | - | 5 m² | 40 | - |
| Window Transmission | 4 m² | 154 | - | 4 m² | 199 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 158 | - | 2 m² | 204 | - |
| Floor Transmission | 5 m² | 0 | - | 5 m² | 27 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 2 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 100 W | 100 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 135 | 323 | - | 141 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 133 | 44 | 10% | 70 | 0 |
| >> Total Zone Loads | - | 1462 | 488 | - | 768 | 0 |

| Zone 2 | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | COOLING DATA AT Jul 1500 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 41.0 °C / 32.0 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 30.0 °C |  |  | OCCUPIED T-STAT 10.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| ZONE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 11 m² | 28 | - | 11 m² | 21 | - |
| Roof Transmission | 3 m² | 14 | - | 3 m² | 6 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 100 | - | 2 m² | 51 | - |
| Floor Transmission | 3 m² | 4 | - | 3 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 1 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 1000 W | 1000 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 115 | 0 | 10% | 8 | 0 |
| >> Total Zone Loads | - | 1262 | 0 | - | 85 | 0 |

D01

SPACE DESIGN LOAD SUMMARY:

# CCTV CONTROL ROOM - BINAK GCS

| TABLE 1.1.A. COMPONENT LOADS FOR SPACE '' 00-Control Room '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Jul 0800 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 27.0 °C / 26.7 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 68 m² | 325 | - | 68 m² | 492 | - |
| Roof Transmission | 47 m² | 425 | - | 47 m² | 400 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 47 m² | 0 | - | 47 m² | 184 | - |
| Partitions | 7 m² | 13 | - | 7 m² | 48 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 693 W | 387 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 500 W | 500 | - | 0 | 0 | - |
| People | 5 | 359 | 300 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 201 | 30 | 10% | 112 | 0 |
| >> Total Zone Loads | - | 2209 | 330 | - | 1237 | 0 |

| TABLE 1.1.B. ENVELOPE LOADS FOR SPACE '' 00-Control Room '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| ENE EXPOSURE |  |  |  |  |  |  |
| WALL | 19 | 0.452 | - | 98 | - | 137 |
| SSE EXPOSURE |  |  |  |  |  |  |
| WALL | 25 | 0.452 | - | 111 | - | 178 |
| NNW EXPOSURE |  |  |  |  |  |  |
| WALL | 25 | 0.452 | - | 116 | - | 178 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 47 | 0.536 | - | 425 | - | 400 |

| TABLE 1.2.A. COMPONENT LOADS FOR SPACE '' 02-Entrance '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Jul 1500 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 41.0 °C / 32.0 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 1 m² | 10 | - | 1 m² | 11 | - |
| Roof Transmission | 5 m² | 40 | - | 5 m² | 41 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 195 | - | 2 m² | 223 | - |
| Floor Transmission | 5 m² | 0 | - | 5 m² | 14 | - |
| Partitions | 6 m² | 41 | - | 6 m² | 43 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 1 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 500 W | 500 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 1521 | 2914 | - | 1431 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 231 | 291 | 10% | 176 | 0 |
| >> Total Zone Loads | - | 2538 | 3205 | - | 1940 | 0 |

| TABLE 1.2.B. ENVELOPE LOADS FOR SPACE '' 02-Entrance '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| WSW EXPOSURE |  |  |  |  |  |  |
| WALL | 1 | 0.495 | - | 10 | - | 11 |
| DOOR | 2 | 5.800 | - | 195 | - | 223 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 5 | 0.536 | - | 40 | - | 41 |

D01

| TABLE 1.3.A. COMPONENT LOADS FOR SPACE '' 03-Pantry '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Aug 1600 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 40.5 °C / 31.9 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 1 m² | 121 | - | 1 m² | - | - |
| Wall Transmission | 12 m² | 85 | - | 12 m² | 101 | - |
| Roof Transmission | 4 m² | 35 | - | 4 m² | 36 | - |
| Window Transmission | 1 m² | 47 | - | 1 m² | 54 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 4 m² | 0 | - | 4 m² | 22 | - |
| Partitions | 7 m² | 45 | - | 7 m² | 48 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 1 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 600 W | 600 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 433 | 867 | - | 420 | 0 |
| Miscellaneous | - | 1000 | 700 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 237 | 157 | 10% | 68 | 0 |
| >> Total Zone Loads | - | 2605 | 1723 | - | 749 | 0 |

| TABLE 1.3.B. ENVELOPE LOADS FOR SPACE '' 03-Pantry '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| NNW EXPOSURE |  |  |  |  |  |  |
| WALL | 5 | 0.541 | - | 33 | - | 44 |
| WINDOW 1 | 1 | 2.819 | 0.700 | 47 | 121 | 54 |
| WSW EXPOSURE |  |  |  |  |  |  |
| WALL | 7 | 0.541 | - | 52 | - | 57 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 4 | 0.536 | - | 35 | - | 36 |

D01

| TABLE 2.1.A. COMPONENT LOADS FOR SPACE '' 01-Rack Room '' IN ZONE '' Zone 2 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Jul 0800 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 27.0 °C / 26.7 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 30.0 °C |  |  | OCCUPIED T-STAT 10.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 21 m² | 121 | - | 21 m² | 45 | - |
| Roof Transmission | 10 m² | 59 | - | 10 m² | 21 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 10 m² | -4 | - | 10 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 2 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 2500 W | 2500 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 268 | 0 | 10% | 7 | 0 |
| >> Total Zone Loads | - | 2946 | 0 | - | 73 | 0 |

| TABLE 2.1.B. ENVELOPE LOADS FOR SPACE '' 01-Rack Room '' IN ZONE '' Zone 2 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| SSE EXPOSURE |  |  |  |  |  |  |
| WALL | 13 | 0.547 | - | 68 | - | 28 |
| WSW EXPOSURE |  |  |  |  |  |  |
| WALL | 8 | 0.547 | - | 53 | - | 17 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 10 | 0.536 | - | 59 | - | 21 |

D01

# CCTV CONTROL ROOM - BINAK DU

| TABLE 1.1.A. COMPONENT LOADS FOR SPACE '' 00-Control Room '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Jul 0800 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 27.0 °C / 26.7 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 68 m² | 323 | - | 68 m² | 492 | - |
| Roof Transmission | 47 m² | 425 | - | 47 m² | 400 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 47 m² | 0 | - | 47 m² | 184 | - |
| Partitions | 7 m² | 13 | - | 7 m² | 48 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 693 W | 387 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 500 W | 500 | - | 0 | 0 | - |
| People | 5 | 359 | 300 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 201 | 30 | 10% | 112 | 0 |
| >> Total Zone Loads | - | 2207 | 330 | - | 1237 | 0 |

| TABLE 1.1.B. ENVELOPE LOADS FOR SPACE '' 00-Control Room '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| ESE EXPOSURE |  |  |  |  |  |  |
| WALL | 19 | 0.452 | - | 98 | - | 137 |
| NNE EXPOSURE |  |  |  |  |  |  |
| WALL | 25 | 0.452 | - | 110 | - | 178 |
| SSW EXPOSURE |  |  |  |  |  |  |
| WALL | 25 | 0.452 | - | 115 | - | 178 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 47 | 0.536 | - | 425 | - | 400 |

D01

| TABLE 1.2.A. COMPONENT LOADS FOR SPACE '' 02-Entrance '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Jul 1500 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 41.0 °C / 32.0 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 1 m² | 9 | - | 1 m² | 11 | - |
| Roof Transmission | 5 m² | 40 | - | 5 m² | 41 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 195 | - | 2 m² | 223 | - |
| Floor Transmission | 5 m² | 0 | - | 5 m² | 14 | - |
| Partitions | 6 m² | 41 | - | 6 m² | 43 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 1 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 500 W | 500 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 1521 | 2964 | - | 1431 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 231 | 296 | 10% | 176 | 0 |
| >> Total Zone Loads | - | 2538 | 3260 | - | 1940 | 0 |

| TABLE 1.2.B. ENVELOPE LOADS FOR SPACE '' 02-Entrance '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| WNW EXPOSURE |  |  |  |  |  |  |
| WALL | 1 | 0.495 | - | 9 | - | 11 |
| DOOR | 2 | 5.800 | - | 195 | - | 223 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 5 | 0.536 | - | 40 | - | 41 |

D01

| TABLE 1.3.A. COMPONENT LOADS FOR SPACE '' 03-Pantry '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Aug 1600 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 40.5 °C / 31.9 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 1 m² | 89 | - | 1 m² | - | - |
| Wall Transmission | 12 m² | 78 | - | 12 m² | 101 | - |
| Roof Transmission | 4 m² | 35 | - | 4 m² | 36 | - |
| Window Transmission | 1 m² | 47 | - | 1 m² | 54 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 4 m² | 0 | - | 4 m² | 22 | - |
| Partitions | 7 m² | 46 | - | 7 m² | 48 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 1 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 600 W | 600 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 447 | 870 | - | 420 | 0 |
| Miscellaneous | - | 1000 | 700 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 234 | 157 | 10% | 68 | 0 |
| >> Total Zone Loads | - | 2576 | 1727 | - | 749 | 0 |

| TABLE 1.3.B. ENVELOPE LOADS FOR SPACE '' 03-Pantry '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| NNE EXPOSURE |  |  |  |  |  |  |
| WALL | 5 | 0.541 | - | 35 | - | 44 |
| WINDOW 1 | 1 | 2.819 | 0.700 | 47 | 89 | 54 |
| WNW EXPOSURE |  |  |  |  |  |  |
| WALL | 7 | 0.541 | - | 42 | - | 57 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 4 | 0.536 | - | 35 | - | 36 |

D01

| TABLE 2.1.A. COMPONENT LOADS FOR SPACE '' 01-Rack Room '' IN ZONE '' Zone 2 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Jul 0800 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 27.0 °C / 26.7 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 30.0 °C |  |  | OCCUPIED T-STAT 10.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 21 m² | 122 | - | 21 m² | 45 | - |
| Roof Transmission | 10 m² | 61 | - | 10 m² | 21 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 10 m² | -9 | - | 10 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 2 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 2500 W | 2500 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 268 | 0 | 10% | 7 | 0 |
| >> Total Zone Loads | - | 2944 | 0 | - | 73 | 0 |

| TABLE 2.1.B. ENVELOPE LOADS FOR SPACE '' 01-Rack Room '' IN ZONE '' Zone 2 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| SSW EXPOSURE |  |  |  |  |  |  |
| WALL | 13 | 0.547 | - | 74 | - | 28 |
| WNW EXPOSURE |  |  |  |  |  |  |
| WALL | 8 | 0.547 | - | 49 | - | 17 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 10 | 0.536 | - | 61 | - | 21 |

D01

# CCTV CONTROL ROOM - BINAK pu

| TABLE 1.1.A. COMPONENT LOADS FOR SPACE '' 00-Guard House '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Sep 1400 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 39.4 °C / 31.4 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 24.0 °C |  |  | OCCUPIED T-STAT 22.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 4 m² | 530 | - | 4 m² | - | - |
| Wall Transmission | 11 m² | 77 | - | 11 m² | 87 | - |
| Roof Transmission | 5 m² | 30 | - | 5 m² | 40 | - |
| Window Transmission | 4 m² | 154 | - | 4 m² | 199 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 158 | - | 2 m² | 204 | - |
| Floor Transmission | 5 m² | 0 | - | 5 m² | 27 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 2 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 100 W | 100 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 135 | 323 | - | 141 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 133 | 44 | 10% | 70 | 0 |
| >> Total Zone Loads | - | 1462 | 488 | - | 768 | 0 |

| TABLE 1.1.B. ENVELOPE LOADS FOR SPACE '' 00-Guard House '' IN ZONE '' Zone 1 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| N EXPOSURE |  |  |  |  |  |  |
| WALL | 3 | 0.495 | - | 10 | - | 20 |
| WINDOW 1 | 1 | 2.845 | 0.700 | 30 | 32 | 38 |
| DOOR | 2 | 5.800 | - | 158 | - | 204 |
| S EXPOSURE |  |  |  |  |  |  |
| WALL | 4 | 0.495 | - | 31 | - | 30 |
| WINDOW 1 | 2 | 2.799 | 0.700 | 62 | 296 | 81 |
| E EXPOSURE |  |  |  |  |  |  |
| WALL | 5 | 0.495 | - | 37 | - | 36 |
| WINDOW 1 | 2 | 2.799 | 0.700 | 62 | 202 | 81 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 5 | 0.536 | - | 30 | - | 40 |

D01

| TABLE 2.1.A. COMPONENT LOADS FOR SPACE '' 01-Rack Room '' IN ZONE '' Zone 2 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | DESIGN COOLING |  |  | DESIGN HEATING |  |  |
|  | COOLING DATA AT Jul 1500 |  |  | HEATING DATA AT DES HTG |  |  |
|  | COOLING OA DB / WB 41.0 °C / 32.0 °C |  |  | HEATING OA DB / WB 6.0 °C / 6.0 °C |  |  |
|  | OCCUPIED T-STAT 30.0 °C |  |  | OCCUPIED T-STAT 10.0 °C |  |  |
|  |  | Sensible | Latent |  | Sensible | Latent |
| SPACE LOADS | Details | (W) | (W) | Details | (W) | (W) |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 11 m² | 28 | - | 11 m² | 21 | - |
| Roof Transmission | 3 m² | 14 | - | 3 m² | 6 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 2 m² | 100 | - | 2 m² | 51 | - |
| Floor Transmission | 3 m² | 4 | - | 3 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 0 W | 1 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 1000 W | 1000 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 115 | 0 | 10% | 8 | 0 |
| >> Total Zone Loads | - | 1262 | 0 | - | 85 | 0 |

| TABLE 2.1.B. ENVELOPE LOADS FOR SPACE '' 01-Rack Room '' IN ZONE '' Zone 2 '' |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | COOLING | COOLING | HEATING |
|  | Area | U-Value | Shade | TRANS | SOLAR | TRANS |
|  | (m²) | (W/(m²-°K)) | Coeff. | (W) | (W) | (W) |
| N EXPOSURE |  |  |  |  |  |  |
| WALL | 3 | 0.484 | - | 7 | - | 6 |
| W EXPOSURE |  |  |  |  |  |  |
| WALL | 4 | 0.484 | - | 14 | - | 8 |
| DOOR | 2 | 5.800 | - | 100 | - | 51 |
| S EXPOSURE |  |  |  |  |  |  |
| WALL | 3 | 0.484 | - | 8 | - | 6 |
| H EXPOSURE |  |  |  |  |  |  |
| ROOF | 3 | 0.536 | - | 14 | - | 6 |

D01

D01

Equipment Selection

## Air Conditioning Unit

# CCTV CONTROL ROOM - BINAK GCS

| Item | Service Area |  |  |
| --- | --- | --- | --- |
|  | Control Room & Entrance | Rack Room | Pantry |
| Calculated Sensible Cooling Load(w) | 2209+2538 | 2946 | 2605 |
| Calculated Latent Cooling Load(w) | 330+3205 | 0 | 1723 |
| Calculated Total Cooling Load(w) | 2539+5743 | 2946 | 4328 |
| Calculated Total Cooling Load (btu/hr) | 8671+19613 | 10061 | 14781 |
| Calculated Sensible Heating Load(w) | 1237+1940 | 73 | 749 |
| Calculated Sensible Heating Load (btu/hr) | 4225+6625 | 249 | 2558 |
| Split Unit ID Indoor Unit ID | 1202-SUI-…-01 | 1202-SUI-…-02 | 1202-SUI-…-03 |
| Split Unit Outdoor Unit ID | 1202-SUO-…-01 | 1202-SUO-…-02 | 1202-SUO-…-03 |
| Equipment QTY. | 1 | 1 | 1 |
| Equipment Type | Wall Mounted Split Unit | Wall Mounted Split Unit | Wall Mounted Split Unit |
| Calculated Cooling Load+ 10% Over Cap. (btu/hr) Each | 31112 | 11067 | 16259 |
| Calculated Heating Load+ 10% Over Cap. (btu/hr) Each | 11935 | 274 | 2814 |
| Selected Eq. Nominal Cooling Cap. (btu/hr) Each | By Vendor | By Vendor | By Vendor |
| Selected Eq. Actual Cooling Cap. (btu/hr) Each | By Vendor | By Vendor | By Vendor |
| Selected Eq. Actual Heating Cap. (btu/hr) Each | By Vendor | By Vendor | By Vendor |
| Power Supply (V/PH/Hz) | 230/1/50 | 230/1/50 | 230/1/50 |
| Max. Power Consumption (w) Each Eq. (Cooling/Heating) | By Vendor | By Vendor | By Vendor |
| REMARKE | Outdoor and Indoor Unit (With Thermostat & All Standard Accessory)-T3 | Outdoor and Indoor Unit (With Thermostat & All Standard Accessory)-T3 | Outdoor and Indoor Unit (With Thermostat & All Standard Accessory)-T3 |

Note: Cooling capacity shall be rated for site outdoor temperature and indoor set point. (In fact vendor shall de-rate split cooling load for standard rating at 35°C /27°C in comparison with 50°C /24°C).

D01

CCTV CONTROL ROOM - BINAK DU

| Item | Service Area |  |  |
| --- | --- | --- | --- |
|  | Control Room & Entrance | Rack Room | Pantry |
| Calculated Sensible Cooling Load(w) | 2207+2538 | 2944 | 2576 |
| Calculated Latent Cooling Load(w) | 330+3260 | 0 | 1727 |
| Calculated Total Cooling Load(w) | 2537+5798 | 2944 | 4303 |
| Calculated Total Cooling Load (btu/hr) | 8664+19801 | 10054 | 14696 |
| Calculated Sensible Heating Load(w) | 1237+1940 | 73 | 749 |
| Calculated Sensible Heating Load (btu/hr) | 4361+6625 | 249 | 2558 |
| Split Unit ID Indoor Unit ID | 1202-SUI-…-01 | 1202-SUI-…-02 | 1202-SUI-…-03 |
| Split Unit Outdoor Unit ID | 1202-SUO-…-01 | 1202-SUO-…-02 | 1202-SUO-…-03 |
| Equipment QTY. | 1 | 1 | 1 |
| Equipment Type | Wall Mounted Split Unit | Wall Mounted Split Unit | Wall Mounted Split Unit |
| Calculated Cooling Load+ 10% Over Cap. (btu/hr) Each | 31312 | 11059 | 16166 |
| Calculated Heating Load+ 10% Over Cap. (btu/hr) Each | 12085 | 274 | 2814 |
| Selected Eq. Nominal Cooling Cap. (btu/hr) Each | By Vendor | By Vendor | By Vendor |
| Selected Eq. Actual Cooling Cap. (btu/hr) Each | By Vendor | By Vendor | By Vendor |
| Selected Eq. Actual Heating Cap. (btu/hr) Each | By Vendor | By Vendor | By Vendor |
| Power Supply (V/PH/Hz) | 230/1/50 | 230/1/50 | 230/1/50 |
| Max. Power Consumption (w) Each Eq. (Cooling/Heating) | By Vendor | By Vendor | By Vendor |
| REMARKE | Outdoor and Indoor Unit (With Thermostat & All Standard Accessory)-T3 | Outdoor and Indoor Unit (With Thermostat & All Standard Accessory)-T3 | Outdoor and Indoor Unit (With Thermostat & All Standard Accessory)-T3 |

Note: Cooling capacity shall be rated for site outdoor temperature and indoor set point. (In fact vendor shall de-rate split cooling load for standard rating at 35°C /27°C in comparison with 50°C /24°C).

D01

CCTV CONTROL ROOM - BINAK pu

| Item | Service Area |  |
| --- | --- | --- |
|  | Guard House | Rack Room |
| Calculated Sensible Cooling Load(w) | 1462 | 1262 |
| Calculated Latent Cooling Load(w) | 488 | 0 |
| Calculated Total Cooling Load(w) | 1950 | 1262 |
| Calculated Total Cooling Load (btu/hr) | 6660 | 4310 |
| Calculated Sensible Heating Load(w) | 768 | 85 |
| Calculated Sensible Heating Load (btu/hr) | 2623 | 290 |
| Split Unit ID Indoor Unit ID | 1202-SUI-…-01 | 1202-SUI-…-02 |
| Split Unit Outdoor Unit ID | 1202-SUO-…-01 | 1202-SUO-…-02 |
| Equipment QTY. | 1 | 1 |
| Equipment Type | Wall Mounted Split Unit | Wall Mounted Split Unit |
| Calculated Cooling Load+ 10% Over Cap. (btu/hr) Each | 7326 | 4741 |
| Calculated Heating Load+ 10% Over Cap. (btu/hr) Each | 2885 | 319 |
| Selected Eq. Nominal Cooling Cap. (btu/hr) Each | By Vendor | By Vendor |
| Selected Eq. Actual Cooling Cap. (btu/hr) Each | By Vendor | By Vendor |
| Selected Eq. Actual Heating Cap. (btu/hr) Each | By Vendor | By Vendor |
| Power Supply (V/PH/Hz) | 230/1/50 | 230/1/50 |
| Max. Power Consumption (w) Each Eq. (Cooling/Heating) | By Vendor | By Vendor |
| REMARKE | Outdoor and Indoor Unit (With Thermostat & All Standard Accessory)-T3 | Outdoor and Indoor Unit (With Thermostat & All Standard Accessory)-T3 |

Note: Cooling capacity shall be rated for site outdoor temperature and indoor set point. (In fact vendor shall de-rate split cooling load for standard rating at 35°C /27°C in comparison with 50°C /24°C).

## Exhaust fan selection

# CCTV CONTROL ROOM - BINAK GCS & DU

WC

Air Flow = 4 (area, m²) × 3.15 (height, m) × 15 ACH ÷ 60 min

=3.15 m³/min

=52.5 L/S ~ 75 L/S

=160 cfm

Pantry

Air Flow = 4.16 (area, m²) × 3.15 (height, m) × 6 ACH ÷ 60 min

=1.31 m³/min

=21.83 L/S ~ 100 L/S

=212 cfm

| Item |  | Service Area |  |
| --- | --- | --- | --- |
|  |  | WC | Pantry |
| Equipment QTY. |  | 1 | 1 |
| Air Flow(L/S) |  | 75 | 100 |
| Air Flow(CFM) |  | 160 | 212 |
| Component Pressure Drop | Diffuser (In.WG.) | 0.00 | 0.00 |
|  | Sand Trap Louver (In.WG.) | 0.00 | 0.00 |
|  | Door Louver (In.WG.) | 0.00 | 0.00 |
|  | Ducting (In.WG.) | 0.0025 | 0.00 |
| Total External Pressure Drop * | (In.WG.) | 0.03936 | 0.00 |
|  | (Pa) | 0.6221 | 0.00 |
| Exhaust Fan ID |  | 1202-EF-…-01 | 1202-EF-…-02 |
| Exhaust Fan type |  | Ceiling Mounted | Wall Mounted/Axial |
| Power Supply (V/PH/Hz) |  | 230/1/50 | 230/1/50 |
| Power Consumption (w) Each Eq. |  | By Vendor | By Vendor |
| REMARKE |  | (∅=200 mm) | Equipped With Exhaust Air Louver |

*Total Pressure Drop Include Louver and etc. Should Be Specified By Vendor.