## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0007-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2669 |  |  | Transmital Date: 23/APR/2024
Document Title: HVAC Calculation Note For CCTV Control Room (DU,PU,GCS) |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-2669 |  |  | Transmital Date: 23/APR/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-CN-0007-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جدول صفحه 33 با محاسبات مربوط به بخش GCS مغایرت دارد. طبق محاسبات ظرفیت کویل سرمایش RAC ROOM در بخش GCS برابر 3.7 KW است که جدول مذکور با آن همخوانی ندارد. |  | 03/2294/87093 | 1403/03/06 | بار کلی کویل (Total Coil Load) در بخش سرمایش، مجموع حداکثر بار سیستم سرمایش را نشان می دهد. این بار شامل بارهای محسوس و نهان و فارغ از زمان بروز بار است. اما اعداد مندرج در جداول انتخاب دستگاه مجموع بار سرمایی و گرمایی در زمان پیک بار را نشان می دهد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: 1403/03/06 |  |  |  |  | Date: