| طرح نگهداشت وافزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CALAULATION NOTE FOR GAS COMPRESSORS FOUNDATION نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D00 |  | DEC. 2024 | IFC | R.Berlouie | M.Fakharian | S.Faramarzpour |  |
| Rev. |  | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class:2 |  |  | COMPANY Doc. Number: F0Z-709121 |  |  |  |  |
| Status: |  | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  |  |  |  | 66 |  |  |  |  |  |
| 2 | X |  |  |  |  |  | 67 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 68 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 70 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 71 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 72 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 73 |  |  |  |  |  |
| 9 | X |  |  |  |  |  | 74 |  |  |  |  |  |
| 10 | X |  |  |  |  |  | 75 |  |  |  |  |  |
| 11 | X |  |  |  |  |  | 76 |  |  |  |  |  |
| 12 | X |  |  |  |  |  | 77 |  |  |  |  |  |
| 13 | X |  |  |  |  |  | 78 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 79 |  |  |  |  |  |
| 15 | X |  |  |  |  |  | 80 |  |  |  |  |  |
| 16 | X |  |  |  |  |  | 81 |  |  |  |  |  |
| 17 | X |  |  |  |  |  | 82 |  |  |  |  |  |
| 18 | X |  |  |  |  |  | 83 |  |  |  |  |  |
| 19 | X |  |  |  |  |  | 84 |  |  |  |  |  |
| 20 | X |  |  |  |  |  | 85 |  |  |  |  |  |
| 21 | X |  |  |  |  |  | 86 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 100 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 101 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 102 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 103 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 104 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 105 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 106 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 107 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 108 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 109 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 110 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 111 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 112 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 113 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 114 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 115 |  |  |  |  |  |
| 51 |  |  |  |  |  |  | 116 |  |  |  |  |  |
| 52 |  |  |  |  |  |  | 117 |  |  |  |  |  |
| 53 |  |  |  |  |  |  | 118 |  |  |  |  |  |
| 54 |  |  |  |  |  |  | 119 |  |  |  |  |  |
| 55 |  |  |  |  |  |  | 120 |  |  |  |  |  |
| 56 |  |  |  |  |  |  | 121 |  |  |  |  |  |
| 57 |  |  |  |  |  |  | 122 |  |  |  |  |  |
| 58 |  |  |  |  |  |  | 123 |  |  |  |  |  |
| 59 |  |  |  |  |  |  | 124 |  |  |  |  |  |
| 60 |  |  |  |  |  |  | 125 |  |  |  |  |  |
| 61 |  |  |  |  |  |  | 126 |  |  |  |  |  |
| 62 |  |  |  |  |  |  | 127 |  |  |  |  |  |
| 63 |  |  |  |  |  |  | 128 |  |  |  |  |  |
| 64 |  |  |  |  |  |  | 129 |  |  |  |  |  |
| 65 |  |  |  |  |  |  | 130 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	4

2.1	Local Codes and Standards	4

2.2	International Codes and Standards	4

2.3	The Project Documents	4

3.0	Material properties	5

4.0	LOADS	7

4.1	Deal Load	7

4.2	Deal Load	7

4.3	Operatio Load	8

4.4	Dynamic Load	8

4.5	Earthquake Load	9

4.6	25% Operating Load	9

5.0	Analysis	10

5.1	3d Model	10

5.2	Analysis Cases	10

5.3	Load Combinations	12

6.0	Checking and Results	19

6.1	Soil Pressure	19

6.2	Minimum Weight of Foundation	19

6.3	Displacement Control	20

7.0	Design	22

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

- Scope

This report covers the foundation calculation report of the “Gas Compressors Foundation”. The foundation modelled by “SAP2000” software.

NORMATIVE REFERENCE

  - Local Codes and Standards

- INBC Part 6 “Iranian National Building Code

- INBC Part 7 “Iranian National Building Code

- INBC Part 9 “Iranian National Building Code

- Iranian Seismic Design Code for Petroleum Facilities(3rd edition)

  - International Codes and Standards

- C.Arya, W.O’Neil, “Design of Structures and Foundations for Vibrating Machines

- ACI 318. “Building Code Requirements for Reinforced Concrete”, American Concrete Institute.

- ACI 351.3R American Concrete Institute– Foundation Dynamic Equipment

- Structural Design Criteria

  - The Project Documents

- BK-GNRAL-PEDCO-000-ST-SP-0001    Specification for Concrete Work

- BK-GNRAL-PEDCO-000-ST-SP-0004    Specification for Grouting

- BK-GCS-PEDCO-120-ST-DW-0059    Foundation Drawing For Gas Compressor Shelter

- BK-GCS-PEDCO-120-ST-DW-0060   Structural Drawing For Gas Compressor Shelter

- BK-GNRAL-PEDCO-000-ST-DC-0001 Structural Design Criteria

- Material properties

Material properties are delivered in the following table.

- table 1 -Material Properties

| Foundation Concrete | F'c = 30 Mpa(28- day cylindrical sample) |
| --- | --- |
| Long. reinforcement bar | Fy = 400 Mpa(AIII) |
| Trans. reinforcement bar | Fy = 400 Mpa(AIII) |
| Soil Shear modulus | G=2.9e7 (kg/m^2) According to geotechnical investigation report |

- LOADS

  - Deal Load

Dead loads are included the following loads:

Foundation weight + pedestals weight + soil weight and finally compressors and their attachments.

  - Operation Load

According to vendor data sheet the following loads are applied to the models

  - Dynamic Load

  - Earthquake Load

Seismic loads applied to the model manually and its calculations are mentioned below:

V=0.7*Ca*I*W

V=0.7*0.3*1.25*W=0.263W

  - 25% Operating Load

According to regulations, 25% of the compressor's operating loads must be applied as dynamic loads in both directions.

- Analysis

  - 3d Model

SAP 2000 was applied for model this foundation and for more accuracy, solids elements have been used for checking of pressure and displacement of foundation.

  - Analysis Cases

  - Load Combinations

- Calculation of Stiffness:

Compressor:

Ix=112ma^2+b^2)=112*6389.31.357^2+1.729^2   = 2572.17

Iy=112ma^2+L^2)=112*6389.31.357^2+4.935^2   = 13977.67

Iz=112mb^2+L^2)=112*6389.31.729^2+4.935^2   = 14558.91

Motor :

Ix=112ma^2+b^2)=112*17854.994^2+2.440^2  = 4595.43

Iy=112ma^2+L^2)=112*17854.994^2+2.755^2   = 4838.85

Iz=112mb^2+L^2)=112*17852.440^2+2.755^2   = 2014.61

Modified Stiffness:

Number of Joints : n=400

- Translational

Kx=Kxn=791768759.4400=1979422   kg/m

Ky=Kyn=812280903.4400=2030703  kg/m

Kz=Kzn=975587126.1400=2438968  kg/m

- Rotational

A=11.2*9.9=111 m2

Ix=LB^312=11.2*9.9^312=906  m3

Iy=BL^312=9.9*11.2^312=1160  m3

Ks=KzA=975587126.1111=8789074  kg/m

Ksx=KxA=791768759.4111=7133052  kg/m

Ksy=KyA=812280903.4111=7317846  kg/m

Kⱷx=[Kⱷ-Ks*Ix]n= [23680093701.5-8789074*906]400=39292982  kg/m

Kⱷy=[Kⱷ-Ks*Iy]n= [28119341850.7-8789074*1160]400=44810040 kg/m

Kⱷz=[Kⱷ-Ksx*Ix-Ksy*Iy]n= [31110283213.8-7133052*906-7317846*1160]400=40397592 kg/m

- Checking and Results

  - Minimum Weight of Foundation

According to design criteria total foundation weight shall be at least 5 times the total machinery weight for Reciprocating machines.

Foundation Weight(Include foundation, pedestal & compressor)= 675.15  ton

Compressor Weight= 81.745  ton

675.15/81.745=8.05 > 5  ok√

  - Displacement Control

All dimensions are meters. This report has been given for compressor.

  - Foundation Design

Since foundation type is block, therefore the moments are negligible. In any directions minimum reinforcement is govern So T16 @ 200 is used.

Longitudinal & Transversal Footing: T16 @200 (Top & Bottom)

A=2x2×6 × 2.01 = 24.12 cm2 => == 0.0027

Based on I.N.B.C. Part: 9 section 2-1-7-10-9:

˃       ok √