## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0013_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2642 |  |  | Transmital Date: 16-Mar-2024
Document Title: Data Sheets For Orifice Plate/Restriction Orifice |  |  |  |  | NISOC Tr. No.: BK-PEDCO-NISOC-0212-IN-TR-2642 |  |  | Transmital Date: 16-Mar-2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DT-0013_D03 |  |  | CRS Status: CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لازم است اصطلاحات مورد نیاز در طراحی انجام گردد به گونه ای که الزامات استاندارد IPS را در خصوص BETA RATIO برآورده سازد. قابل ذکر است در بیشتر موارد میزان BETA RATIO از میزان استاندارد پایین تر است. |  | 03/2291/51200 | 1403/02/12 | پس از محاسبات orifice توسط سازنده، در صورت قرار نگرفتن beta ratio در رنج استاندارد از multi stage یا multi hole در طراحی استفاده می گردد که این بند به صورت NOTE در صفحه 4 مدرک اضافه گردید.
2 | چرا سوراخ VENT و DRAIN برای ادوات در نظر گرفته نشده است؟ |  | 03/2291/51200 | 1403/02/12 | آیتم 24 صفحه 5 مربوط به drain و vent تجهیزات orifice plate می باشد. لازم به ذکر است طبق مدرک SPECIFICATION FOR INSTRUMENTATION برای restriction orifice plate نیاز به vent/ drain نمی باشند.
3 | لازم است قطر مد نظر برای سوراخ اصلی و سوراخ های DRAIN و VENT اعلام گردد و در قالب NOTE اشاره گردد که سایز نهایی بر عهده سازنده می باشد. |  | 03/2291/51200 | 1403/02/12 | این مورد در note 2 صفحه 5 این مورد ذکر شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 30 Mar 2024 |  |  |  |  | Date: