## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0018 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR ROTAMETER نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  |  | JAN.2025 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.FARAMARZPOUR
D02 |  |  | SEP.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.FARAMARZPOUR
D01 |  |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: F9Z-708938
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0018 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X |  | X | [5 empty] | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 |  | X | X | [5 empty] | 72
9 |  |  | X | [5 empty] | 73
10 |  |  | X | [5 empty] | 74
11 |  |  | X | [5 empty] | 75
12 |  |  | X |  | X |  |  |  | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 12
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 | D03
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## Notes
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 12
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 | D03
GENERAL NOTES:
1- Environmental Condition For Field Instrumentation Of BINAK Complex Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: -5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
2- Surface roughness shall be in accordance with ASME 16.5; - 125 to 250 AARH for raised Face Flanges and Flat Face Flanges - 63 AARH for Ring Joint Flanges
3- Gland assemblies shall be of “O” ring construction, unless process conditions noted on the individual data sheet require otherwise.
4-Rotameters shall be completely assembled with all accessories before shipping with the orientation of connections as noted on the individual data sheet.
5-Indicating scales shall have full length safety glass shielding which has gasket in both sides and should be approximately 125mm in length for extension meters used for transmitting service or for armoured meters
6-Will be finalized after receiving vendor data.

## FG (Corrosion Inhibitor1)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 5 از 12
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 |  | D03
ROTAMETER
| General | 1 |  | Tag No. |  |  | FG-2101 |  |  |  | FG-2102 |  |  |  | FG-2111
|  | 2 |  | Service |  |  | CHEMICAL (Corrosion Inhibitor) |  |  |  | CHEMICAL (Corrosion Inhibitor) |  |  |  | CHEMICAL (Corrosion Inhibitor)
|  | 3 |  | P&ID No. |  |  | BK-GCS-PEDCO-120-PR-PI-0002-D07 |  |  |  | BK-GCS-PEDCO-120-PR-PI-0003-D07 |  |  |  | BK-GCS-PEDCO-120-PR-PI-0005-D07
|  | 4 |  | Line Name |  |  | CHM-112-0001-AS00-3/4"-NP |  |  |  | CHM-112-0002-AS00-3/4"-NP |  |  |  | CHM-112-0003-AS00-3/4"-NP
|  | 5 |  | Area Classification |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4
|  | 6 |  | Piping Class |  |  | AS00 |  |  |  | AS00 |  |  |  | AS00
|  | 7 |  | Line Size |  |  | 3/4" |  |  |  | 3/4" |  |  |  | 3/4"
|  | 8 |  | Enclosure Type |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass)
|  | 9 |  | Schedule |  |  | SCH.40S |  |  |  | SCH.40S |  |  |  | SCH.40S
| Process Data | 10 |  | Fluid |  |  | CHEMICAL (Corrosion Inhibitor) |  |  |  | CHEMICAL (Corrosion Inhibitor) |  |  |  | CHEMICAL (Corrosion Inhibitor)
|  | 11 |  | Phase |  |  | LIQUID |  |  |  | LIQUID |  |  |  | LIQUID
|  | 12 |  | Flow Rate Min. |  |  | 0.068 lit/hr |  |  |  | 0.132 lit/hr |  |  |  | 0.020 lit/hr
|  | 13 |  | Flow Rate Operating. |  |  | 0.354 lit/hr |  |  |  | 0.354 lit/hr |  |  |  | 1.034 lit/hr
|  | 14 |  | Flow Rate Max. |  |  | 0.354 lit/hr |  |  |  | 0.354 lit/hr |  |  |  | 1.034 lit/hr
|  | 15 |  | Operating Temperature |  |  | AMB. |  |  |  | AMB. |  |  |  | AMB.
|  | 16 |  | Operating Pressure |  |  | 7.5 |  |  |  | 7.5 |  |  |  | 5.1
|  | 17 |  | Design Temperature |  |  | 55(°C) |  |  |  | 55(°C) |  |  |  | 55(°C)
|  | 18 |  | Design Pressure |  |  | 13.9 |  |  |  | 13.9 |  |  |  | 13.9
|  | 19 |  | Molecular Weight |  |  | 198~202 |  |  |  | 198~202 (Note 6) |  |  |  | 198~202 (Note 6)
|  | 20 |  | Operating Viscosity (CSt) |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s
|  | 21 |  | Operating Density |  |  | 860 (Note 6) | kg/m³ |  |  | 860 (Note 6) | kg/m³ |  |  | 860(Note 6) | kg/m³
|  | 22 |  | Color/Transparency |  |  | Colored fluid |  |  |  | Colored fluid |  |  |  | Colored fluid
|  | 23 |  | Max. Allowable Press. Drop |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC)
|  | 24 |  | CP/CV |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6)
| Meter | 25 |  | Function |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD)
|  | 26 |  | Mounting |  |  | In Line - Vertical |  |  |  | In Line - Vertical |  |  |  | In Line - Vertical
|  | 27 |  | Size (in) |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 28 |  | Rating (lbs.) |  |  | 300#(RF) |  |  |  | 300#(RF) |  |  |  | 300#(RF)
|  | 29 |  | Process Connection |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged
|  | 30 |  | Meter scale range |  |  | 0~0.5 Lit/hr (VTC) | lit/h |  |  | 0~0.5 Lit/hr (VTC) | lit/h |  |  | 0~2 Lit/hr (VTC) | lit/h
|  | 31 |  | Meter Scale: Length & Type |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 32 |  | Tube Material |  |  | Flange & Tube: 316 SS (VTC) |  |  |  | Flange & Tube: 316L SS (VTC) |  |  |  | Flange & Tube: 316L SS (VTC)
|  | 33 |  | Float Material |  |  | 316 SS |  |  |  | 316L SS |  |  |  | 316L SS
|  | 34 |  | Scale Length |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 35 |  | Accuracy |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S
|  | 36 |  | Meter Type |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC)
|  | 37 |  | Hydraulic Calib. Required |  |  | Yes |  |  |  | Yes |  |  |  | Yes
|  | 38 |  | Weather Protection |  |  | IP65 |  |  |  | IP65 |  |  |  | IP65
|  | 39 |  | Housing Material |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum
| Transmitter | 40 |  | RFI Protection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 41 |  | Output Signal |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 42 |  | Instrument Range |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 43 |  | Power Supply |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 44 |  | Electrical Certification |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 45 |  | Electrical Connection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 46 |  | Weather Protection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 47 |  | Tropicalization |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 48 |  | Integral Indicator |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 49 |  | - |  |  | - |  |  |  | - |  |  |  | -
| Options | 50 |  | Valve Size |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 51 |  | Valve material |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 52 |  | Air set |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 53 |  | Differential Pressure Regulator |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 54 |  | Gasket material |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 55 |  | NACE Requirements |  |  | No |  |  |  | No |  |  |  | No
| Purchasing Data | 56 |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later |  |  |  | Will be finalized later
|  | 57 |  | Model |  |  | Will be finalized later |  |  |  | Will be finalized later |  |  |  | Will be finalized later
58
59
| NOTES : |  | VTA : VENDOR TO ADVISE | [7 empty] | VTC: VENDOR TO CONFIRM
• The flow direction will be clearly stamped or cast on the body
• Bidder shall be submitted calculation sheet.
D03
D03

## FG (Corrosion Inhibitor2)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 6 از 12
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 |  | D03
ROTAMETER
| General | 1 |  | Tag No. |  |  | FG-2112 |  |  |  | FG-2141 |  |  |  | FG-2151
|  | 2 |  | Service |  |  | CHEMICAL (Corrosion Inhibitor) |  |  |  | CHEMICAL (Corrosion Inhibitor) |  |  |  | CHEMICAL (Corrosion Inhibitor)
|  | 3 |  | P&ID No. |  |  | BK-GCS-PEDCO-120-PR-PI-0004-D07 (1/2) |  |  |  | BK-GCS-PEDCO-120-PR-PI-0012-D07 |  |  |  | BK-GCS-PEDCO-120-PR-PI-0013-D07 (1/3)
|  | 4 |  | Line Name |  |  | CHM-112-0021-AS00-3/4"-NP |  |  |  | CHM-112-0010-FS00-3/4"-NP |  |  |  | CHM-112-0011-FS00-3/4"-NP
|  | 5 |  | Area Classification |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4
|  | 6 |  | Piping Class |  |  | AS00 |  |  |  | FS00 |  |  |  | FS00
|  | 7 |  | Line Size |  |  | 3/4" |  |  |  | 3/4" |  |  |  | 3/4"
|  | 8 |  | Enclosure Type |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass)
|  | 9 |  | Schedule |  |  | SCH.40S |  |  |  | SCH.40S |  |  |  | SCH.40S
| Process Data | 10 |  | Fluid |  |  | CHEMICAL (Corrosion Inhibitor) |  |  |  | CHEMICAL (Corrosion Inhibitor) |  |  |  | CHEMICAL (Corrosion Inhibitor)
|  | 11 |  | Phase |  |  | LIQUID |  |  |  | LIQUID |  |  |  | LIQUID
|  | 12 |  | Flow Rate Min. |  |  | 0.133lit/hr |  |  |  | 0.069 lit/hr |  |  |  | 0.068 lit/hr
|  | 13 |  | Flow Rate Operating. |  |  | 0.680 lit/hr |  |  |  | - |  |  |  | -
|  | 14 |  | Flow Rate Max. |  |  | 0.680 lit/hr |  |  |  | 0.35 lit/hr |  |  |  | 0.349 lit/hr
|  | 15 |  | Operating Temperature |  |  | AMB. |  |  |  | AMB. |  |  |  | AMB.
|  | 16 |  | Operating Pressure |  |  | 7.5 |  |  |  | 54.1 |  |  |  | 52.9
|  | 17 |  | Design Temperature |  |  | 55(°C) |  |  |  | 55(°C) |  |  |  | 55(°C)
|  | 18 |  | Design Pressure |  |  | 13.9 |  |  |  | 62.4 barg (Note 6) |  |  |  | 62.4 barg (Note 6)
|  | 19 |  | Molecular Weight |  |  | 198~202 |  |  |  | 198~202 (Note 6) |  |  |  | 198~202 (Note 6)
|  | 20 |  | Operating Viscosity (CSt) |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s
|  | 21 |  | Operating Density |  |  | 860 (Note 6) | kg/m³ |  |  | 860 (Note 6) | kg/m³ |  |  | 860 (Note 6) | kg/m³
|  | 22 |  | Color/Transparency |  |  | Colored fluid |  |  |  | Colored fluid |  |  |  | Colored fluid
|  | 23 |  | Max. Allowable Press. Drop |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC)
|  | 24 |  | CP/CV |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6)
| Meter | 25 |  | Function |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD)
|  | 26 |  | Mounting |  |  | In Line - Vertical |  |  |  | In Line - Vertical |  |  |  | In Line - Vertical
|  | 27 |  | Size (in) |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 28 |  | Rating (lbs.) |  |  | 300#(RF) |  |  |  | 600#(RF) |  |  |  | 600#(RF)
|  | 29 |  | Process Connection |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged
|  | 30 |  | Meter scale range |  |  | 0~1 Lit/hr (VTC) | lit/h |  |  | 0~0.5 Lit/hr (VTC) | lit/h |  |  | 0~0.5 Lit/hr (VTC) | lit/h
|  | 31 |  | Meter Scale: Length & Type |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 32 |  | Tube Material |  |  | Flange & Tube: 316 SS (VTC) |  |  |  | Flange & Tube: 316 SS (VTC) |  |  |  | Flange & Tube: 316 SS (VTC)
|  | 33 |  | Float Material |  |  | 316 SS |  |  |  | 316 SS |  |  |  | 316 SS
|  | 34 |  | Scale Length |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 35 |  | Accuracy |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S
|  | 36 |  | Meter Type |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC)
|  | 37 |  | Hydraulic Calib. Required |  |  | Yes |  |  |  | Yes |  |  |  | Yes
|  | 38 |  | Weather Protection |  |  | IP65 |  |  |  | IP65 |  |  |  | IP65
|  | 39 |  | Housing Material |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum
| Transmitter | 40 |  | RFI Protection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 41 |  | Output Signal |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 42 |  | Instrument Range |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 43 |  | Power Supply |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 44 |  | Electrical Certification |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 45 |  | Electrical Connection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 46 |  | Weather Protection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 47 |  | Tropicalization |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 48 |  | Integral Indicator |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 49 |  | - |  |  | - |  |  |  | - |  |  |  | -
| Options | 50 |  | Valve Size |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 51 |  | Valve material |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 52 |  | Air set |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 53 |  | Differential Pressure Regulator |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 54 |  | Gasket material |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 55 |  | NACE Requirements |  |  | No |  |  |  | No |  |  |  | No
| Purchasing Data | 56 |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later |  |  |  | Will be finalized later
|  | 57 |  | Model |  |  | Will be finalized later |  |  |  | Will be finalized later |  |  |  | Will be finalized later
58
59
| NOTES : |  | VTA : VENDOR TO ADVISE | [7 empty] | VTC: VENDOR TO CONFIRM
• The flow direction will be clearly stamped or cast on the body
• Bidder shall be submitted calculation sheet.
Note on W28: Shokufeh Azagh: Note 6 to be added
Note on AE26: Shokufeh Azagh: I think operating pressure to be more than line operating pressure
Note on AE34: Shokufeh Azagh: Note 6 to be added

## FG (Corrosion Inhibitor3)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 12
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 | D03
ROTAMETER
| General | 1 |  | Tag No. |  |  | FG-2271
|  | 2 |  | Service |  |  | CHEMICAL (Corrosion Inhibitor)
|  | 3 |  | P&ID No. |  |  | BK-GCS-PEDCO-120-PR-PI-0022-D06
|  | 4 |  | Line Name |  |  | CHM-112-0020-AS00-3/4"-NP
|  | 5 |  | Area Classification |  |  | ZONE 2, IIB T4
|  | 6 |  | Piping Class |  |  | AS00
|  | 7 |  | Line Size |  |  | 3/4"
|  | 8 |  | Enclosure Type |  |  | Safety glass(Borosilicate glass)
|  | 9 |  | Schedule |  |  | SCH.40S
| Process Data | 10 |  | Fluid |  |  | CHEMICAL (Corrosion Inhibitor)
|  | 11 |  | Phase |  |  | LIQUID
|  | 12 |  | Flow Rate Min. |  |  | 0.006 lit/hr
|  | 13 |  | Flow Rate Operating. |  |  | -
|  | 14 |  | Flow Rate Max. |  |  | 0.033 lit/hr
|  | 15 |  | Operating Temperature |  |  | AMB.
|  | 16 |  | Operating Pressure |  |  | 4.9
|  | 17 |  | Design Temperature |  |  | 55(°C)
|  | 18 |  | Design Pressure |  |  | 13.9 barg (Note 6)
|  | 19 |  | Molecular Weight |  |  | 198~202 (Note 6)
|  | 20 |  | Operating Viscosity (CSt) |  |  | 5.5 (Note 6) | Pa·s
|  | 21 |  | Operating Density |  |  | 860 (Note 6) | kg/m³
|  | 22 |  | Color/Transparency |  |  | Colored fluid
|  | 23 |  | Max. Allowable Press. Drop |  |  | 20 mbar(VTC)
|  | 24 |  | CP/CV |  |  | 1.21 (Note 6)
| Meter | 25 |  | Function |  |  | Local Indicator-Gage Type (LZD)
|  | 26 |  | Mounting |  |  | In Line - Vertical
|  | 27 |  | Size (in) |  |  | VTA
|  | 28 |  | Rating (lbs.) |  |  | 300#(RF)
|  | 29 |  | Process Connection |  |  | 3/4", Flanged
|  | 30 |  | Meter scale range |  |  | 0~0.05 Lit/hr (VTC) | lit/h
|  | 31 |  | Meter Scale: Length & Type |  |  | VTA
|  | 32 |  | Tube Material |  |  | Flange & Tube: 316L SS (VTC)
|  | 33 |  | Float Material |  |  | 316L SS
|  | 34 |  | Scale Length |  |  | VTA
|  | 35 |  | Accuracy |  |  | 2% 0f F.S
|  | 36 |  | Meter Type |  |  | Metal tube, Armored type with magnetic pick up (VTC)
|  | 37 |  | Hydraulic Calib. Required |  |  | Yes
|  | 38 |  | Weather Protection |  |  | IP65
|  | 39 |  | Housing Material |  |  | Die Cast Aluminum
| Transmitter | 40 |  | RFI Protection |  |  | N/A
|  | 41 |  | Output Signal |  |  | N/A
|  | 42 |  | Instrument Range |  |  | N/A
|  | 43 |  | Power Supply |  |  | N/A
|  | 44 |  | Electrical Certification |  |  | N/A
|  | 45 |  | Electrical Connection |  |  | N/A
|  | 46 |  | Weather Protection |  |  | N/A
|  | 47 |  | Tropicalization |  |  | N/A
|  | 48 |  | Integral Indicator |  |  | N/A
|  | 49 |  | - |  |  | -
| Options | 50 |  | Valve Size |  |  | N/A
|  | 51 |  | Valve material |  |  | N/A
|  | 52 |  | Air set |  |  | N/A
|  | 53 |  | Differential Pressure Regulator |  |  | N/A
|  | 54 |  | Gasket material |  |  | VTA
|  | 55 |  | NACE Requirements |  |  | No
| Purchasing Data | 56 |  | Manufacturer |  |  | Will be finalized later
|  | 57 |  | Model |  |  | Will be finalized later
58
59
| NOTES : |  | VTA : VENDOR TO ADVISE | [7 empty] | VTC: VENDOR TO CONFIRM
• The flow direction will be clearly stamped or cast on the body
• Bidder shall be submitted calculation sheet.
Note on W28: Shokufeh Azagh: Note 6 to be added
Note on AE26: Shokufeh Azagh: I think operating pressure to be more than line operating pressure
Note on AE34: Shokufeh Azagh: Note 6 to be added

## FG (Methanol1)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 8 از 12
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 |  | D03
ROTAMETER
| General | 1 |  | Tag No. |  |  | FG-2132A |  |  |  | FG-2132B |  |  |  | FG-2132C
|  | 2 |  | Service |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol)
|  | 3 |  | P&ID No. |  |  | BK-GCS-PEDCO-120-PR-PI-0011-D06 (1 / 3) |  |  |  | BK-GCS-PEDCO-120-PR-PI-0011-D06 (2 / 3) |  |  |  | BK-GCS-PEDCO-120-PR-PI-0011-D06 (3 / 3)
|  | 4 |  | Line Name |  |  | CHM-112-0005A-FS00-3/4"-NP |  |  |  | CHM-112-0005B-FS00-3/4"-NP |  |  |  | CHM-112-0005C-FS00-3/4"-NP
|  | 5 |  | Area Classification |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4
|  | 6 |  | Piping Class |  |  | FS00 |  |  |  | FS00 |  |  |  | FS00
|  | 7 |  | Line Size |  |  | 3/4" |  |  |  | 3/4" |  |  |  | 3/4"
|  | 8 |  | Enclosure Type |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass)
|  | 9 |  | Schedule |  |  | SCH.40S |  |  |  | SCH.40S |  |  |  | SCH.40S
| Process Data | 10 |  | Fluid |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol)
|  | 11 |  | Phase |  |  | LIQUID |  |  |  | LIQUID |  |  |  | LIQUID
|  | 12 |  | Flow Rate Min. |  |  | - |  |  |  | - |  |  |  | -
|  | 13 |  | Flow Rate Operating. |  |  | 17.92 lit/hr |  |  |  | 17.92 lit/hr |  |  |  | 17.92 lit/hr
|  | 14 |  | Flow Rate Max. |  |  | 21.5 lit/hr |  |  |  | 21.5 lit/hr |  |  |  | 21.5 lit/hr
|  | 15 |  | Operating Temperature |  |  | AMB. |  |  |  | AMB. |  |  |  | AMB.
|  | 16 |  | Operating Pressure |  |  | 54.8 |  |  |  | 54.8 |  |  |  | 54.8
|  | 17 |  | Design Temperature |  |  | 55(°C) |  |  |  | 55(°C) |  |  |  | 55(°C)
|  | 18 |  | Design Pressure |  |  | 62.4 barg (Note 6) |  |  |  | 62.4 barg (Note 6) |  |  |  | 62.4 barg (Note 6)
|  | 19 |  | Molecular Weight |  |  | 198~202 (Note 6) |  |  |  | 198~202 (Note 6) |  |  |  | 198~202 (Note 6)
|  | 20 |  | Operating Viscosity (CSt) |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s
|  | 21 |  | Operating Density |  |  | 860 (Note 6) | kg/m³ |  |  | 860 (Note 6) | kg/m³ |  |  | 860 (Note 6) | kg/m³
|  | 22 |  | Color/Transparency |  |  | Colored fluid |  |  |  | Colored fluid |  |  |  | Colored fluid
|  | 23 |  | Max. Allowable Press. Drop |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC)
|  | 24 |  | CP/CV |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6)
| Meter | 25 |  | Function |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD)
|  | 26 |  | Mounting |  |  | In Line - Vertical |  |  |  | In Line - Vertical |  |  |  | In Line - Vertical
|  | 27 |  | Size (in) |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 28 |  | Rating (lbs.) |  |  | 600#(RF) |  |  |  | 600#(RF) |  |  |  | 600#(RF)
|  | 29 |  | Process Connection |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged
|  | 30 |  | Meter scale range |  |  | 0~30 Lit/hr (VTC) | lit/h |  |  | 0~30 Lit/hr (VTC) | lit/h |  |  | 0~30 Lit/hr (VTC) | lit/h
|  | 31 |  | Meter Scale: Length & Type |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 32 |  | Tube Material |  |  | Flange & Tube: 316 SS (VTC) |  |  |  | Flange & Tube: 316L SS (VTC) |  |  |  | Flange & Tube: 316L SS (VTC)
|  | 33 |  | Float Material |  |  | 316 SS |  |  |  | 316L SS |  |  |  | 316L SS
|  | 34 |  | Scale Length |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 35 |  | Accuracy |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S
|  | 36 |  | Meter Type |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC)
|  | 37 |  | Hydraulic Calib. Required |  |  | Yes |  |  |  | Yes |  |  |  | Yes
|  | 38 |  | Weather Protection |  |  | IP65 |  |  |  | IP65 |  |  |  | IP65
|  | 39 |  | Housing Material |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum
| Transmitter | 40 |  | RFI Protection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 41 |  | Output Signal |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 42 |  | Instrument Range |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 43 |  | Power Supply |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 44 |  | Electrical Certification |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 45 |  | Electrical Connection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 46 |  | Weather Protection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 47 |  | Tropicalization |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 48 |  | Integral Indicator |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 49 |  | - |  |  | - |  |  |  | - |  |  |  | -
| Options | 50 |  | Valve Size |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 51 |  | Valve material |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 52 |  | Air set |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 53 |  | Differential Pressure Regulator |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 54 |  | Gasket material |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 55 |  | NACE Requirements |  |  | No |  |  |  | No |  |  |  | No
| Purchasing Data | 56 |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later |  |  |  | Will be finalized later
|  | 57 |  | Model |  |  | Will be finalized later |  |  |  | Will be finalized later |  |  |  | Will be finalized later
58
59
| NOTES : |  | VTA : VENDOR TO ADVISE | [7 empty] | VTC: VENDOR TO CONFIRM
• The flow direction will be clearly stamped or cast on the body
• Bidder shall be submitted calculation sheet.

## FG (Methanol2)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 9 از 12
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 |  | D03
ROTAMETER
| General | 1 |  | Tag No. |  |  | FG-2134A |  |  |  | FG-2134B |  |  |  | FG-2134C
|  | 2 |  | Service |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol)
|  | 3 |  | P&ID No. |  |  | BK-GCS-PEDCO-120-PR-PI-0009-D07 (1 / 3) |  |  |  | BK-GCS-PEDCO-120-PR-PI-0009-D07 (2 / 3) |  |  |  | BK-GCS-PEDCO-120-PR-PI-0009-D07 (3 / 3)
|  | 4 |  | Line Name |  |  | CHM-112-0004A-FS00-3/4"-NP |  |  |  | CHM-112-0004B-FS00-3/4"-NP |  |  |  | CHM-112-0004C-FS00-3/4"-NP
|  | 5 |  | Area Classification |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4
|  | 6 |  | Piping Class |  |  | FS00 |  |  |  | FS00 |  |  |  | FS00
|  | 7 |  | Line Size |  |  | 3/4" |  |  |  | 3/4" |  |  |  | 3/4"
|  | 8 |  | Enclosure Type |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass)
|  | 9 |  | Schedule |  |  | SCH.40S |  |  |  | SCH.40S |  |  |  | SCH.40S
| Process Data | 10 |  | Fluid |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol)
|  | 11 |  | Phase |  |  | LIQUID |  |  |  | LIQUID |  |  |  | LIQUID
|  | 12 |  | Flow Rate Min. |  |  | - |  |  |  | - |  |  |  | -
|  | 13 |  | Flow Rate Operating. |  |  | 6.32 lit/hr |  |  |  | 6.32 lit/hr |  |  |  | 6.32 lit/hr
|  | 14 |  | Flow Rate Max. |  |  | 7.58 lit/hr |  |  |  | 7.58 lit/hr |  |  |  | 7.58 lit/hr
|  | 15 |  | Operating Temperature |  |  | AMB. |  |  |  | AMB. |  |  |  | AMB.
|  | 16 |  | Operating Pressure |  |  | 54.8 |  |  |  | 54.8 |  |  |  | 54.8
|  | 17 |  | Design Temperature |  |  | 55(°C) |  |  |  | 55(°C) |  |  |  | 55(°C)
|  | 18 |  | Design Pressure |  |  | 62.4 barg (Note 6) |  |  |  | 62.4 barg (Note 6) |  |  |  | 62.4 barg (Note 6)
|  | 19 |  | Molecular Weight |  |  | 198~202 (Note 6) |  |  |  | 198~202 (Note 6) |  |  |  | 198~202 (Note 6)
|  | 20 |  | Operating Viscosity (CSt) |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s
|  | 21 |  | Operating Density |  |  | 860 (Note 6) | kg/m³ |  |  | 860 (Note 6) | kg/m³ |  |  | 860 (Note 6) | kg/m³
|  | 22 |  | Color/Transparency |  |  | Colored fluid |  |  |  | Colored fluid |  |  |  | Colored fluid
|  | 23 |  | Max. Allowable Press. Drop |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC)
|  | 24 |  | CP/CV |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6)
| Meter | 25 |  | Function |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD)
|  | 26 |  | Mounting |  |  | In Line - Vertical |  |  |  | In Line - Vertical |  |  |  | In Line - Vertical
|  | 27 |  | Size (in) |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 28 |  | Rating (lbs.) |  |  | 600#(RF) |  |  |  | 600#(RF) |  |  |  | 600#(RF)
|  | 29 |  | Process Connection |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged
|  | 30 |  | Meter scale range |  |  | 0~11 Lit/hr (VTC) | lit/h |  |  | 0~11 Lit/hr (VTC) | lit/h |  |  | 0~11 Lit/hr (VTC) | lit/h
|  | 31 |  | Meter Scale: Length & Type |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 32 |  | Tube Material |  |  | Flange & Tube: 316 SS (VTC) |  |  |  | Flange & Tube: 316L SS (VTC) |  |  |  | Flange & Tube: 316L SS (VTC)
|  | 33 |  | Float Material |  |  | 316 SS |  |  |  | 316L SS |  |  |  | 316L SS
|  | 34 |  | Scale Length |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 35 |  | Accuracy |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S
|  | 36 |  | Meter Type |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC)
|  | 37 |  | Hydraulic Calib. Required |  |  | Yes |  |  |  | Yes |  |  |  | Yes
|  | 38 |  | Weather Protection |  |  | IP65 |  |  |  | IP65 |  |  |  | IP65
|  | 39 |  | Housing Material |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum
| Transmitter | 40 |  | RFI Protection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 41 |  | Output Signal |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 42 |  | Instrument Range |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 43 |  | Power Supply |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 44 |  | Electrical Certification |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 45 |  | Electrical Connection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 46 |  | Weather Protection |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 47 |  | Tropicalization |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 48 |  | Integral Indicator |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 49 |  | - |  |  | - |  |  |  | - |  |  |  | -
| Options | 50 |  | Valve Size |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 51 |  | Valve material |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 52 |  | Air set |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 53 |  | Differential Pressure Regulator |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  | 54 |  | Gasket material |  |  | VTA |  |  |  | VTA |  |  |  | VTA
|  | 55 |  | NACE Requirements |  |  | No |  |  |  | No |  |  |  | No
| Purchasing Data | 56 |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later |  |  |  | Will be finalized later
|  | 57 |  | Model |  |  | Will be finalized later |  |  |  | Will be finalized later |  |  |  | Will be finalized later
58
59
| NOTES : |  | VTA : VENDOR TO ADVISE | [7 empty] | VTC: VENDOR TO CONFIRM
• The flow direction will be clearly stamped or cast on the body
• Bidder shall be submitted calculation sheet.

## FG (Methanol3)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 10 از 12
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 |  | D03
ROTAMETER
| General | 1 |  | Tag No. |  |  | FG-2142 |  |  |  | FG-2152
|  | 2 |  | Service |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol)
|  | 3 |  | P&ID No. |  |  | BK-GCS-PEDCO-120-PR-PI-0012-D07 |  |  |  | BK-GCS-PEDCO-120-PR-PI-0013-D07 (1/3)
|  | 4 |  | Line Name |  |  | CHM-112-0006-FS00-3/4"-NP |  |  |  | CHM-112-0007-FS00-3/4"-NP
|  | 5 |  | Area Classification |  |  | ZONE 2, IIB T4 |  |  |  | ZONE 2, IIB T4
|  | 6 |  | Piping Class |  |  | FS00 |  |  |  | FS00
|  | 7 |  | Line Size |  |  | 3/4" |  |  |  | 3/4"
|  | 8 |  | Enclosure Type |  |  | Safety glass(Borosilicate glass) |  |  |  | Safety glass(Borosilicate glass)
|  | 9 |  | Schedule |  |  | SCH.40S |  |  |  | SCH.40S
| Process Data | 10 |  | Fluid |  |  | CHEMICAL (Methanol) |  |  |  | CHEMICAL (Methanol)
|  | 11 |  | Phase |  |  | LIQUID |  |  |  | LIQUID
|  | 12 |  | Flow Rate Min. |  |  | - |  |  |  | -
|  | 13 |  | Flow Rate Operating. |  |  | 44.43 lit/hr |  |  |  | 50.2 lit/hr
|  | 14 |  | Flow Rate Max. |  |  | 53.31 lit/hr |  |  |  | 60.25 lit/hr
|  | 15 |  | Operating Temperature |  |  | AMB. |  |  |  | AMB.
|  | 16 |  | Operating Pressure |  |  | 54.1 |  |  |  | 54.1
|  | 17 |  | Design Temperature |  |  | 55(°C) |  |  |  | 55(°C)
|  | 18 |  | Design Pressure |  |  | 62.4 barg (Note 6) |  |  |  | 62.4 barg (Note 6)
|  | 19 |  | Molecular Weight |  |  | 198~202 (Note 6) |  |  |  | 198~202 (Note 6)
|  | 20 |  | Operating Viscosity (CSt) |  |  | 5.5 (Note 6) | Pa·s |  |  | 5.5 (Note 6) | Pa·s
|  | 21 |  | Operating Density |  |  | 860 (Note 6) | kg/m³ |  |  | 860 (Note 6) | kg/m³
|  | 22 |  | Color/Transparency |  |  | Colored fluid |  |  |  | Colored fluid
|  | 23 |  | Max. Allowable Press. Drop |  |  | 20 mbar(VTC) |  |  |  | 20 mbar(VTC)
|  | 24 |  | CP/CV |  |  | 1.22 (Note 6) |  |  |  | 1.22 (Note 6)
| Meter | 25 |  | Function |  |  | Local Indicator-Gage Type (LZD) |  |  |  | Local Indicator-Gage Type (LZD)
|  | 26 |  | Mounting |  |  | In Line - Vertical |  |  |  | In Line - Vertical
|  | 27 |  | Size (in) |  |  | VTA |  |  |  | VTA
|  | 28 |  | Rating (lbs.) |  |  | 600#(RF) |  |  |  | 600#(RF)
|  | 29 |  | Process Connection |  |  | 3/4", Flanged |  |  |  | 3/4", Flanged
|  | 30 |  | Meter scale range |  |  | 0~75 Lit/hr (VTC) | lit/h |  |  | 0~75 Lit/hr (VTC) | lit/h
|  | 31 |  | Meter Scale: Length & Type |  |  | VTA |  |  |  | VTA
|  | 32 |  | Tube Material |  |  | Flange & Tube: 316L SS (VTC) |  |  |  | Flange & Tube: 316L SS (VTC)
|  | 33 |  | Float Material |  |  | 316L SS |  |  |  | 316L SS
|  | 34 |  | Scale Length |  |  | VTA |  |  |  | VTA
|  | 35 |  | Accuracy |  |  | 2% 0f F.S |  |  |  | 2% 0f F.S
|  | 36 |  | Meter Type |  |  | Metal tube, Armored type with magnetic pick up (VTC) |  |  |  | Metal tube, Armored type with magnetic pick up (VTC)
|  | 37 |  | Hydraulic Calib. Required |  |  | Yes |  |  |  | Yes
|  | 38 |  | Weather Protection |  |  | IP65 |  |  |  | IP65
|  | 39 |  | Housing Material |  |  | Die Cast Aluminum |  |  |  | Die Cast Aluminum
| Transmitter | 40 |  | RFI Protection |  |  | N/A |  |  |  | N/A
|  | 41 |  | Output Signal |  |  | N/A |  |  |  | N/A
|  | 42 |  | Instrument Range |  |  | N/A |  |  |  | N/A
|  | 43 |  | Power Supply |  |  | N/A |  |  |  | N/A
|  | 44 |  | Electrical Certification |  |  | N/A |  |  |  | N/A
|  | 45 |  | Electrical Connection |  |  | N/A |  |  |  | N/A
|  | 46 |  | Weather Protection |  |  | N/A |  |  |  | N/A
|  | 47 |  | Tropicalization |  |  | N/A |  |  |  | N/A
|  | 48 |  | Integral Indicator |  |  | N/A |  |  |  | N/A
|  | 49 |  | - |  |  | - |  |  |  | -
| Options | 50 |  | Valve Size |  |  | N/A |  |  |  | N/A
|  | 51 |  | Valve material |  |  | N/A |  |  |  | N/A
|  | 52 |  | Air set |  |  | N/A |  |  |  | N/A
|  | 53 |  | Differential Pressure Regulator |  |  | N/A |  |  |  | N/A
|  | 54 |  | Gasket material |  |  | VTA |  |  |  | VTA
|  | 55 |  | NACE Requirements |  |  | No |  |  |  | No
| Purchasing Data | 56 |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
|  | 57 |  | Model |  |  | Will be finalized later |  |  |  | Will be finalized later
58
59
| NOTES : |  | VTA : VENDOR TO ADVISE | [7 empty] | VTC: VENDOR TO CONFIRM
• The flow direction will be clearly stamped or cast on the body
• Bidder shall be submitted calculation sheet.

## FG (CHEMICAL)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 11 از 12
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 | D03
ROTAMETER
| General | 1 |  | Tag No. |  |  | FG-3201
|  | 2 |  | Service |  |  | CHEMICAL
|  | 3 |  | P&ID No. |  |  | BK-PPL-PEDCO-320-PR-PI-0001-D04
|  | 4 |  | Line Name |  |  | CHM-112-0007-FS00-3/4"-NP
|  | 5 |  | Area Classification |  |  | ZONE 2, IIB T4
|  | 6 |  | Piping Class |  |  | FS00
|  | 7 |  | Line Size |  |  | 3/4"
|  | 8 |  | Enclosure Type |  |  | Safety glass(Borosilicate glass)
|  | 9 |  | Schedule |  |  | SCH.40S
| Process Data | 10 |  | Fluid |  |  | CHEMICAL (Methanol)
|  | 11 |  | Phase |  |  | LIQUID
|  | 12 |  | Flow Rate Min. |  |  | -
|  | 13 |  | Flow Rate Operating. |  |  | 12.53 lit/hr
|  | 14 |  | Flow Rate Max. |  |  | 15.03 lit/hr
|  | 15 |  | Operating Temperature |  |  | AMB.
|  | 16 |  | Operating Pressure |  |  | 54.8
|  | 17 |  | Design Temperature |  |  | 55(°C)
|  | 18 |  | Design Pressure |  |  | 62.4 barg (Note 6)
|  | 19 |  | Molecular Weight |  |  | 198~202 (Note 6)
|  | 20 |  | Operating Viscosity (CSt) |  |  | 5.5 (Note 6) | Pa·s
|  | 21 |  | Operating Density |  |  | 860 (Note 6) | kg/m³
|  | 22 |  | Color/Transparency |  |  | Colored fluid
|  | 23 |  | Max. Allowable Press. Drop |  |  | 20 mbar(VTC)
|  | 24 |  | CP/CV |  |  | 1.22 (Note 6)
| Meter | 25 |  | Function |  |  | Local Indicator-Gage Type (LZD)
|  | 26 |  | Mounting |  |  | In Line - Vertical
|  | 27 |  | Size (in) |  |  | VTA
|  | 28 |  | Rating (lbs.) |  |  | 600#(RF)
|  | 29 |  | Process Connection |  |  | 3/4", Flanged
|  | 30 |  | Meter scale range |  |  | 0~22 Lit/hr (VTC) | lit/h
|  | 31 |  | Meter Scale: Length & Type |  |  | VTA
|  | 32 |  | Tube Material |  |  | Flange & Tube: 316 SS (VTC)
|  | 33 |  | Float Material |  |  | 316 SS
|  | 34 |  | Scale Length |  |  | VTA
|  | 35 |  | Accuracy |  |  | 2% 0f F.S
|  | 36 |  | Meter Type |  |  | Metal tube, Armored type with magnetic pick up (VTC)
|  | 37 |  | Hydraulic Calib. Required |  |  | Yes
|  | 38 |  | Weather Protection |  |  | IP65
|  | 39 |  | Housing Material |  |  | Die Cast Aluminum
| Transmitter | 40 |  | RFI Protection |  |  | N/A
|  | 41 |  | Output Signal |  |  | N/A
|  | 42 |  | Instrument Range |  |  | N/A
|  | 43 |  | Power Supply |  |  | N/A
|  | 44 |  | Electrical Certification |  |  | N/A
|  | 45 |  | Electrical Connection |  |  | N/A
|  | 46 |  | Weather Protection |  |  | N/A
|  | 47 |  | Tropicalization |  |  | N/A
|  | 48 |  | Integral Indicator |  |  | N/A
|  | 49 |  | - |  |  | -
| Options | 50 |  | Valve Size |  |  | N/A
|  | 51 |  | Valve material |  |  | N/A
|  | 52 |  | Air set |  |  | N/A
|  | 53 |  | Differential Pressure Regulator |  |  | N/A
|  | 54 |  | Gasket material |  |  | VTA
|  | 55 |  | NACE Requirements |  |  | No
| Purchasing Data | 56 |  | Manufacturer |  |  | Will be finalized later
|  | 57 |  | Model |  |  | Will be finalized later
58
59
| NOTES : |  | VTA : VENDOR TO ADVISE | [7 empty] | VTC: VENDOR TO CONFIRM
• The flow direction will be clearly stamped or cast on the body
• Bidder shall be submitted calculation sheet.

## FG (FLARE GAS)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ROTAMETER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 12 از 12
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0018 | D03
ROTAMETER
| General | 1 |  | Tag No. |  |  | FG-2272
|  | 2 |  | Service |  |  | FLARE GAS
|  | 3 |  | P&ID No. |  |  | BK-GCS-PEDCO-120-PR-PI-0022-D07
|  | 4 |  | Line Name |  |  | FL-112-0040-AN07-2"-PT
|  | 5 |  | Area Classification |  |  | ZONE 2, IIB T4
|  | 6 |  | Piping Class |  |  | AN07
|  | 7 |  | Line Size |  |  | 2"
|  | 8 |  | Enclosure Type |  |  | Safety glass(Borosilicate glass)
|  | 9 |  | Schedule |  |  | SCH.160
| Process Data | 10 |  | Fluid |  |  | FLARE GAS
|  | 11 |  | Phase |  |  | GAS
|  | 12 |  | Flow Rate Min. |  |  | 26 Kg/hr
|  | 13 |  | Flow Rate Operating. |  |  | 26 Kg/hr
|  | 14 |  | Flow Rate Max. |  |  | 31 Kg/hr
|  | 15 |  | Operating Temperature |  |  | 19 /37
|  | 16 |  | Operating Pressure |  |  | 4.9
|  | 17 |  | Design Temperature |  |  | 55(°C)
|  | 18 |  | Design Pressure |  |  | 18.2
|  | 19 |  | Molecular Weight |  |  | 24.5
|  | 20 |  | Operating Viscosity (CSt) |  |  | 0.011474
|  | 21 |  | Operating Density |  |  | 5.77
|  | 22 |  | Color/Transparency |  |  | Transparency
|  | 23 |  | Max. Allowable Press. Drop |  |  | 10 mbar(VTC)
|  | 24 |  | CP/CV |  |  | 1.245
| Meter | 25 |  | Function |  |  | Local Indicator-Gage Type (LZD)
|  | 26 |  | Mounting |  |  | In Line - (Note)
|  | 27 |  | Size (in) |  |  | VTA
|  | 28 |  | Rating (lbs.) |  |  | 300#(RF)
|  | 29 |  | Process Connection |  |  | 2", Flanged
|  | 30 |  | Meter scale range |  |  | 0~46 Kg/hr (VTC) | lit/h
|  | 31 |  | Meter Scale: Length & Type |  |  | VTA
|  | 32 |  | Tube Material |  |  | Flange & Tube: 316L SS (VTC)
|  | 33 |  | Float Material |  |  | 316L SS
|  | 34 |  | Scale Length |  |  | VTA
|  | 35 |  | Accuracy |  |  | 2% 0f F.S
|  | 36 |  | Meter Type |  |  | Metal tube, Armored type with magnetic pick up (VTC)
|  | 37 |  | Hydraulic Calib. Required |  |  | Yes
|  | 38 |  | Weather Protection |  |  | IP65
|  | 39 |  | Housing Material |  |  | Die Cast Aluminum
| Transmitter | 40 |  | RFI Protection |  |  | N/A
|  | 41 |  | Output Signal |  |  | N/A
|  | 42 |  | Instrument Range |  |  | N/A
|  | 43 |  | Power Supply |  |  | N/A
|  | 44 |  | Electrical Certification |  |  | N/A
|  | 45 |  | Electrical Connection |  |  | N/A
|  | 46 |  | Weather Protection |  |  | N/A
|  | 47 |  | Tropicalization |  |  | N/A
|  | 48 |  | Integral Indicator |  |  | N/A
|  | 49 |  | - |  |  | -
| Options | 50 |  | Valve Size |  |  | N/A
|  | 51 |  | Valve material |  |  | N/A
|  | 52 |  | Air set |  |  | N/A
|  | 53 |  | Differential Pressure Regulator |  |  | N/A
|  | 54 |  | Gasket material |  |  | VTA
|  | 55 |  | NACE Requirements |  |  | No
| Purchasing Data | 56 |  | Manufacturer |  |  | Will be finalized later
|  | 57 |  | Model |  |  | Will be finalized later
58
59
| NOTES : |  | VTA : VENDOR TO ADVISE | [7 empty] | VTC: VENDOR TO CONFIRM
• The flow direction will be clearly stamped or cast on the body
• Bidder shall be submitted calculation sheet.
• FG-2272 shall be installed on slope line (not vertical) so vendor shall select suitable type.
D03