## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-DT-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2833 |  |  | Transmital Date: 13-Nov-2024
Document Title: Data Sheets For ON/OFF & Shutdown Valves |  |  |  |  | NISOC Tr. No.: BK-PEDCO-NISOC-0308-IN-TR-2833 |  |  | Transmital Date: 13-Nov-2024
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-IN-DT-0006_D04 |  |  | CRS Status: | CM-C2
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-02-07958 | 2023-06-25 | ملاحظه گردید. |  |  | بسته شد.
2 | براي رسيدن به SIL-3 بنظر مي رسد كه تعداد دو عدد ESD Solenoid بايد در نظر گرفته شود. |  | BK-SUR-ENG-INS-02-07958 | 2023-06-25 | الزام SIL3 برای این شیر وجود ندارد. همچنین نگرانی کارفرما در مورد اضافه کردن کابل مشابه با در نظر گرفتن JB مرتفع خواهد شد ( نوت* به مدرک اضافه گردید.) |  |  | در صورت تایید کارفرما مورد قبول می باشد.
D03
1 | Design Pressure و shut-off Pressure می بایست مطابق با اطلاعات FN05 باشد. در صورت لزوم می بایست مدرک PMS مورد بازنگری قرار گیرد. |  | BK-SUR-ENG-INS-03-09755 | 2024-11-30 | مدرک مطابق آخرین نسخه از P&ID بروز رسانی گردید . لازم به ذکر است این مورد در نسخه بعدی مدرک PMS توسط بخش PIPINGاصلاح می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 30 Nov 2024 |  |  |  |  | Date: