| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| PMR FOR EXISTENT MV SWITCHGEAR EXPANSION, RCP & MV CAPACITOR BANK نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |
| D03 | Jan. 2025 | FI | M.Fahimi | M.Fakharian | S.Faramarzpour |  |
| D02 | Aug. 2024 | IFI | H.Shakiba | M.Fakharian | M.Sadeghian |  |
| D01 | Sep. 2023 | IFI | H.Shakiba | M.Fakharian | S.Faramarzpour |  |
| D00 | Jan. 2023 | IFI | H.Shakiba | M.Fakharian | M.Mehrshad |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | Client Approval |
| Class:3 |  | Client Doc. Number: F0Z-709331 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for Client Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X | X |  |  | 51 |  |  |  |  |  |
| 2 | X | X | X | X |  |  | 52 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 53 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 54 |  |  |  |  |  |
| 5 | X | X |  |  |  |  | 55 |  |  |  |  |  |
| 6 | X | X |  |  |  |  | 56 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 57 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 58 |  |  |  |  |  |
| 9 | X |  |  |  |  |  | 59 |  |  |  |  |  |
| 10 | X | X |  |  |  |  | 60 |  |  |  |  |  |
| 11 | X | X | X | X |  |  | 61 |  |  |  |  |  |
| 12 | X | X |  |  |  |  | 62 |  |  |  |  |  |
| 13 | X | X |  |  |  |  | 63 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 64 |  |  |  |  |  |
| 15 | X | X |  |  |  |  | 65 |  |  |  |  |  |
| 16 | X |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 |  |  |  |  |  |  | 68 |  |  |  |  |  |
| 19 |  |  |  |  |  |  | 69 |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	GENERAL	5

3.0	reference / ATTACHED DOCUMENTS	5

4.0	SUBJECT OF THE SUPPLY	6

5.0	LIMITS OF SUPPLY	6

5.1	scope of supply	6

5.1.1	main description	6

5.1.2	Spare Parts	7

5.1.3	Other items	7

5.2	Exclusions	7

5.3	Battery Limits	8

6.0	INSPECTION AND TESTS	8

7.0	VENDOR DOCUMENTATION REQUIREMENTS & SCHEDULE	8

8.0	UNIT RESPONSIBILITY	8

9.0	GUARANTEE AND WARRANTY	8

10.0	DEVIATION	9

11.0	PRICE BREAKDOWN	10

ATTACHMENT 1	11

11.1	LIST OF REFERENCE / APPLICABLE DOCUMENTS	11

ATTACHMENT 2	12

11.2	VENDOR DOCUMENTS MIN. REQUIREMENT	12

ATTACHMENT 3	15

11.3	DEVIATIONS / EXCEPTIONS TO JOB SPECIFICATION	15

ATTACHMENT 4	16

11.4	ALTERNATIVES TO JOB SPECIFICATION	16

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

As a part of the Project, a New Gas Compressor Station (adjacent to existing Binak GCS) shall be constructed to gather of 15 MMSCFD (approx.) associated gases and compress & transfer them to Siahmakan GIS.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – Surface Facilities; New Gas Compressor Station |
| EPD/EPC CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection (D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR (GC) and approved by CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- GENERAL

- This document presents the item material requisitions for Contractor’s use as appropriate.

- This material requisition covers the requirements for the design, manufacturing, testing and supply of MV Switchgear, MV Capacitor Bank & RCP Panel as listed below. All equipment/devices/items shall conform to this requisition and all specifications which have been mentioned in attachment 1 of this material requisition.

- The vendor's supply shall include:

| No. | Item | Description | Total QTY |
| --- | --- | --- | --- |
| 1 | MV Switchgear | 11 KV, 50 Hz, 1600 A, 25 KA, 1s, Indoor, Free Standing, Floor Mounted | 1 (Note 1) |
| 2 |  | 3.3 KV, 50 Hz, 630 A, 25 KA, 1s, Indoor, Free Standing, Floor Mounted | 1 |
| 3 |  | Individual MV Capacitor Bank, 11 KV, Free Standing, Floor Mounted | 3 |
| 4 | RCP | Remote Control Panel for MV Switchgear, Wall Mounted | 1 |

Note 1: there is MV Switchgear in BINAK GCS which extension on both sides is required. It means only 8 outgoing cells 11 KV shall be provided by vendor. 4 cells on switchgear A & 4 cells on switchgear B according to “BK-GCS-PEDCO-120-EL-SL-0003”. If adaptor is required, vendor shall consider on both side.

- reference / ATTACHED DOCUMENTS

- Specified documents in attachment 1 shall be considered as a part of this material Requisition.

- All codes and standards which have been referenced in above mentioned specs shall be considered.

- In case of any conflict between the contents of this document or any discrepancy between this document and other project documents or reference standards, this issue must be reported to the CLIENT. The final decision in this situation will be made by CLIENT.

- Deviations

Any exceptions/clarifications to codes/standards and specifications listed in attachment 1 must be clearly stated in a separate dedicated section of the proposal in the format submitted in attachment 3.

The proposed deviations/comments list shall include as minimum:

- Reference for the involved specification, chapter and paragraph.

- Technical justification for the non-compliance.

- Detailed description of the proposed alternative.

If no exceptions or clarifications exist, either for the complete referenced document or an individual paragraph, the supplier shall be considered to be in full compliance with the relevant document.

The supplier may propose materials of equivalent or better quality compared to those indicated in the equipment data sheet. Even these cases shall be duly included/technically supported in the deviations/clarifications list.

- SUBJECT OF THE SUPPLY

The supplier shall supply MV Switchgear, MV Capacitor Bank & RCP. The scope of supply is detailed at para. 5. The supplier shall include in the supply, all other equipment/devices/items not listed in the following, but necessary for a good design and a safe operation, taking into account process data and installation conditions such as area classification and climatic conditions.

The grade of shop assembly of the equipment/devices/items supplied shall be at maximum extent to facilitate site erection and pre-commissioning activities.

- LIMITS OF SUPPLY

  - scope of supply

### main description

MV Switchgear & MV Capacitor Bank shall be according to “Existent MV Switchgear Expansion Single Line Diagram (BK-GCS-PEDCO-120-EL-SL-0003)”, “Data Sheets for Expansion of MV Switchgear (BK-GCS-PEDCO-120-EL-DT-0004)” & “Capacitor Banks Single Line Diagram (BK-GCS-PEDCO-120-EL-SL-0007)” & “Data Sheets for Remote Control Panel (BK-GCS-PEDCO-120-EL-DT-0015)”.

The supplier shall assume overall responsibility for the design, manufacture, assembly, test and performance of all equipment/devices/items supplied as indicated in this requisition. This shall include, but not be limited to:

- Resolve engineering issues relating to equipment/devices/items within the scope of supply.

- Provide detailed design and documentation of all equipment/devices/items and components within the scope of supply in accordance with attachment 2 of this document.

- Provide all necessary information documents in order to allow the contractor to erect, install and verify the proposed equipment/devices/items.

- Implement a quality assurance plan

- The quality plan applied to the scope of supply shall include:

  - QA/ QC organization chart and procedures that shall be submitted for approval.

  - Plan for HOLD points in the production process proposed to PURCHASER for witness or approval particular activities.

  - Production schedule indicating main quality manufacturing processes, inspection and tests.

  - Qualification of all personnel performing tests to be reviewed by the inspector

  - Supplier shall also provide the description of the following quality activities:

- Sub suppliers products quality

- Quality check and identification of the materials and equipment entering in their manufacturing shop.

- Calibration of test instruments and equipment

- Provide detailed specifications and data sheets.

### Spare Parts

Following items shall be considered (supplied) and included in the bid documentation:

- Spare parts for commissioning and start-up; a qualified and complete list based on PROJECT SPARE PART SUPPLY PROCEDURE (Doc. No. E&D-QC-SP-1).

- Spare parts for two years operation; a qualified and complete list based on PROJECT SPARE PART SUPPLY PROCEDURE (Doc. No. E&D-QC-SP-1).

- Capital spare parts (as option / if any)

### Other items

Special tools required for installation and maintenance

  - Exclusions

The following items are excluded by the supplier scope of supply and will be provided by purchaser:

Not Applicable

  - Battery Limits

The battery limits are summarized as follows:

Not Applicable

- INSPECTION AND TESTS

The equipment shall be inspected and tested in accordance with the quality control plan issued by the supplier and approved by the PURCHASER before the award of the order. The ITP shall at least be according to the PROJECT ITP PROCEDURE (Doc. No. ICE-EID-MI-SP01-Rev01 & ICE-EID-MI-SP02-REV-01) and data sheets (if any).

The supplier shall in any case conduct all the tests required by contractual documents, specifications, codes and standards, manufacturer standard quality system and keep the relevant documentation.

- VENDOR DOCUMENTATION REQUIREMENTS & SCHEDULE

- Vendor document shall be according to attachment 2 of this document.

- All documents, preliminary or final, are to be stamped and signed by the supplier.

- Failure in dispatch of the required documents shall cause the supply to be considered as unfulfilled.

- PURCHASER’s approval does not relieve vendor, in any way, from his obligation to fulfill the requirements of the purchase order documents.

- All vendor drawings and documents shall be in English language.

All drawings and documents are to be identified as per clause 1 “GENERAL DEFINITION”

- UNIT RESPONSIBILITY

VENDOR shall be responsible for the design, engineering, co-ordination, supply, delivery, testing, final check-out and satisfactory operation of the equipment/devices/items. The engineering coordination also includes responsibility for handing and expediting drawings.

Also VENDOR shall be responsible for ensuring that all relevant information and documentation is passed on the sub-suppliers.

- GUARANTEE AND WARRANTY

All material and Equipment/Devices/Items in VENDOR’s scope of work/supply shall be guaranteed by VENDOR.

The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site

VENDOR shall guarantee the performance of supplied items (if any).

VENDOR shall guarantee that the Equipment/Device/Item is suitable for the operating conditions herein specified, and that all materials and components are free from any defects; verifications of all calculations are in VENDOR’s responsibility.

VENDOR shall unconditionally guarantee the materials and workmanship of all material and/or services. If, within the guarantee period, any defects occur which are due to faulty material and/or services included in his scope (design, manufacturing, inspection, testing, supply & etc.), VENDOR shall, at his own expense, repair or adjust the condition, or replace the material and/or services to the complete satisfaction of CLIENT’s representative. These repairs, replacement or adjustments shall be made only at such time as will be least detrimental to the operation of the CLIENT’s business.

VENDOR warrants promptly repairing or replacing the defective parts in the warranty period.

Vendor shall ensure a correct and safe operation of the unit, providing all safety protection Devices.

Vendor shall be responsible for the safe, reliable, continuous functioning of the Equipment/Devices/Items.

VENDOR is fully responsible for the design of package for correct and safe operation based on project requirement during package life time; therefore, VENDOR shall specify any documents/specifications which may be required for design, manufacture and finalizing of Equipment/Devices/Items to avoid any problems during the package operation at site before P.O; otherwise, VENDOR shall be hold responsible for any corresponding deviation from expectations from the Equipment/Devices/Items.

- DEVIATION

VENDOR’s proposal shall be prepared in strict compliance with the requirements set forth in the relevant specifications of tender documents.

VENDOR shall include in his proposal the statement of compliance with the tender documents should VENDOR wish to submit exception to the requirements of tender documents. They shall be submitted for PURCHASER’s approval.

- PRICE BREAKDOWN

Breakdown price of following items shall be included in the proposal, as well as total price.

- Material and Fabrication for each Section Separately

- Pre-commissioning & commissioning spare parts (END-QC-SP-1)

- 2 years operational spare parts (END-QC-SP-1)

- Packing & transportation

- Other fee (if any)

D03

ATTACHMENT 1

## LIST OF REFERENCE / APPLICABLE DOCUMENTS

| No. | Document No. | Document Title | Rev. |
| --- | --- | --- | --- |
| Process |  |  |  |
|  | BK-GNRAL-PEDCO-000-PR-DB-0001 | Process Basis of Design | D08 |
| Electrical |  |  |  |
|  | BK-GNRAL-PEDCO-000-EL-DC-0001 | Electrical System Design Criteria | D02 |
|  | BK-GNRAL-PEDCO-000-EL-SP-0002 | Specification for MV Switchgear | D03 |
|  | BK-GNRAL-PEDCO-000-EL-SP-0012 | Specification for Capacitor Bank | D03 |
|  | BK-GNRAL-PEDCO-000-EL-SP-0008 | Specification for Bulk Materials | D04 |
|  | BK-GCS-PEDCO-120-EL-LI-0001 | Electrical Load List | D08 |
|  | BK-GCS-PEDCO-120-EL-SL-0003 | Existent MV Switchgear Expansion Single Line Diagram | D06 |
|  | BK-GCS-PEDCO-120-EL-DG-0001 | Electrical Typical Schematic Diagrams For MV Panel | D08 |
|  | BK-GCS-PEDCO-120-EL-DT-0004 | Data Sheets for Expansion of MV Switchgear | D03 |
|  | BK-GCS-PEDCO-120-EL-DT-0015 | Data Sheets For Remote Control Panel | D02 |
|  | BK-GCS-PEDCO-120-EL-CN-0011 | Calculation Note for Capacitor Banks | D04 |
|  | BK-GCS-PEDCO-120-EL-SL-0007 | Capacitor Banks Single Line Diagram | D04 |
|  | BK-GCS-PEDCO-120-EL-DT-0007 | Data Sheets for Capacitor Bank | D03 |
|  | BK-GCS-PEDCO-120-EL-LI-0005 | Electrical I/O Signal List | D03 |
|  | BK-GCS-PEDCO-120-EL-DG-0005 | Wiring Diagram for Remote Control Panel (RCP) | D01 |
|  | BK-GCS-PEDCO-120-EL-PY-0008 | Electrical Equipment Arrangement Layout for Building | D04 |
|  | BK-GCS-PEDCO-120-EL-LI-0002 | Electrical Power & Control Cable Schedule | D02 |
| Architect |  |  |  |
|  | BK-GCS-PEDCO-120-AR-DW-0002 | Architectural Detail Drawing for Extension of Existing Elect. Building | D07 |
| General |  |  |  |
|  | BK-GNRAL-PEDCO-000-QC-PR-0022 | Specification for Final Data Book ( FDB ) Requirements | D00 |
|  | BK-GNRAL-PEDCO-000-QC-PR-0045 | Packing , Marking , Transportation Procedure | D00 |
|  | ICE-EID-MI-SP01-Rev01 | دستورالعمل بازرسی، خرید و ساخت کالا | - |
|  | ICE-EID-MI-SP02-Rev01 | سطح بازرسی کالا و تجهیزات | - |
|  | E&C-QC-SP-1 | دستورالعمل تامین قطعات یدکی راه اندازی و راهبری دو سالانه | - |
|  | BK-GNRAL-PEDCO-000-PI-SP-0006 | Specification For Painting | D04 |
|  | BK-GNRAL-HD-000-PM-PR-0003 | Document Numbering Procedure | G04 |

# ATTACHMENT 2

## VENDOR DOCUMENTS MIN. REQUIREMENT

| Item No. | Document | With Bid | TIME SCHEDULE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | For Review |  | Final Issue |  |
|  |  | Copies No./Type (7) | Copies No./Type (1) | Solar days (2) | Copies No./Type (1) | Calendar days (3) |
| MANAGEMENT |  |  |  |  |  |  |
|  | Vendor Document Index and Schedule | 4N | 6C+E |  | 6C+E |  |
|  | Organization Brief | 3N | 6C+E |  |  |  |
|  | Schedule Level 1, 2, 3 & 4 showing Engineering, Procurement, Fabrication, Inspection, Testing, and Delivery Plan. | 4N | 6C+E |  | 6C+E |  |
|  | Physically Progress Report (Every 2 Weeks)) |  | 6C+E |  |  |  |
|  | Project Organization Chart | 3N | 6C+E |  |  |  |
|  | Reference List | 3N |  |  |  |  |
|  | Vendor Catalogue | 3N |  |  |  |  |
|  | Sub-vendors list | 3N |  |  |  |  |
|  | Final Data Book | 3N |  |  |  |  |
|  | Final Data Book Index | 3N |  |  |  |  |
| QUALITY |  |  |  |  |  |  |
|  | Quality Assurance Manual /Quality Management System Certificate (according to latest rev. of ISO) | 4N |  |  | 6C+E |  |
|  | Preliminary Inspection and Test Plan | 4N |  |  |  |  |
|  | Inspection and Test Plan |  | 6C+E |  | 6C+E |  |
| HSE |  |  |  |  |  |  |
|  | HSE Procedure |  | 6C+E |  | 6C+E |  |
| ENGINEERING |  |  |  |  |  |  |
|  | Updated and Completed enquiry data sheet/s. |  | 6C+E |  | 6C+E |  |
|  | Detail Specification |  | 6C+E |  | 6C+E |  |
|  | General Description |  | 6C+E |  | 6C+E |  |
|  | Single Line Diagram |  | 6C+E |  | 6C+E |  |
|  | Schematic Diagrams |  | 6C+E |  | 6C+E |  |
|  | Wiring Diagram |  | 6C+E |  | 6C+E |  |
|  | Termination Diagram |  | 6C+E |  | 6C+E |  |
|  | Heat Dissipation |  | 6C+E |  | 6C+E |  |
|  | gland plate drawing |  | 6C+E |  | 6C+E |  |
|  | Alarm and set point list for protection relays |  | 6C+E |  | 6C+E |  |
|  | Dimensional and outline drawings |  | 6C+E |  | 6C+E |  |
|  | Civil Work Guide Drawings and Loads |  | 6C+E |  | 6C+E |  |
|  | Bus bars Calculation |  | 6C+E |  | 6C+E |  |
|  | Technical Specification |  | 6C+E |  | 6C+E |  |
|  | CT & PT Calculation |  | 6C+E |  | 6C+E |  |
|  | Calculation of Capacitor Bank |  | 6C+E |  | 6C+E |  |
|  | Protective relay/s types, calculation, |  | 6C+E |  | 6C+E |  |
|  | Final Logic Diagram and Interlocking |  | 6C+E |  | 6C+E |  |
| PROCUREMENT |  |  |  |  |  |  |
|  | List of Sub-Suppliers ( table giving: part of equipment, tag no., sub-supplier reference)(5.1.3) | 4N |  |  | 6C+E |  |
|  | Unpriced copy of sub-orders |  | 6C+E |  |  |  |
| MANUFACTURING |  |  |  |  |  |  |
|  | Surface Preparation and Painting Procedures |  | 6C+E |  | 6C+E |  |
|  | Welder Qualification Procedure |  | 6C+E |  | 6C+E |  |
| TESTING |  |  |  |  |  |  |
|  | Factory Acceptance Test (FAT) Procedure |  | 6C+E |  | 6C+E |  |
|  | SAT Procedure |  | 6C+E |  | 6C+E |  |
| RECORDS, REPORTS & CERTIFICATES |  |  |  |  |  |  |
|  | Type Test Certificate |  | 6C+E |  | 6C+E |  |
| INSTALLATION |  |  |  |  |  |  |
|  | Sub-Assembly Documentation |  | 6C+E |  | 6C+E |  |
|  | Sub-Assembly Drawings |  | 6C+E |  | 6C+E |  |
|  | Erection/Installation Manual (if required) |  | 6C+E |  | 6C+E |  |
|  | Handling, Transportation & Storage Instructions & Preservation |  | 6C+E |  | 6C+E |  |
|  | Unpacking & Inspection Instructions |  | 6C+E |  |  |  |
|  | Packing List |  | 6C+E |  | 6C+E |  |
| OPERATION & MAINTENANCE |  |  |  |  |  |  |
|  | Operating Instructions |  | 6C+E |  | 6C+E |  |
|  | Maintenance Instructions (if required) |  | 6C+E |  | 6C+E |  |
|  | Commissioning & Start-up Manual |  | 6C+E |  | 6C+E |  |
|  | List of Spare Parts Commissioning & Start-up | 4N | 6C+E |  | 6C+E |  |
|  | List of Spare Parts 2 Years Operation | 4N | 6C+E |  | 6C+E |  |
|  | List of Special Tools | 4N | 6C+E |  | 6C+E |  |
|  | Software Manual (incl. Troubleshooting) |  | 6C+E |  | 6C+E |  |
|  | Function Test Procedure |  | 6C+E |  | 6C+E |  |
| OTHERS |  |  |  |  |  |  |
|  | All others documents (if required) will be listed in the order |  | 6C+E |  |  |  |
| NOTES: (1) N= Number of document, C=Copy, E=Electronic Copy (2) Starting from date of order placement (3) Starting from reception of documentation without comments (4) First issue of the document is subjected to the release of payment milestone as per purchase order (5) Calendar days after reception of drive data (6) Prior to testing (7) One copy each bid copy (8) List of Documents Will be Finalized in Vendor Document index and Schedule. |  |  |  |  |  |  |

# ATTACHMENT 3

## DEVIATIONS / EXCEPTIONS TO JOB SPECIFICATION

Requisition No.:

Description:

Equipment No.:

| Item No. | Description of proposed exception | Recommended revision to job specification | Reason for proposed exception | Effect on base proposal if CONTRACTOR rejects exception |
| --- | --- | --- | --- | --- |

# ATTACHMENT 4

## ALTERNATIVES TO JOB SPECIFICATION

Requisition No.:

Description:

Equipment No.:

| Item No. | Job Specification No. & Paragraph No. | Requirements of Job Specification | Description of Proposed Alternative | Reason for Proposed Alternative |
| --- | --- | --- | --- | --- |