## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-DG-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2795 |  |  | Transmital Date: 6-Oct-2024
Document Title: Control System/ESD system Loop Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0307-IN-TR-2795 |  |  | Transmital Date: 6-Oct-2024
[5 empty] | CRS No:NISOC-CRS-BK-PPL-PEDCO-320-IN-DG-0005_D03 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در مورد نظرات و پاسخ C.R.S ، با توجه به اینکه برای شیر قطع اضطراری موجود از JB استفاده نشده است و فاصله شیر تا اتاق کنترل زیاد می باشد، کشیده یک جفت مشابه برای مواقع قطع ناخواسته کابل ضروری می باشد. |  | 03-2294-308012 | 1403/08/07 | برای ESOV یک کابل مشابه اضافه شد، همچنین بخاطر Terminate کردن کابل در سمت فیلد، یک JB اضافه شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 2 Oct 2023 |  |  |  |  | Date: