## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0010 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-NISOC-T-2836 |  |  | Transmital Date: 16-Nov-2024
Document Title: Data Sheets For ON/OFF & Shutdown Valves |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0308-IN-TR-2836 |  |  | Transmital Date: 16-Nov-2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-DT-0010_D04 |  |  | CRS Status: | C2
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در خصوص متریال اعلام شده تطابق مشخصات با PMS تأیید شده الزامی است. |  | 1401-2294-296295 | 1401/08/14 | با توجه به نظر کارفرمای محترم مدرک مطابق آخرین نسخه از مدارک پیشنیاز تهیه گردید.
2 | علت تغیر فشار INLET/OUTLET PRESSURE جهت ESDV-2102/2101 درج شده در مدرک نسبت به ویرایش پیشین ارائه گردد. |  | 1401-2294-296295 | 1401/08/14 | فشار گزارش شده بر اساس ماکزیمم فشار عملیاتی ورودی ایستگاه و یکسان برای ورودی و خروجی شیر اعلام شده است.
D02
1 | کامنت ها به پیوست ارایه می گردد. |  | BK-SUR-ENG-INS-03-09493 | 2024-09-01 | پاسخ کارفرمای محترم به ضمیمه ارسال گردید.
2 | با توجه به اینکه مدرک پیش نیاز MR و TBE می باشد و مدارک فوق ارایه شده اند می بایست هر چه سریعتر بروز رسانی گردد. |  | BK-SUR-ENG-INS-03-09493 | 2024-09-01 | مدرک بروز رسانی و ارسال گردید.
D03
1 | حذف شیرهای XV-2123 A/B/C به عنوان خط Equalizing مورد تایید نمی باشد. |  | BK-SUR-ENG-INS-03-09767 | 2024-12-01 | مطابق آخرین نسخه از مدرک (BK-GCS-PEDCO-120-PR-PI-0006)P&ID شیرهای XV-2123 A/B/C حذف گردیدند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: F.Amiri P.Maleki S.Akbari | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 1 Dec 2024 |  |  |  |  | Date: