## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 56
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0009 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT / F&G CABLE LIST نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  | JAN.2025 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D03 |  | SEP.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D02 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | COMPANY Approval
Class: 1 |  |  |  | COMPANY Doc. Number: F0Z-708975
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for COMPANY Review
AB-A: As-Built –Approved

## Revisions
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 56
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0009 |  | D04
ITEM | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 55 |  | X |  | X |  | X |  | X
2 | X | X | X |  | X |  | X |  | 56 |  | X |  | X |  | X | X | X
3 | X | X | X |  | X |  | X |  | 57 |  | X |  | X |  | X | X
4 | X | X | X |  | X |  | X |  | 58 |  | X |  | X |  | X | X
5 | X | X | X |  | X |  | X |  | 59 |  | X |  |  |  | X | X
6 | X | X | X |  | X |  | X |  | 60 |  | X |  |  |  | X | X
7 | X | X | X |  | X |  | X |  | 61 |  | X |  |  |  | X | X
8 | X | X | X |  | X |  | X |  | 62 | [5 empty] | X | X
9 | X | X | X |  | X |  | X |  | 63 | [5 empty] | X | X
10 | X | X | X |  | X |  | X |  | 64 | [5 empty] | X | X
11 | X | X | X |  | X |  | X |  | 65 | [6 empty] | X
12 | X | X | X |  | X |  | X |  | 66 | [6 empty] | X
13 | X | X | X |  | X |  | X |  | 67 | [6 empty] | X
14 | X | X | X |  | X |  | X |  | 68 | [6 empty] | X
15 | X | X | X |  | X |  | X |  | 69 | [6 empty] | X
16 | X | X | X |  | X |  | X |  | 70
17 | X | X | X |  | X |  | X |  | 71
18 | X | X | X |  | X |  | X |  | 72
19 | X | X | X |  | X |  | X |  | 73
20 | X | X | X |  | X |  | X |  | 74
21 | X | X | X |  | X |  | X |  | 75
22 | X | X | X |  | X |  | X |  | 76
23 | X | X | X |  | X |  | X |  | 77
24 | X | X | X |  | X |  | X |  | 78
25 | X | X | X |  | X |  | X |  | 79
26 | X | X | X |  | X |  | X |  | 80
27 | X | X | X |  | X |  | X |  | 81
28 | X | X | X |  | X |  | X |  | 82
29 | X | X | X |  | X |  | X |  | 83
30 | X | X | X |  | X |  | X |  | 84
31 | X | X | X |  | X |  | X |  | 85
32 | X | X | X |  | X |  | X |  | 86
33 | X | X | X |  | X |  | X |  | 87
34 | X | X | X |  | X |  | X |  | 88
35 | X | X | X |  | X |  | X |  | 89
36 | X | X | X |  | X |  | X |  | 90
37 | X | X | X |  | X |  | X |  | 91
38 | X | X | X |  | X |  | X |  | 92
39 | X | X | X |  | X |  | X |  | 93
40 | X | X | X |  | X |  | X |  | 94
41 | X | X | X |  | X |  | X |  | 95
42 | X | X | X |  | X |  | X |  | 96
43 | X | X | X |  | X |  | X |  | 97
44 | X | X | X |  | X |  | X |  | 98
45 | X | X | X |  | X |  | X |  | 99
46 | X | X | X |  | X |  | X |  | 100
47 | X | X | X |  | X |  | X |  | 101
48 | X | X | X |  | X |  | X |  | 102
49 | X | X | X |  | X |  | X |  | 103
50 | X | X | X |  | X |  | X |  | 104
51 | X | X | X |  | X |  | X |  | 105
52 | X | X | X |  | X |  | X |  | 106
53 | X | X | X |  | X |  | X |  | 107
54 | X | X | X |  | X |  | X |  | 108

## Notes & References
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 56
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO | 120 | IN | LI |  | 0009 | D04
1- Cable length will be finalized after Received Vendor Document
2- Gland Size will be finalized after Instrument Cable/Cable Gland P.O
3- Cutting column/Drum no. will be finalized after cable P.O.
4- All cables shall be accordance with Flame retardant standard IEC 60332
5- Fire Resistant cables shall be accordance with standard IEC 60331.
6- All conductors shall be accordance with standard IEC 60228 and the material shall be Tinned cupper.
7- The sequence of each Horn / Beacon Junction box is its corresponding tag Number.
Flame Retardant : PVC , Color : Light Blue for I.S. & Gray for N.I.S
Fire Resistant : PVC , Color : Light Blue with Red Strip for I.S. & Gray with Red Strip for N.I.S & Red for F&G
[6 empty] | 8- Cable type legend : | [9 empty] | 9- Junction Box Numbering : :
[5 empty] | X - X X - X - X X | [9 empty] | JBX - X - XXXX
| BL: Light Blue | [15 empty] | Sequence No.
| BR: Light Blue/Red Strip | [15 empty] | NOTE 9
| GY: Gray | [15 empty] | A : Analoge
| GR: Gray /Red Strip | [15 empty] | D : Digital
| RD: Red | [15 empty] | S : Solenoid
D : DCS
| Number of core | [15 empty] | E : ESD
| or pair or triad | [10 empty] | 1: 1 mm² |  |  |  |  | F : F&G
2: 1.5 mm²
3: 2.5 mm²
[7 empty] | P: Pair |  |  |  |  | 4: 6 mm²
[7 empty] | C: Core |  |  |  |  | 5: 16 mm²
[7 empty] | T: Triad |  |  |  |  | 6: 35 mm²
REFERENCES:
| 1 | BK-GCS-PEDCO-120-IN-LI-0002- IO LIST FOR CONTROL SYSTEM
| 2 | BK-GCS-PEDCO-120-IN-LI-0003- IO LIST FOR ESD SYSTEM
| 3. | BK-GCS-PEDCO-120-IN-LI-0004-D04 IO LIST FOR F&G SYSTEM
| 4 | BK-GNRAL-PEDCO-000-IN-SP-0010- SPECIFICATION FOR INSTRUMENT & F&G CABLES
| 5 | BK-GCS-PEDCO-120-IN-DG-0008- INSTRUMENT & F&G JUNCTION BOX TERMINATION DIAGRAM
ABBREVIATION :
| 1- CU |  | : Conductor (Standard tinned copper)
| 2- XLPE |  | : Insulation (Cross-linked polyethylene, low smoke, zero halogen)
| 3- DW |  | : Drain Wire
| 4- ISC |  | : Individual Screen
| 5- DW |  | : Drain Wire
| 6- OSC |  | : Overall Screen
| 7- PVC |  | : Inner sheath (polyvinyl chloride insulation )
| 8- SWA |  | : Armoure (Steel wire Armord )
| 9- PVC |  | : Outer sheath (polyvinyl chloride insulation)
| 10- FRT |  | : Flame Retardant
| 11- FRS |  | : Fire Resistant
| 12- FMX |  | : F&G Matix Panel
D04

## SUMMARY
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 56
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0009 | D04
1
ITEM | TYPE | DESCRIPTION | [8 empty] | QUANTITY (m)(NOTE1) |  | ITEM | TYPE | DESCRIPTION | QUANTITY (m)(NOTE1)
[11 empty] | ACTUAL (m) | (PLUS 20%) (m) |  |  |  | DCS (m) | ESD (m) | F&G (m) | N2 PK (m) | G.C. PK (m) | Dy. PK (m)
Flame Redandant , IS , Light Blue Cables (IEC-60332) | [12 empty] | Flame Redandant , IS , Light Blue Cables
1 | BL-1P-2-A | 1 PAIR * 1.5 mm² , ( CU/XLPE/DW/OSC/PVC/SWA/PVC ) | [8 empty] | 4090 | 4908 | 1 | BL-1P-2-A | 1 PAIR * 1.5 mm² , ( CU/XLPE/DW/OSC/PVC/SWA/PVC ) | 2920 |  |  |  | 1170
2 | BL-12P-1-LA | 12 PAIR * 1 mm² , ( CU/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 4980 | 5976 | 2 | BL-12P-1-LA | 12 PAIR * 1 mm² , ( CU/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) | 2440 |  |  |  | 2120 | 420
3 | BL-7T-1-LA | 7 Traid * 1 mm² , ( CU/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 1060 | 1272 | 3 | BL-7T-1-LA | 7 Traid * 1 mm² , ( CU/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) |  |  |  |  | 1060
4 | BL-19P-1-LA | 19 PAIR * 1 mm² , ( CU/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 5340 | 6408 | 4 | BL-19P-1-LA | 19 PAIR * 1 mm² , ( CU/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) | 1550 |  |  | 2310 | 1060 | 420
Flame Redandant , NIS , Gray Cables , (IEC-60332) | [12 empty] | Flame Redandant , IS , Gray Cables
5 | GY-1P-2-A | 1 PAIR * 1.5 mm² , ( CU/XLPE/DW/OSC/PVC/SWA/PVC ) | [8 empty] | 2270 | 2724 | 5 | GY-1P-2-A | 1 PAIR * 1.5 mm² , ( CU/XLPE/DW/OSC/PVC/SWA/PVC ) | 2270
6 | GY-1P-3-A | 1 PAIR * 2.5 mm² , ( CU/XLPE/DW/OSC/PVC/SWA/PVC ) | [8 empty] | 1180 | 1416 | 6 | GY-1P-3-A | 1 PAIR * 2.5 mm² , ( CU/XLPE/DW/OSC/PVC/SWA/PVC ) | 1180
7 | GY-7P-1-LA | 7 PAIR *1 mm² , ( CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 1590 | 1908 | 7 | GY-7P-1-LA | 7 PAIR *1 mm² , ( CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC ) | 530 |  |  |  | 1060
8 | GY-19P-1-LA | 19 PAIR * 1 mm² , ( CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC) | [8 empty] | 8620 | 10344 | 8 | GY-19P-1-LA | 19 PAIR * 1 mm² , ( CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC) | 2330 |  |  | 990 | 5300
9 | GY-19P-1-A | 19 PAIR * 1 mm² ,( CU/XLPE/DW/OSC/PVC/SWA/PVC ) | [8 empty] | 4200 | 5040 | 9 | GY-19P-1-A | 19 PAIR * 1 mm² ,( CU/XLPE/DW/OSC/PVC/SWA/PVC ) | 1120 |  |  | 420 | 2100 | 560
10 | GY-12P-1 | 12 PAIR * 1 mm² , ( CU/XLPE/DW/OSC//PVC ) | [8 empty] | 300 | 360 | 10 | GY-12P-1 | 12 PAIR * 1 mm² ,( CU/XLPE/DW/OSC//PVC ) | 300
11 | GY-12P-3-LA | 12 PAIR * 2.5 mm² , ( CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 2090 | 2508 | 11 | GY-12P-3-LA | 12 PAIR * 2.5 mm² ,( CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC ) | 1430 |  |  | 660
Fire resistant , IS , Light Blue with Red Strip Cables , (IEC-60331) | [12 empty] | Fire resistant , IS , Light Blue with Red Strip Cables
12 | BR-1P-2-FA | 1 PAIR * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC ) | [8 empty] | 1770 | 2124 | 12 | BR-1P-2-FA | 1 PAIR * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC ) |  | 1770
13 | BR-12P-1-LFA | 12 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 1610 | 1932 | 13 | BR-12P-1-LFA | 12 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) |  | 1190 |  |  |  | 420
14 | BR-19P-1-LFA | 19 PAIR * 1 mm² , (CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 2770 | 3324 | 14 | BR-19P-1-LFA | 19 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC ) |  | 1290 |  |  | 1060 | 420
Fire resistant , NIS , Gray with Red Strip Cables , (IEC-60331) | [12 empty] | Fire resistant , NIS , Gray with Red Strip Cables
15 | GR-1P-2-FA | 1 PAIR * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC ) | [8 empty] | 1160 | 1392 | 15 | GR-1P-2-FA | 1 PAIR * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC ) |  | 980 |  |  | 180
16 | GR-1P-3-FA | 1 PAIR * 2.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC ) | [8 empty] | 2420 | 2904 | 16 | GR-1P-3-FA | 1 PAIR * 2.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC ) |  | 1270 |  |  | 1150
17 | GR-19P-1-FA | 19 PAIR * 1 mm² , (CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC) | [8 empty] | 980 | 1176 | 17 | GR-19P-1-FA | 19 PAIR * 1 mm² , (CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC) |  | 420 |  |  | 420 | 140
18 | GR-7P-1-F | 7 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC ) | [8 empty] | 350 | 420 | 18 | GR-7P-1-F | 7 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC ) |  | 350
19 | GR-7P-1-LFA | 7 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 3230 | 3876 | 19 | GR-7P-1-LFA | 7 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC ) |  | 1110 |  |  | 2120
20 | GR-12P-1-LFA | 12 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC) | [8 empty] | 2100 | 2520 | 20 | GR-12P-1-LFA | 12 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC) | [5 empty] | 2100
21 | GR-12P-3-LFA | 12 PAIR * 2.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC ) | [8 empty] | 3170 | 3804 | 21 | GR-12P-3-LFA | 12 PAIR * 2.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC ) |  | 1690 |  |  | 1060 | 420
22 | GR-12P-1-F | 12 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC ) | [8 empty] | 300 | 360 | 22 | GR-12P-1-F | 12 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC ) |  | 300
Fire resistant , NIS , Red Cables ( F&G ) , (IEC-60331) | [12 empty] | Fire resistant , NIS , Red Cables ( F&G )
23 | RD-1P-2-F | 1 PAIR * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC) | [8 empty] | 815 | 978 | 23 | RD-1P-2-F | 1 PAIR * 1.5 mm² ,( CU/Mica-tape/XLPE/DW/OSC/PVC) |  |  | 815
24 | RD-1P-2-FA | 1 PAIR * 1.5 mm² ,( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, ) | [8 empty] | 2380 | 2856 | 24 | RD-1P-2-FA | 1 PAIR * 1.5 mm² ,( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, ) |  |  | 2380
25 | RD-7P-3-LFA | 7 PAIR * 2.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC, ) | [8 empty] | 3560 | 4272 | 25 | RD-7P-3-LFA | 7 PAIR * 2.5 mm² ,( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC, ) |  |  | 3560
26 | RD-7P-1-FA | 7 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC) | [8 empty] | 660 | 792 | 26 | RD-7P-1-FA | 7 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC) |  |  | 660
27 | RD-7P-1-LFA | 7 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC) | [8 empty] | 2790 | 3348 | 27 | RD-7P-1-LFA | 7 PAIR * 1 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC) |  |  | 2790
28 | RD-19P-1-F | 19 PAIR * 1 mm² ,( CU/Mica-tape/XLPE/DW/OSC/PVC) | [8 empty] | 250 | 300 | 28 | RD-19P-1-F | 19 PAIR * 1 mm² ,( CU/Mica-tape/XLPE/DW/OSC/PVC) |  |  | 250
29 | RD-1T-2-F | 1 Traid * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC) | [8 empty] | 350 | 420 | 29 | RD-1T-2-F | 1 Traid * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC) |  |  | 350
30 | RD-1T-2-FA | 1 Traid * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, ) | [8 empty] | 2490 | 2988 | 30 | RD-1T-2-FA | 1 Traid * 1.5 mm² , ( CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, ) |  |  | 2490
31 | RD-7T-1-LFA | 7 Traid * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC, ) | [8 empty] | 1470 | 1764 | 31 | RD-7T-1-LFA | 7 Traid * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC, ) |  |  | 1470
32 | RD-12T-1-FA | 12 Traid * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWA/PVC,) | [8 empty] | 300 | 360 | 32 | RD-12T-1-FA | 12 Traid * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWA/PVC,) |  |  | 300
33 | RD-12T-1-LFA | 12 Traid * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC,) | [8 empty] | 2780 | 3336 | 33 | RD-12T-1-LFA | 12 Traid * 1 mm² , ( CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC,) |  |  | 2780
Flame Redandant , Black Cables (Power) | [12 empty] | Flame Redandant , Black Cables (Power)
34 | 12*3*1.5mm2 | CU,PVC,SC,OSC,SWA,PVC,Lead Sheath ,PVC | [8 empty] | 1060 | 1272 | 34 | 12*3*1.5mm2 | CU,PVC,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT Black |  |  |  |  | 1060
35 | 3x2.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,Lead Sheath ,PVC | [8 empty] | 5300 | 6360 | 35 | 3x2.5mm^2 | CU,PVC,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT Black |  |  |  |  | 5300
Modbus Cables | [12 empty] | Modbus Cables
36 | Modubus Cable | By vendor | [8 empty] | 500 | 600 | 36 | Modubus Cable | By vendor | 500

## Cable list (DCS)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 |  | IN |  | LI | 0009 |  | D04
INSTRUMENT CABLE LIST FOR DCS SYSTEM
ITEM | Cable Code | Tag No. | Description | Cable No. |  | From | To. | SYSTEM | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | Lead Cover | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | CABLE LENGTH (M) | GLAND SIZE | Remark
1 | BL-1P-2-A | FIT-2102 | Flow Transmitter | IC- | FIT-2102 | FIT-2102 | JBD-A-2101 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
2 | BL-1P-2-A | TIT-2104 | Temperature Transmitter | IC- | TIT-2104 | TIT-2104 | JBD-A-2101 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
3 | BL-1P-2-A | PIT-2104 | Pressure Transmitter | IC- | PIT-2104 | PIT-2104 | JBD-A-2101 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
4 | BL-1P-2-A | FCV-2102 | Flow Control Valve | IC- | FCV-2102 | FCV-2102 | JBD-A-2101 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
5 | BL-12P-1-LA | JBD-A-2101 | Junction Box | MC- | JBD-A-2101 | JBD-A-2101 | DCS | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 320 | M32
6 | BL-1P-2-A | FIT-2111 | Flow Indicator Transmitter | IC- | FIT-2111 | FIT-2111 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
7 | BL-1P-2-A | FCV-2111 | Flow Control Valve | IC- | FCV-2111 | FCV-2111 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
8 | BL-1P-2-A | PIT-2114 | Pressure Indicator Transmitter | IC- | PIT-2114 | PIT-2114 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
9 | BL-1P-2-A | TIT-2102 | Temperature Traansmitter | IC- | TIT-2102 | TIT-2102 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
10 | BL-1P-2-A | PIT-2102 | Pressure Transmitter | IC- | PIT-2102 | PIT-2102 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
11 | BL-1P-2-A | FIT-2101 | Flow Transmitter | IC- | FIT-2101 | FIT-2101 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
12 | BL-1P-2-A | FCV-2101 | Flow Control Valve | IC- | FCV-2101 | FCV-2101 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
13 | BL-1P-2-A | LIT-2271 | Level Indicator Transmitter | IC- | LIT-2271 | LIT-2271 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
14 | BL-1P-2-A | PIT-2271 | Pressure Indicator Transmitter | IC- | PIT-2271 | PIT-2271 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
15 | BL-1P-2-A | PDIT-2271 | Diff Pressure Indicator Transmitter | IC- | PDIT-2271 | PDIT-2271 | JBD-A-2102 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
16 | BL-19P-1-LA | JBD-A-2102 | Junction Box | MC- | JBD-A-2102 | JBD-A-2102 | DCS | DCS | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 260 | M50
17 | BL-1P-2-A | TIT-2112 | Temperature Indicator Transmitter | IC- | TIT-2112 | TIT-2112 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
18 | BL-1P-2-A | PIT-2117 | Pressure Indicator Transmitter | IC- | PIT-2117 | PIT-2117 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
19 | BL-1P-2-A | PDIT-2112 | Diff. Pressure Indicator Transmitter | IC- | PDIT-2112 | PDIT-2112 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
20 | BL-1P-2-A | LIT-2119 | Level Indicator Transmitter | IC- | LIT-2119 | LIT-2119 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
21 | BL-1P-2-A | LCV-2114 | Level Control Valve | IC- | LCV-2114 | LCV-2114 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
22 | BL-1P-2-A | TIT-2271 | Temperature Indicator Transmitter | IC- | TIT-2271 | TIT-2271 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
23 | BL-1P-2-A | FIT-2271 | Flow Indicator Transmitter | IC- | FIT-2271 | FIT-2271 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
24 | BL-1P-2-A | PCV-2272 | Pressure Control Valve | IC- | PCV-2272 | PCV-2272 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
25 | BL-1P-2-A | PIT-2272 | Pressure Indicator Transmitter | IC- | PIT-2272 | PIT-2272 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
26 | BL-1P-2-A | PIT-2112 | Pressure Indicator Transmitter | IC- | PIT-2112 | PIT-2112 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
27 | BL-1P-2-A | PDIT-2111 | Diff. Pressure Indicator Transmitter | IC- | PDIT-2111 | PDIT-2111 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
28 | BL-1P-2-A | LIT-2111 | Level Indicator Transmitter | IC- | LIT-2111 | LIT-2111 | JBD-A-2103 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
29 | BL-19P-1-LA | JBD-A-2103 | Junction Box | MC- | JBD-A-2103 | JBD-A-2103 | DCS | DCS | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 260 | M50
30 | BL-1P-2-A | PIT-2121A | Pressure Indicator Transmitter | IC- | PIT-2121A | PIT-2121A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
31 | BL-1P-2-A | PDIT-2121A | Diff. Pressure Indicator Transmitter | IC- | PDIT-2121A | PDIT-2121A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
32 | BL-1P-2-A | LIT-2121A | Level Indicator Transmitter | IC- | LIT-2121A | LIT-2121A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
33 | BL-1P-2-A | TIT-2121A | Temperature Indicator Transmitter | IC- | TIT-2121A | TIT-2121A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
34 | BL-1P-2-A | PDIT-2131A | Diff. Pressure Indicator Transmitter | IC- | PDIT-2131A | PDIT-2131A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
35 | BL-1P-2-A | LIT-2131A | Level Indicator Transmitter | IC- | LIT-2131A | LIT-2131A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
36 | BL-1P-2-A | TIT-2131A | Temperature Indicator Transmitter | IC- | TIT-2131A | TIT-2131A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
37 | BL-1P-2-A | TIT-2126A | Temperature Indicator Transmitter | IC- | TIT-2126A | TIT-2126A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
38 | BL-1P-2-A | TIT-2135A | Temperature Indicator Transmitter | IC- | TIT-2135A | TIT-2135A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
39 | BL-1P-2-A | PIT-2135A | Pressure Indicator Transmitter | IC- | PIT-2135A | PIT-2135A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
40 | BL-1P-2-A | PCV-2135A | Pressure Control Valve | IC- | PCV-2135A | PCV-2135A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
41 | BL-1P-2-A | TY-2122A | Cooler Actuator Positioner | IC- | TY-2122A | TY-2122A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
42 | BL-1P-2-A | TY-2132A | Cooler Actuator Positioner | IC- | TY-2132A | TY-2132A | JBD-A-2104 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
43 | BL-19P-1-LA | JBD-A-2104 | Junction Box | MC- | JBD-A-2104 | JBD-A-2104 | DCS | DCS | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 320 | M50
44 | BL-1P-2-A | PIT-2121B | Pressure Indicator Transmitter | IC- | PIT-2121B | PIT-2121B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
45 | BL-1P-2-A | PDIT-2121B | Diff. Pressure Indicator Transmitter | IC- | PDIT-2121B | PDIT-2121B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
46 | BL-1P-2-A | LIT-2121B | Level Indicator Transmitter | IC- | LIT-2121B | LIT-2121B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
47 | BL-1P-2-A | TIT-2121B | Temperature Indicator Transmitter | IC- | TIT-2121B | TIT-2121B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
48 | BL-1P-2-A | PDIT-2131B | Diff. Pressure Indicator Transmitter | IC- | PDIT-2131B | PDIT-2131B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
49 | BL-1P-2-A | LIT-2131B | Level Indicator Transmitter | IC- | LIT-2131B | LIT-2131B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
50 | BL-1P-2-A | TIT-2131B | Temperature Indicator Transmitter | IC- | TIT-2131B | TIT-2131B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
51 | BL-1P-2-A | TIT-2126B | Temperature Indicator Transmitter | IC- | TIT-2126B | TIT-2126B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
52 | BL-1P-2-A | TIT-2135B | Temperature Indicator Transmitter | IC- | TIT-2135B | TIT-2135B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
53 | BL-1P-2-A | PIT-2135B | Pressure Indicator Transmitter | IC- | PIT-2135B | PIT-2135B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
54 | BL-1P-2-A | PCV-2135B | Pressure Control Valve | IC- | PCV-2135B | PCV-2135B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
55 | BL-1P-2-A | TY-2122B | Cooler Actuator Positioner | IC- | TY-2122B | TY-2122B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
56 | BL-1P-2-A | TY-2132B | Cooler Actuator Positioner | IC- | TY-2132B | TY-2132B | JBD-A-2105 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
57 | BL-19P-1-LA | JBD-A-2105 | Junction Box | MC- | JBD-A-2105 | JBD-A-2105 | DCS | DCS | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 340 | M50
58 | BL-1P-2-A | PIT-2121C | Pressure Indicator Transmitter | IC- | PIT-2121C | PIT-2121C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
59 | BL-1P-2-A | PDIT-2121C | Diff. Pressure Indicator Transmitter | IC- | PDIT-2121C | PDIT-2121C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
60 | BL-1P-2-A | LIT-2121C | Level Indicator Transmitter | IC- | LIT-2121C | LIT-2121C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
61 | BL-1P-2-A | TIT-2121C | Temperature Indicator Transmitter | IC- | TIT-2121C | TIT-2121C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
62 | BL-1P-2-A | PDIT-2131C | Diff. Pressure Indicator Transmitter | IC- | PDIT-2131C | PDIT-2131C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
63 | BL-1P-2-A | LIT-2131C | Level Indicator Transmitter | IC- | LIT-2131C | LIT-2131C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
64 | BL-1P-2-A | TIT-2131C | Temperature Indicator Transmitter | IC- | TIT-2131C | TIT-2131C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
65 | BL-1P-2-A | TIT-2126C | Temperature Indicator Transmitter | IC- | TIT-2126C | TIT-2126C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
66 | BL-1P-2-A | TIT-2135C | Temperature Indicator Transmitter | IC- | TIT-2135C | TIT-2135C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
67 | BL-1P-2-A | PIT-2135C | Pressure Indicator Transmitter | IC- | PIT-2135C | PIT-2135C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
68 | BL-1P-2-A | PCV-2135C | Pressure Control Valve | IC- | PCV-2135C | PCV-2135C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
69 | BL-1P-2-A | TY-2122C | Cooler Actuator Positioner | IC- | TY-2122C | TY-2122C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
70 | BL-1P-2-A | TY-2132C | Cooler Actuator Positioner | IC- | TY-2132C | TY-2132C | JBD-A-2106 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
71 | BL-19P-1-LA | JBD-A-2106 | Junction Box | MC- | JBD-A-2106 | JBD-A-2106 | DCS | DCS | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 370 | M50
72 | BL-1P-2-A | PDIT-2141 | Diff. Pressure Indicator Transmitter | IC- | PDIT-2141 | PDIT-2141 | JBD-A-2107 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
73 | BL-1P-2-A | LIT-2141 | Level Indicator Transmitter | IC- | LIT-2141 | LIT-2141 | JBD-A-2107 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
74 | BL-1P-2-A | PDIT-2143 | Diff. Pressure Indicator Transmitter | IC- | PDIT-2143 | PDIT-2143 | JBD-A-2107 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
75 | BL-1P-2-A | PIT-2151 | Pressure Indicator Transmitter | IC- | PIT-2151 | PIT-2151 | JBD-A-2107 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
76 | BL-1P-2-A | PCV-2151 | Pressure Control Vavle | IC- | PCV-2151 | PCV-2151 | JBD-A-2107 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
77 | BL-1P-2-A | PCV-2152 | Pressure Control Vavle | IC- | PCV-2152 | PCV-2152 | JBD-A-2107 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
78 | BL-1P-2-A | FIT-2151 | Flow Indicator Transmitter | IC- | FIT-2151 | FIT-2151 | JBD-A-2107 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
79 | BL-12P-1-LA | JBD-A-2107 | Junction Box | MC- | JBD-A-2107 | JBD-A-2107 | DCS | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 400 | M32
80 | BL-1P-2-A | LIT-2221 | Level Indicator Transmitter | IC- | LIT-2221 | LIT-2221 | JBD-A-2108 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
81 | BL-1P-2-A | LIT-2223 | Level Indicator Transmitter | IC- | LIT-2223A | LIT-2223A | JBD-A-2108 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
82 | BL-1P-2-A | LIT-2251 | Level Indicator Transmitter | IC- | LIT-2251 | LIT-2251 | JBD-A-2108 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
83 | BL-1P-2-A | LIT-2273 | Level Indicator Transmitter | IC- | LIT-2273 | LIT-2273 | JBD-A-2108 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
84 | BL-1P-2-A | LIT-2293 | Level Indicator Transmitter | IC- | LIT-2293 | LIT-2293 | JBD-A-2108 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
85 | BL-1P-2-A | PIT-2252 | Pressure Indicator Transmitter | IC- | PIT-2252 | PIT-2252 | JBD-A-2108 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
86 | BL-1P-2-A | PIT-2191 | Pressure Indicator Transmitter | IC- | PIT-2191 | PIT-2191 | JBD-A-2108 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
87 | BL-12P-1-LA | JBD-A-2108 | Junction Box | MC- | JBD-A-2108 | JBD-A-2108 | DCS | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 420 | M32
88 | BL-1P-2-A | PIT-2201 | Pressure Indicator Transmitter | IC- | PIT-2201 | PIT-2201 | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
89 | BL-1P-2-A | PCV-2201 | Pressure Control Valve | IC- | PCV-2201 | PCV-2201 | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
90 | BL-1P-2-A | PIT-2203A | Pressure Indicator Transmitter | IC- | PIT-2203A | PIT-2203A | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Rename
91 | BL-1P-2-A | PIT-2203B | Pressure Indicator Transmitter | IC- | PIT-2203B | PIT-2203B | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20 | Added
92 | BL-1P-2-A | PIT-2213 | Pressure Indicator Transmitter | IC- | PIT-2213 | PIT-2213 | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
93 | BL-1P-2-A | PCV-2211 | Pressure Control Valve | IC- | PCV-2211 | PCV-2211 | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
94 | BL-1P-2-A | FIT-2211 | Flow Indicator Transmitter | IC- | FIT-2211 | FIT-2211 | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
95 | BL-1P-2-A | TT-2211 | Temperature Transmitter | IC- | TT-2211 | TT-2211 | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
96 | BL-1P-2-A | PIT-2214 | Pressure Indicator Transmitter | IC- | PIT-2214 | PIT-2214 | JBD-A-2109 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
97 | BL-12P-1-LA | JBD-A-2109 | Junction Box | MC- | JBD-A-2109 | JBD-A-2109 | DCS | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 320 | M32
98 | BL-1P-2-A | LIT-2281 | Level Indicator Transmitter | IC- | LIT-2281A | LIT-2281A | JBD-A-2110 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
99 | - | LIT-2281B | Level Indicator Transmitter | IC- | LIT-2281B | LIT-2281B | JBD-A-2110 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | - | M20 | Deleted
100 | BL-1P-2-A | LIT-2301A | Level Indicator Transmitter | IC- | LIT-2301A | LIT-2301A | JBD-A-2110 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
101 | BL-1P-2-A | LIT-2301B | Level Indicator Transmitter | IC- | LIT-2301B | LIT-2301B | JBD-A-2110 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
102 | - | PIT-2301 | Pressure Indicator Transmitter | IC- | PIT-2301 | PIT-2301 | JBD-A-2110 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | - | M20 | Deleted
103 | BL-12P-1-LA | JBD-A-2110 | Junction Box | MC- | JBD-A-2110 | JBD-A-2110 | DCS | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 210 | M32
104 | BL-1P-2-A | PIT-2161 | Pressure Indicator Transmitter | IC- | PIT-2161 | PIT-2161 | JBD-A-2111 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
105 | BL-1P-2-A | LIT-2162 | Level Indicator Transmitter | IC- | LIT-2162 | LIT-2162 | JBD-A-2111 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
106 | BL-12P-1-LA | JBD-A-2111 | Junction Box | MC- | JBD-A-2111 | JBD-A-2111 | DCS | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 450 | M32
108 | GY-1P-2-A | EZSC-2102 | Limit Switch Close | IC- | EZSC-2102 | EZSC-2102 | JBD-D-2101 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 60 | M20
109 | GY-1P-2-A | EZSO-2102 | Limit Switch Open | IC- | EZSO-2102 | EZSO-2102 | JBD-D-2101 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 60 | M20
110 | GY-7P-1-LA | JBD-D-2101 | Junction Box | MC- | JBD-D-2101 | JBD-D-2101 | DCS | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 320 | M40
111 | GY-1P-2-A | EZSC-2101 | Limit Switch Close | IC- | EZSC-2101 | EZSC-2101 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
112 | GY-1P-2-A | EZSO-2101 | Limit Switch Open | IC- | EZSO-2101 | EZSO-2101 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
113 | GY-1P-2-A | EZSC-2112 | Limit Switch Close | IC- | EZSC-2112 | EZSC-2112 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
114 | GY-1P-2-A | EZSO-2112 | Limit Switch Open | IC- | EZSO-2112 | EZSO-2112 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
115 | GY-1P-2-A | EZSO-2113 | Limit Switch Open | IC- | EZSO-2113 | EZSO-2113 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
116 | GY-1P-2-A | EZSC-2113 | Limit Switch Close | IC- | EZSC-2113 | EZSC-2113 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
117 | GY-1P-2-A | XZSC-2271 | Limit Switch Close | IC- | XZSC-2271 | XZSC-2271 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
118 | GY-1P-2-A | XZSO-2271 | Limit Switch Open | IC- | XZSO-2271 | XZSO-2271 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
119 | GY-1P-2-A | EZSC-2272 | Limit Switch Close | IC- | EZSC-2272 | EZSC-2272 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
120 | GY-1P-2-A | EZSO-2272 | Limit Switch Open | IC- | EZSO-2272 | EZSO-2272 | JBD-D-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
121 | GY-19P-1-LA | JBD-D-2102 | Junction Box | MC- | JBD-D-2102 | JBD-D-2102 | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 260 | M50
122 | GY-1P-2-A | XZSC-2121A | Limit Switch Close | IC- | XZSC-2121A | XZSC-2121A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
123 | GY-1P-2-A | XZSO-2121A | Limit Switch Open | IC- | XZSO-2121A | XZSO-2121A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
124 | GY-1P-2-A | XZSC-2122A | Limit Switch Close | IC- | XZSC-2122A | XZSC-2122A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
125 | GY-1P-2-A | XZSO-2122A | Limit Switch Open | IC- | XZSO-2122A | XZSO-2122A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
126 | GY-1P-2-A | XZSC-2131A | Limit Switch Close | IC- | XZSC-2131A | XZSC-2131A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
127 | GY-1P-2-A | XZSO-2131A | Limit Switch Open | IC- | XZSO-2131A | XZSO-2131A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
128 | GY-1P-2-A | BZSC-2132A | Limit Switch Close | IC- | BZSC-2132A | BZSC-2132A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
129 | GY-1P-2-A | BZSO-2132A | Limit Switch Open | IC- | BZSO-2132A | BZSO-2132A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
130 | GY-1P-2-A | XZSC-2133A | Limit Switch Close | IC- | XZSC-2133A | XZSC-2133A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
131 | GY-1P-2-A | XZSO-2133A | Limit Switch Open | IC- | XZSO-2133A | XZSO-2133A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
132 | GY-1P-2-A | BZSC-2134A | Limit Switch Close | IC- | BZSC-2134A | BZSC-2134A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
133 | GY-1P-2-A | BZSO-2134A | Limit Switch Open | IC- | BZSO-2134A | BZSO-2134A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
134 | GY-1P-2-A | BZSC-2110 | Limit Switch Open | IC- | BZSC-2110 | BZSC-2110 | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
135 | GY-1P-2-A | BZSO-2110 | Limit Switch Close | IC- | BZSO-2110 | BZSO-2110 | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
136 | - | BZSC-2122A | Limit Switch Close | IC- | BZSC-2122A | BZSC-2122A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | Deleted
137 | - | BZSO-2122A | Limit Switch Open | IC- | BZSO-2122A | BZSO-2122A | JBD-D-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | Deleted
138 | GY-19P-1-LA | JBD-D-2103 | Junction Box | MC- | JBD-D-2103 | JBD-D-2103 | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 320 | M50
139 | GY-1P-2-A | XZSC-2121B | Limit Switch Close | IC- | XZSC-2121B | XZSC-2121B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
140 | GY-1P-2-A | XZSO-2121B | Limit Switch Open | IC- | XZSO-2121B | XZSO-2121B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
141 | GY-1P-2-A | XZSC-2122B | Limit Switch Close | IC- | XZSC-2122B | XZSC-2122B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
142 | GY-1P-2-A | XZSO-2122B | Limit Switch Open | IC- | XZSO-2122B | XZSO-2122B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
143 | GY-1P-2-A | XZSC-2131B | Limit Switch Close | IC- | XZSC-2131B | XZSC-2131B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
144 | GY-1P-2-A | XZSO-2131B | Limit Switch Open | IC- | XZSO-2131B | XZSO-2131B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
145 | GY-1P-2-A | BZSC-2132B | Limit Switch Close | IC- | BZSC-2132B | BZSC-2132B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
146 | GY-1P-2-A | BZSO-2132B | Limit Switch Open | IC- | BZSO-2132B | BZSO-2132B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
147 | GY-1P-2-A | XZSC-2133B | Limit Switch Close | IC- | XZSC-2133B | XZSC-2133B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
148 | GY-1P-2-A | XZSO-2133B | Limit Switch Open | IC- | XZSO-2133B | XZSO-2133B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
149 | GY-1P-2-A | BZSC-2134B | Limit Switch Close | IC- | BZSC-2134B | BZSC-2134B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
150 | GY-1P-2-A | BZSO-2134B | Limit Switch Open | IC- | BZSO-2134B | BZSO-2134B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
151 | - | BZSC-2122B | Limit Switch Close | IC- | BZSC-2122B | BZSC-2122B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | Deleted
152 | - | BZSO-2122B | Limit Switch Open | IC- | BZSO-2122B | BZSO-2122B | JBD-D-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | Deleted
153 | GY-19P-1-LA | JBD-D-2104 | Junction Box | MC- | JBD-D-2104 | JBD-D-2104 | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 340 | M50
154 | GY-1P-2-A | XZSC-2121C | Limit Switch Close | IC- | XZSC-2121C | XZSC-2121C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
155 | GY-1P-2-A | XZSO-2121C | Limit Switch Open | IC- | XZSO-2121C | XZSO-2121C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
156 | GY-1P-2-A | XZSC-2122C | Limit Switch Close | IC- | XZSC-2122C | XZSC-2122C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
157 | GY-1P-2-A | XZSO-2122C | Limit Switch Open | IC- | XZSO-2122C | XZSO-2122C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
158 | GY-1P-2-A | XZSC-2131C | Limit Switch Close | IC- | XZSC-2131C | XZSC-2131C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
159 | GY-1P-2-A | XZSO-2131C | Limit Switch Open | IC- | XZSO-2131C | XZSO-2131C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
160 | GY-1P-2-A | BZSC-2132C | Limit Switch Close | IC- | BZSC-2132C | BZSC-2132C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
161 | GY-1P-2-A | BZSO-2132C | Limit Switch Open | IC- | BZSO-2132C | BZSO-2132C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
162 | GY-1P-2-A | XZSC-2133C | Limit Switch Close | IC- | XZSC-2133C | XZSC-2133C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
163 | GY-1P-2-A | XZSO-2133C | Limit Switch Open | IC- | XZSO-2133C | XZSO-2133C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
164 | GY-1P-2-A | BZSC-2134C | Limit Switch Close | IC- | BZSC-2134C | BZSC-2134C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
165 | GY-1P-2-A | BZSO-2134C | Limit Switch Open | IC- | BZSO-2134C | BZSO-2134C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
166 | - | BZSC-2122C | Limit Switch Close | IC- | BZSC-2122C | BZSC-2122C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | Deleted
167 | - | BZSO-2122C | Limit Switch Open | IC- | BZSO-2122C | BZSO-2122C | JBD-D-2105 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | Deleted
168 | GY-19P-1-LA | JBD-D-2105 | Junction Box | MC- | JBD-D-2105 | JBD-D-2105 | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 370 | M50
169 | GY-1P-2-A | XZSC-2142 | Limit Switch Close | IC- | XZSC-2142 | XZSC-2142 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
170 | GY-1P-2-A | XZSO-2142 | Limit Switch Open | IC- | XZSO-2142 | XZSO-2142 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
171 | GY-1P-2-A | XZSC-2143 | Limit Switch Close | IC- | XZSC-2143 | XZSC-2143 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
172 | GY-1P-2-A | XZSO-2143 | Limit Switch Open | IC- | XZSO-2143 | XZSO-2143 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
173 | GY-1P-2-A | XZSC-2144 | Limit Switch Close | IC- | XZSC-2141 | XZSC-2141 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
174 | GY-1P-2-A | XZSO-2144 | Limit Switch Open | IC- | XZSO-2141 | XZSO-2141 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
175 | GY-1P-2-A | BZSC-2141 | Limit Switch Close | IC- | BZSC-2141 | BZSC-2141 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
176 | GY-1P-2-A | BZSO-2141 | Limit Switch Open | IC- | BZSO-2141 | BZSO-2141 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
177 | GY-1P-2-A | BZSC-2151 | Limit Switch Close | IC- | BZSC-2151 | BZSC-2151 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
178 | GY-1P-2-A | BZSO-2151 | Limit Switch Open | IC- | BZSO-2151 | BZSO-2151 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
179 | GY-1P-2-A | EZSC-3201 | Limit Switch Close | IC- | EZSC-3201 | EZSC-3201 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 100 | M20
180 | GY-1P-2-A | EZSO-3201 | Limit Switch Open | IC- | EZSO-3201 | EZSO-3201 | JBD-D-2106 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 100 | M20
181 | GY-19P-1-LA | JBD-D-2106 | Junction Box | MC- | JBD-D-2106 | JBD-D-2106 | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 400 | M50
182 | GY-1P-2-A | ZSC-2301 | Solenoid Valve | IC- | ZSC-2301 | ZSC-2301 | JBD-D-2108 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
183 | GY-1P-2-A | ZSO-2301 | Solenoid Valve | IC- | ZSO-2301 | ZSO-2301 | JBD-D-2108 | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
184 | GY-7P-1-LA | JBD-D-2107 | Junction Box | MC- | JBD-D-2107 | JBD-D-2107 | DCS | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 600/1000 V | 210 | M32
186 | GY-1P-3-A | PSOV-2121A | Solenoid Valve | IC- | PSOV-2121A | PSOV-2121A | JBD-S-2101 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
187 | GY-1P-3-A | PSOV-2122A | Solenoid Valve | IC- | PSOV-2122A | PSOV-2122A | JBD-S-2101 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
188 | GY-1P-3-A | PSOV-2131A | Solenoid Valve | IC- | PSOV-2131A | PSOV-2131A | JBD-S-2101 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
189 | GY-1P-3-A | PSOV-2132A | Solenoid Valve | IC- | PSOV-2132A | PSOV-2132A | JBD-S-2101 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
190 | GY-1P-3-A | PSOV-2133A | Solenoid Valve | IC- | PSOV-2133A | PSOV-2133A | JBD-S-2101 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
191 | GY-1P-3-A | PSOV-2271 | Solenoid Valve | IC- | PSOV-2271 | PSOV-2271 | JBD-S-2101 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
192 | GY-12P-3-LA | JBD-S-2101 | Junction Box | MC- | JBD-S-2101 | JBD-S-2101 | DCS | DCS | FRT | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray | NOTE 3 | 600/1000 V | 320 | M40
193 | GY-1P-3-A | PSOV-2121B | Solenoid Valve | IC- | PSOV-2121B | PSOV-2121B | JBD-S-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
194 | GY-1P-3-A | PSOV-2122B | Solenoid Valve | IC- | PSOV-2122B | PSOV-2122B | JBD-S-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
195 | GY-1P-3-A | PSOV-2131B | Solenoid Valve | IC- | PSOV-2131B | PSOV-2131B | JBD-S-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
196 | GY-1P-3-A | PSOV-2132B | Solenoid Valve | IC- | PSOV-2132B | PSOV-2132B | JBD-S-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
197 | GY-1P-3-A | PSOV-2133B | Solenoid Valve | IC- | PSOV-2133B | PSOV-2133B | JBD-S-2102 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
198 | GY-12P-3-LA | JBD-S-2102 | Junction Box | MC- | JBD-S-2102 | JBD-S-2102 | DCS | DCS | FRT | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray | NOTE 3 | 600/1000 V | 340 | M32
199 | GY-1P-3-A | PSOV-2121C | Solenoid Valve | IC- | PSOV-2121C | PSOV-2121C | JBD-S-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
200 | GY-1P-3-A | PSOV-2122C | Solenoid Valve | IC- | PSOV-2122C | PSOV-2122C | JBD-S-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
201 | GY-1P-3-A | PSOV-2131C | Solenoid Valve | IC- | PSOV-2131C | PSOV-2131C | JBD-S-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
202 | GY-1P-3-A | PSOV-2132C | Solenoid Valve | IC- | PSOV-2132C | PSOV-2132C | JBD-S-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
203 | GY-1P-3-A | PSOV-2133C | Solenoid Valve | IC- | PSOV-2133C | PSOV-2133C | JBD-S-2103 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 60 | M20
204 | GY-12P-3-LA | JBD-S-2103 | Junction Box | MC- | JBD-S-2103 | JBD-S-2103 | DCS | DCS | FRT | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray | NOTE 3 | 600/1000 V | 370 | M32
205 | GY-1P-3-A | PSOV-2144 | Solenoid Valve | IC- | PSOV-2141 | PSOV-2141 | JBD-S-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
206 | GY-1P-3-A | PSOV-2142 | Solenoid Valve | IC- | PSOV-2142 | PSOV-2142 | JBD-S-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
207 | GY-1P-3-A | PSOV-2143 | Solenoid Valve | IC- | PSOV-2143 | PSOV-2143 | JBD-S-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 30 | M20
208 | GY-1P-3-A | PSOV-3201 | Solenoid Valve | IC- | PSOV-3201 | PSOV-3201 | JBD-S-2104 | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 100 | M20
209 | GY-12P-3-LA | JBD-S-2104 | Junction Box | MC- | JBD-S-2104 | JBD-S-2104 | DCS | DCS | FRT | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray | NOTE 3 | 600/1000 V | 400 | M32
107 | BL-1P-2-A | LIT-2291 | Level Indicator Transmitter | IC- | LIT-2291 | LIT-2291 | DCS | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 130 | M20 | Direct
185 | GY-1P-3-A | PSOV-2301 | Solenoid Valve | IC- | PSOV-2301 | PSOV-2301 | DCS | DCS | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 210 | M20 | Direct
210 | BL-12P-1-LA | TI-2261A | Temperature Indicator | MC- | LCP-IG-2201/1 | LCP-IG-2201 | DCS | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 320 | M32
211 |  | TI-2261B | Temperature Indicator |  | Ignition Control Panel | [14 empty] | - | M20
212 |  | TI-2261C | Temperature Indicator | [16 empty] | - | M20
213 | GY-19P-1-LA | XR-2261 | LPG Bottle Inservuce | MC- | LCP-IG-2201/2 | LCP-IG-2201 | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 320 | M40
214 |  | XR-2261A | Pilot 1 Status |  | Ignition Control Panel
215 |  | XR-2261B | Pilot 2 Status
216 |  | XR-2261C | Pilot 3 Status
217 |  | XA-2261 | Common Fault Alarm
218 |  | XF-2261 | Auto Ignition Failure
219 |  | XA-2262 | Burn Back Alarm
220 | GY-19P-1-LA | XSP-2231 | STOP Command | MC- | LCP-PK-2207 | LCP-PK-2207 | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 320 | M50
221 |  | LSLL-2231 | Level Low Low Alarm |  | CORROSION INHIBITOR PACKAGE
222 |  | XR-2231A | Running Status
223 |  | XR-2231B | Running Status
224 |  | XR-2231C | Running Status
225 |  | XR-2231D | Running Status
226 |  | XR-2231F | Running Status
227 |  | XF-2231A | FAULT STATUS
228 |  | XF-2231B | FAULT STATUS
229 |  | XF-2231C | FAULT STATUS
230 |  | XF-2231D | FAULT STATUS
231 |  | XF-2231F | FAULT STATUS
232 | - | [6 empty] | SIGNALS BETWEEN DCS AND UCP (A,B,C) SYSTEM & OTHER SYSTEMS | [11 empty] | -
233 | GY-12P-1 | XSP-2201A | STOP Command | MC- | DCS-PK-AC-2203A | DCS | PK-AC-2203A | DCS | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M40
234 |  | XSS-2201A | START Command
235 |  | PI-2203A | Pressure Indicator | [18 empty] | Added
236 | GY-12P-1 | XSP-2201B | STOP Command | MC- | DCS-PK-AC-2203B | DCS | PK-AC-2203B | DCS | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M40
237 |  | XSS-2201B | START Command
238 |  | PI-2203B | Pressure Indicator | [18 empty] | Added
239 | GY-12P-1 | XSP-2211 | STOP Command | MC- | DCS-PK-G-2204 | DCS | DCS-NIT. PK | DCS | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M40
240 |  | XSS-2211 | START Command
241 | GY-1P-2-A | PI-2121A | SPILL BACK | IC- | PI-2121A | DCS | UCP-GC-2101A | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 50 | M20 | Direct
242 | GY-12P-1 | XSS-2123A | Start Permission | MC- | DCS-UCP-GC-2101A | DCS | UCP-GC-2101A | DCS | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M40
243 |  | XSS-2126A | Request Start Permission from C-2101A | [18 empty] | Added
244 |  | XR-2124A | Running/Stop Status | [18 empty] | Added
245 |  | XS-2100A | Time Syncron Signal for C-2101A | [18 empty] | Added
246 |  | XSS-2124A | Start Permission | [18 empty] | Deleted
247 |  | XSP-2123A | STOP Command | [18 empty] | Deleted
248 | GY-1P-2-A | PI-2121B | SPILL BACK | IC- | PI-2121B | DCS | UCP-GC-2101B | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 50 | M20 | Direct
249 | GY-12P-1 | XSS-2123B | Start Permission | MC- | DCS-UCP-GC-2101B | DCS | UCP-GC-2101B | DCS | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M40
250 |  | XSS-2126B | Request Start Permission from C-2101B | [18 empty] | Added
251 |  | XR-2124B | Running/Stop Status | [18 empty] | Added
252 |  | XS-2100B | Time Syncron Signal for C-2101B | [18 empty] | Added
253 |  | XSS-2124B | Start Permission | [18 empty] | Deleted
254 |  | XSP-2123B | STOP Command | [18 empty] | Deleted
255 | GY-1P-2-A | PI-2121C | SPILL BACK | IC- | PI-2121C | DCS | UCP-GC-2101C | DCS | FRT | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | 50 | M20 | Direct
256 | GY-12P-1 | XSS-2123C | Start Permission | MC- | DCS-UCP-GC-2101C | DCS | UCP-GC-2101C | DCS | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M40
257 |  | XSS-2126C | Request Start Permission from C-2101C | [18 empty] | Added
258 |  | XR-2124C | Running/Stop Status | [18 empty] | Added
259 |  | XS-2100C | Time Syncron Signal for C-2101C | [18 empty] | Added
260 |  | XSS-2124C | Start Permission | [18 empty] | Deleted
261 |  | XSP-2123C | STOP Command | [18 empty] | Deleted
262 | GR-7P-1-F | ESDR 1-PCS | PCS FAILURE | IC- | DCS-ESD | DCS | ESD | DCS | FRT | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M32 |  | طول این کابل در بخش ESD دیده شده است
263 | - | ESDR 0-UPS | UPS FAILURE | [18 empty] | Deleted
264 | - | ESDR 1-FLR | FLARE IGNITION FAILURE | [18 empty] | Deleted
265 | - | CI-UPS1 | CURRENT MEASURMENT UPS1 | MC- | DCS-UPS1 | DCS | UPS1 | DCS | FRT | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M32 | Deleted
266 |  | VI-UPS1 | VOLTAGE MEASURMENT UPS1 | [18 empty] | Deleted
267 |  | XF-UPS1 | UPS1 FAILURE | [18 empty] | Deleted
268 | - | CI-UPS2 | CURRENT MEASURMENT UPS2 | MC- | DCS-UPS2 | DCS | UPS2 | DCS | FRT | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M32 | Deleted
269 |  | VI-UPS2 | VOLTAGE MEASURMENT UPS2 | [18 empty] | Deleted
270 |  | XF-UPS2 | UPS2 FAILURE | [18 empty] | Deleted
271 |  | XD-UPS | DUTY STANDBY STATUS in UPS | [18 empty] | Deleted
272 | - | [7 empty] | SIGNALS BETWEEN DCS AND MCC | [10 empty] | -
273 | GY-19P-1-A | XL-2111A | Local Remote Status | MC- | IRP-DCS 1 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
274 |  | XR-2111A | Running Status
275 |  | XF-2111A | Fault Status
276 |  | XL-2111B | Local Remote Status
277 |  | XR-2111B | Running Status
278 |  | XF-2111B | Fault Status
279 |  | XF-2121A | Fault Status
280 |  | XR-2121A | Running Status
281 |  | XL-2121A | Local / Remote Status
282 |  | XF-2122A | Fault Status
283 |  | XR-2122A | Running Status
284 |  | XL-2122A | Local / Remote Status
285 |  | XF-2121B | Fault Status
286 |  | XR-2121B | Running Status
287 |  | XL-2121B | Local / Remote Status
288 | GY-19P-1-A | XF-2122B | Fault Status | MC- | IRP-DCS 2 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
289 |  | XR-2122B | Running Status
290 |  | XL-2122B | Local / Remote Status
291 |  | XF-2121C | Fault Status
292 |  | XR-2121C | Running Status
293 |  | XL-2121C | Local / Remote Status
294 |  | XF-2122C | Fault Status
295 |  | XR-2122C | Running Status
296 |  | XL-2122C | Local / Remote Status
297 |  | XF-2131A | Fault Status
298 |  | XR-2131A | Running Status
299 |  | XL-2131A | Local / Remote Status
300 |  | XF-2132A | Fault Status
301 |  | XR-2132A | Running Status
302 |  | XL-2132A | Local / Remote Status
303 | GY-19P-1-A | XF-2131B | Fault Status | MC- | IRP-DCS 3 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
304 |  | XR-2131B | Running Status
305 |  | XL-2131B | Local / Remote Status
306 |  | XF-2132B | Fault Status
307 |  | XR-2132B | Running Status
308 |  | XL-2132B | Local / Remote Status
309 |  | XF-2131C | Fault Status
310 |  | XR-2131C | Running Status
311 |  | XL-2131C | Local / Remote Status
312 |  | XF-2132C | Fault Status
313 |  | XR-2132C | Running Status
314 |  | XL-2132C | Local / Remote Status
315 |  | XF-2161A | Fault Status
316 |  | XR-2161A | Running Status
317 |  | XL-2161A | Local / Remote Status
318 | GY-19P-1-A | XF-2161B | Fault Status | MC- | IRP-DCS 4 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
319 |  | XR-2161B | Running Status
320 |  | XL-2161B | Local / Remote Status
321 |  | XF-2221A | Fault Status
322 |  | XR-2221A | Running Status
323 |  | XL-2221A | Local / Remote Status
324 |  | XF-2221B | Fault Status
325 |  | XR-2221B | Running Status
326 |  | XL-2221B | Local / Remote Status
327 |  | XF-2222A | Fault Status
328 |  | XR-2222A | Running Status
329 |  | XL-2222A | Local / Remote Status
330 |  | XF-2222B | Fault Status
331 |  | XR-2222B | Running Status
332 |  | XL-2222B | Local / Remote Status
333 | GY-19P-1-A | XF-2251A | Fault Status | MC- | IRP-DCS 5 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
334 |  | XR-2251A | Running Status
335 |  | XL-2251A | Local / Remote Status
336 |  | XF-2251B | Fault Status
337 |  | XR-2251B | Running Status
338 |  | XL-2251B | Local / Remote Status
339 |  | XF-2281 | Fault Status
340 |  | XR-2281 | Running Status
341 |  | XF-2281A | Fault Status
342 |  | XR-2281A | Running Status
343 |  | XF-2291 | Fault Status
344 |  | XR-2291 | Running Status
345 |  | XL-2291 | Local / Remote Status
346 |  | XF-2293 | Fault Status
347 |  | XR-2293 | Running Status
348 | GY-19P-1-A | XL-2293 | Local / Remote Status | MC- | IRP-DCS 6 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
349 |  | XSP-2111A | STOP Command
350 |  | XSP-2111B | STOP Command
351 |  | XSP-2121A | STOP Command
352 |  | XSS-2121A | START Command
353 |  | XSP-2122A | STOP Command
354 |  | XSS-2122A | START Command
355 |  | XSP-2121B | STOP Command
356 |  | XSS-2121B | START Command
357 |  | XSP-2122B | STOP Command
358 |  | XSS-2122B | START Command
359 |  | XSP-2121C | STOP Command
360 |  | XSS-2121C | START Command
361 |  | XSP-2122C | STOP Command
362 |  | XSS-2122C | START Command
363 | GY-19P-1-A | XSP-2131A | STOP Command | MC- | IRP-DCS 7 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
364 |  | XSS-2131A | START Command
365 |  | XSP-2132A | STOP Command
366 |  | XSS-2132A | START Command
367 |  | XSP-2131B | STOP Command
368 |  | XSS-2131B | START Command
369 |  | XSP-2132B | STOP Command
370 |  | XSS-2132B | START Command
371 |  | XSP-2131C | STOP Command
372 |  | XSS-2131C | START Command
373 |  | XSP-2132C | STOP Command
374 |  | XSS-2132C | START Command
375 |  | XSP-2161A | STOP Command
376 |  | XSS-2161A | START Command | [18 empty] | Deleted
377 |  | XSP-2161B | STOP Command
378 |  | XSS-2161B | START Command | [18 empty] | Deleted
379 | GY-19P-1-A | XSP-2221A | STOP Command | MC- | IRP-DCS 8 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
380 |  | XSS-2221A | Start Command | [18 empty] | Added
381 |  | XSP-2221B | STOP Command
382 |  | XSS-2221B | Start Command | [18 empty] | Added
383 |  | XSP-2222A | STOP Command
384 |  | XSS-2222A | Start Command | [18 empty] | Added
385 |  | XSP-2222B | STOP Command
386 |  | XSS-2222B | Start Command | [18 empty] | Added
387 |  | XSP-2251A | STOP Command
388 |  | XSS-2251A | Start Command | [18 empty] | Added
389 |  | XSP-2251B | STOP Command
390 |  | XSS-2251B | Start Command | [18 empty] | Added
391 |  | XSP-2291 | STOP Command
392 |  | XSP-2281A | STOP Command | [18 empty] | Added
393 |  | XSP-2281B | STOP Command | [18 empty] | Deleted
394 |  | XSP-2293 | STOP Command
395 | GY-19P-1-A | XOC-LV-Q0A | Open/Close Status (SWGR-Incoming A-Q0A) | MC- | IRP-DCS 9 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
396 |  | XF-LV-Q0A | Fault Status (SWGR-Incoming A-Q0A)
397 |  | XF-TR-001 | Fault Status (Transformer-001)
398 |  | XOC-LV-Q0B | Open/Close Status (SWGR-Incoming B-Q0B)
399 |  | XF-LV-Q0B | Fault Status(SWGR-Incoming B-Q0B)
400 |  | XF-TR-002 | Fault Status (Transformer-002)
401 |  | XOC-LV-Q0C | Open/Close Status (SWGR-Bus Tie C-Q0C)
402 |  | XF-LV-Q0C | Fault Status (SWGR-Bus Tie C-Q0C)
403 |  | XOC-LV-Q0E | Open/Close Status (SWGR-DG C.B-Q0E)
404 |  | XF-LV-Q0E | Fault Status (SWGR-DG C.B-Q0E)
405 |  | XOC-LV-Q0D | Open/Close Status (SWGR-DG Bus Tie-Q0D)
406 |  | XF-LV-Q0D | Fault Status (SWGR-DG Bus Tie-Q0D)
407 |  | XOC-MV-001A-Q2 | Open/Close Status (SWGR-Transformer feeder-Q2)
408 |  | XF-MV-001A-Q2 | Fault Status(SWGR-Transformer feeder-Q2)
409 | GY-19P-1-A | XOC-MV-001A-Q5 | Open/Close Status (SWGR-Spare -Q5) | MC- | IRP-DCS 10 | IRP | DCS | DCS | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
410 |  | XF-MV-001A-Q5 | Fault Status (SWGR-Spare -Q5)
411 |  | XOC-MV-001B-Q2 | Open/Close Status (SWGR-Transformer feeder-Q2)
412 |  | XF-MV-001B-Q2 | Fault Status (SWGR-Transformer feeder-Q2)
413 |  | XOC-MV-001B-Q4 | Open/Close Status (SWGR-Transformer feeder-Q4)
414 |  | XF-MV-001B-Q4 | Fault Status (SWGR-Transformer feeder-Q4)
415 |  | XOC-MV-001B-Q5 | Open/Close Status (SWGR-Spare -Q5)
416 |  | XF-MV-001B-Q5 | Fault Status (SWGR-Spare -Q5)
417 |  | XOC-MV-001C-Q3 | Open/Close Status (SWGR-Fire Pump -Q3)
418 |  | XF-MV-001C-Q3 | Fault Status (SWGR-Fire Pump -Q3)
419 |  | XL-ATS | Auto/Manual Status
420 |  | XM-LV-IN1 | Multifunction Meter | [18 empty] | Deleted
421 |  | XM-LV-IN2 | Multifunction Meter | [18 empty] | Deleted
D04
TOTALLY REVIZED

## Cable list (ESD)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 |  | IN |  | LI | 0009 |  | D04
INSTRUMENT CABLE LIST FOR ESD SYSTEM
ITEM | Cable Code | Tag No. | Description | Cable No. |  | From | To. | SYSTEM | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | Lead Cover | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | CABLE LENGTH (M) | GLAND SIZE | Remark
1 | BR-1P-2-FA | PIT-2111 | Pressure Indicator Transmitter | IC- | PIT-2111 | PIT-2111 | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
2 | BR-1P-2-FA | LIT-2112 | Level Indicator Transmitter | IC- | LIT-2112 | LIT-2112 | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
3 | BR-1P-2-FA | PIT-2115 | Pressure Indicator Transmitter | IC- | PIT-2115 | PIT-2115 | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
4 | BR-1P-2-FA | PIT-2114A | Pressure Indicator Transmitter | IC- | PIT-2114A | PIT-2114A | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
5 | BR-1P-2-FA | PIT-2114B | Pressure Indicator Transmitter | IC- | PIT-2114B | PIT-2114B | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
6 | BR-1P-2-FA | LIT-2117 | Level Indicator Transmitter | IC- | LIT-2117 | LIT-2117 | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
7 | BR-1P-2-FA | LIT-2118 | Level Indicator Transmitter | IC- | LIT-2118 | LIT-2118 | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
8 | BR-1P-2-FA | PIT-2116 | Pressure Indicator Transmitter | IC- | PIT-2116 | PIT-2116 | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
9 | BR-1P-2-FA | PIT-2116A | Pressure Indicator Transmitter | IC- | PIT-2116A | PIT-2116A | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
10 | BR-1P-2-FA | PIT-2116B | Pressure Indicator Transmitter | IC- | PIT-2116B | PIT-2116B | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
11 | BR-1P-2-FA | LIT-2272 | Level Indicator Transmitter | IC- | LIT-2272 | LIT-2272 | JBE-A-2101 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
12 | BR-19P-1-LFA | JBE-A-2101 | Junction Box | MC- | JBE-A-2101 | JBE-A-2101 | ESD | ESD | FRS | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 260 | M50
13 | BR-1P-2-FA | LIT-2122A | Level Indicator Transmitter | IC- | LIT-2122A | LIT-2122A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
14 | BR-1P-2-FA | PIT-2122A | Pressure Indicator Transmitter | IC- | PIT-2122A | PIT-2122A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
15 | BR-1P-2-FA | PIT-2125A | Pressure Indicator Transmitter | IC- | PIT-2125A | PIT-2125A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
16 | BR-1P-2-FA | TIT-2124A | Temperature Indicator Transmitter | IC- | TIT-2124A | TIT-2124A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
17 | BR-1P-2-FA | LIT-2132A | Level Indicator Transmitter | IC- | LIT-2132A | LIT-2132A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
18 | BR-1P-2-FA | PIT-2131A | Pressure Indicator Transmitter | IC- | PIT-2131A | PIT-2131A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
19 | BR-1P-2-FA | PIT-2134A | Pressure Indicator Transmitter | IC- | PIT-2134A | PIT-2134A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
20 | BR-1P-2-FA | TIT-2134A | Temperature Indicator Transmitter | IC- | TIT-2134A | TIT-2134A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
21 | BR-1P-2-FA | TIT-2125A | Temperature Indicator Transmitter | IC- | TIT-2125A | TIT-2125A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
22 | BR-1P-2-FA | TIT-2136A | Temperature Indicator Transmitter | IC- | TIT-2136A | TIT-2136A | JBE-A-2102 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
23 | BR-19P-1-LFA | JBE-A-2102 | Junction Box | MC- | JBE-A-2102 | JBE-A-2102 | ESD | ESD | FRS | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 320 | M50
24 | BR-1P-2-FA | LIT-2122B | Level Indicator Transmitter | IC- | LIT-2122B | LIT-2122B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
25 | BR-1P-2-FA | PIT-2122B | Pressure Indicator Transmitter | IC- | PIT-2122B | PIT-2122B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
26 | BR-1P-2-FA | PIT-2125B | Pressure Indicator Transmitter | IC- | PIT-2125B | PIT-2125B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
27 | BR-1P-2-FA | TIT-2124B | Temperature Indicator Transmitter | IC- | TIT-2124B | TIT-2124B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
28 | BR-1P-2-FA | LIT-2132B | Level Indicator Transmitter | IC- | LIT-2132B | LIT-2132B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
29 | BR-1P-2-FA | PIT-2131B | Pressure Indicator Transmitter | IC- | PIT-2131B | PIT-2131B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
30 | BR-1P-2-FA | PIT-2134B | Pressure Indicator Transmitter | IC- | PIT-2134B | PIT-2134B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
31 | BR-1P-2-FA | TIT-2134B | Temperature Indicator Transmitter | IC- | TIT-2134B | TIT-2134B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
32 | BR-1P-2-FA | TIT-2125B | Temperature Indicator Transmitter | IC- | TIT-2125B | TIT-2125B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
33 | BR-1P-2-FA | TIT-2136B | Temperature Indicator Transmitter | IC- | TIT-2136B | TIT-2136B | JBE-A-2103 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
34 | BR-19P-1-LFA | JBE-A-2103 | Junction Box | MC- | JBE-A-2103 | JBE-A-2103 | ESD | ESD | FRS | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 340 | M50
35 | BR-1P-2-FA | LIT-2122C | Level Indicator Transmitter | IC- | LIT-2122C | LIT-2122C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
36 | BR-1P-2-FA | PIT-2122C | Pressure Indicator Transmitter | IC- | PIT-2122C | PIT-2122C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
37 | BR-1P-2-FA | PIT-2125C | Pressure Indicator Transmitter | IC- | PIT-2125C | PIT-2125C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
38 | BR-1P-2-FA | TIT-2124C | Temperature Indicator Transmitter | IC- | TIT-2124C | TIT-2124C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
39 | BR-1P-2-FA | LIT-2132C | Level Indicator Transmitter | IC- | LIT-2132C | LIT-2132C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
40 | BR-1P-2-FA | PIT-2131C | Pressure Indicator Transmitter | IC- | PIT-2131C | PIT-2131C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
41 | BR-1P-2-FA | PIT-2134C | Pressure Indicator Transmitter | IC- | PIT-2134C | PIT-2134C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
42 | BR-1P-2-FA | TIT-2134C | Temperature Indicator Transmitter | IC- | TIT-2134C | TIT-2134C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
43 | BR-1P-2-FA | TIT-2125C | Temperature Indicator Transmitter | IC- | TIT-2125C | TIT-2125C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
44 | BR-1P-2-FA | TIT-2136C | Temperature Indicator Transmitter | IC- | TIT-2136C | TIT-2136C | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
45 | BR-1P-2-FA | LIT-2142 | Level Indicator Transmitter | IC- | LIT-2142 | LIT-2142 | JBE-A-2104 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
46 | BR-19P-1-LFA | JBE-A-2104 | Junction Box | MC- | JBE-A-2104 | JBE-A-2104 | ESD | ESD | FRS | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 370 | M50
47 | BR-1P-2-FA | PIT-3201A | Pressure Indicator Transmitter | IC- | PIT-3201A | PIT-3201A | JBE-A-2105 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
48 | BR-1P-2-FA | PIT-3201B | Pressure Indicator Transmitter | IC- | PIT-3201B | PIT-3201B | JBE-A-2105 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
49 | BR-1P-2-FA | PIT-3201C | Pressure Indicator Transmitter | IC- | PIT-3201C | PIT-3201C | JBE-A-2105 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
50 | BR-1P-2-FA | LIT-2161 | Level Indicator Transmitter | IC- | LIT-2161 | LIT-2161 | JBE-A-2105 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
51 | BR-12P-1-LFA | JBE-A-2105 | Junction Box | MC- | JBE-A-2105 | JBE-A-2105 | ESD | ESD | FRS | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 450 | M40
52 | - | PIT-2161 | Level Indicator Transmitter | IC- | PIT-2161 | PIT-2161 | JBE-A-2106 | DCS | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | - | M20 | Deleted
53 | BR-1P-2-FA | PIT-2222A | Pressure Indicator Transmitter | IC- | PIT-2222A | PIT-2222A | JBE-A-2106 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
54 | BR-1P-2-FA | PIT-2222B | Pressure Indicator Transmitter | IC- | PIT-2222B | PIT-2222B | JBE-A-2106 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
55 | BR-1P-2-FA | LIT-2252A | Level Indicator Transmitter | IC- | LIT-2252A | LIT-2252A | JBE-A-2106 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
56 | BR-1P-2-FA | LIT-2252B | Level Indicator Transmitter | IC- | LIT-2252B | LIT-2252B | JBE-A-2106 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
57 | BR-1P-2-FA | LIT-2252C | Level Indicator Transmitter | IC- | LIT-2252C | LIT-2252C | JBE-A-2106 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
58 | BR-1P-2-FA | LIT-2253 | Level Indicator Transmitter | IC- | LIT-2253 | LIT-2253 | JBE-A-2106 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
59 | BR-1P-2-FA | PIT-2251A | Pressure Indicator Transmitter | IC- | PIT-2251A | PIT-2251A | JBE-A-2106 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
60 | BR-1P-2-FA | PIT-2251B | Pressure Indicator Transmitter | IC- | PIT-2251B | PIT-2251B | JBE-A-2106 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
61 | BR-12P-1-LFA | JBE-A-2106 | Junction Box | MC- | JBE-A-2106 | JBE-A-2106 | ESD | ESD | FRS | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 420 | M40
62 | BR-1P-2-FA | PIT-2201A | Pressure Indicator Transmitter | IC- | PIT-2201A | PIT-2201A | JBE-A-2107 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
63 | BR-1P-2-FA | PIT-2201B | Pressure Indicator Transmitter | IC- | PIT-2201B | PIT-2201B | JBE-A-2107 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
64 | BR-1P-2-FA | PIT-2201C | Pressure Indicator Transmitter | IC- | PIT-2201C | PIT-2201C | JBE-A-2107 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
65 | BR-1P-2-FA | PIT-2211 | Pressure Indicator Transmitter | IC- | PIT-2211A | PIT-2211A | JBE-A-2107 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
66 | BR-1P-2-FA | PIT-2202 | Pressure Indicator Transmitter | IC- | PIT-2202 | PIT-2202 | JBE-A-2107 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 30 | M20
67 | BR-12P-1-LFA | JBE-A-2107 | Junction Box | MC- | JBE-A-2107 | JBE-A-2107 | ESD | ESD | FRS | SWA | IS | 12 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 320 | M40
68 | GR-1P-2-FA | VSHH-2121A | Vibration Switch | IC- | VSHH-2121A | VSHH-2121A | JBE-D-2101 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
69 | GR-1P-2-FA | VSHH-2122A | Vibration Switch | IC- | VSHH-2122A | VSHH-2122A | JBE-D-2101 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
70 | GR-1P-2-FA | VSHH-2131A | Vibration Switch | IC- | VSHH-2131A | VSHH-2131A | JBE-D-2101 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
71 | GR-1P-2-FA | VSHH-2132A | Vibration Switch | IC- | VSHH-2132A | VSHH-2132A | JBE-D-2101 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
72 | GR-7P-1-LFA | JBE-D-2101 | Junction Box | MC- | JBE-D-2101 | JBE-D-2101 | ESD | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 350 | M32
73 | GR-1P-2-FA | VSHH-2121B | Vibration Switch | IC- | VSHH-2121B | VSHH-2121B | JBE-D-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
74 | GR-1P-2-FA | VSHH-2122B | Vibration Switch | IC- | VSHH-2122B | VSHH-2122B | JBE-D-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
75 | GR-1P-2-FA | VSHH-2131B | Vibration Switch | IC- | VSHH-2131B | VSHH-2131B | JBE-D-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
76 | GR-1P-2-FA | VSHH-2132B | Vibration Switch | IC- | VSHH-2132B | VSHH-2132B | JBE-D-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
77 | GR-7P-1-LFA | JBE-D-2102 | Junction Box | MC- | JBE-D-2102 | JBE-D-2102 | ESD | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 370 | M32
78 | GR-1P-2-FA | VSHH-2121C | Vibration Switch | IC- | VSHH-2121C | VSHH-2121C | JBE-D-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
79 | GR-1P-2-FA | VSHH-2122C | Vibration Switch | IC- | VSHH-2122C | VSHH-2122C | JBE-D-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
80 | GR-1P-2-FA | VSHH-2131C | Vibration Switch | IC- | VSHH-2131C | VSHH-2131C | JBE-D-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
81 | GR-1P-2-FA | VSHH-2132C | Vibration Switch | IC- | VSHH-2132C | VSHH-2132C | JBE-D-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 30 | M20
82 | GR-7P-1-LFA | JBE-D-2103 | Junction Box | MC- | JBE-D-2103 | JBE-D-2103 | ESD | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 390 | M32
83 | - | JBE-S-2101 | Junction Box | MC- | JBE-S-2101 | JBE-S-2101 | ESD | ESD | FRS | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | - | M40 | Deleted
84 | GR-1P-3-FA | ESOV-2101 | Solenoid Valve | IC- | ESOV-2101 | ESOV-2101 | JBE-S-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
85 | GR-1P-3-FA | ESOV-2112 | Solenoid Valve | IC- | ESOV-2112 | ESOV-2112 | JBE-S-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
86 | GR-1P-3-FA | ESOV-2113 | Solenoid Valve | IC- | ESOV-2113 | ESOV-2113 | JBE-S-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
87 | GR-1P-3-FA | ESOV-2271 | Solenoid Valve | IC- | ESOV-2271 | ESOV-2271 | JBE-S-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
88 | GR-1P-3-FA | ESOV-2272 | Solenoid Valve | IC- | ESOV-2272 | ESOV-2272 | JBE-S-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
89 | GR-1P-3-FA | ESOV-2102 | Solenoid Valve | IC- | ESOV-2102 | ESOV-2102 | JBE-S-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
90 | GR-1P-3-FA | BSOV-2110 | Solenoid Valve | IC- | BSOV-2110 | BSOV-2110 | JBE-S-2102 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20 | Added
91 | GR-12P-3-LFA | JBE-S-2102 | Junction Box | MC- | JBE-S-2102 | JBE-S-2102 | ESD | ESD | FRS | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 260 | M40
92 | GR-1P-3-FA | BSOV-2132A | Solenoid Valve | IC- | BSOV-2132A | BSOV-2132A | JBE-S-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
93 | GR-1P-3-FA | BSOV-2134A | Solenoid Valve | IC- | BSOV-2134A | BSOV-2134A | JBE-S-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
94 | GR-1P-3-FA | ESOV-2121A | Solenoid Valve | IC- | ESOV-2121A | ESOV-2121A | JBE-S-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
95 | GR-1P-3-FA | ESOV-2122A | Solenoid Valve | IC- | ESOV-2122A | ESOV-2122A | JBE-S-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
96 | GR-1P-3-FA | ESOV-2131A | Solenoid Valve | IC- | ESOV-2131A | ESOV-2131A | JBE-S-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
97 | GR-1P-3-FA | ESOV-2133A | Solenoid Valve | IC- | ESOV-2133A | ESOV-2133A | JBE-S-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
98 | - | BSOV-2122A | Solenoid Valve | IC- | BSOV-2122A | BSOV-2122A | JBE-S-2103 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | - | M20 | Deleted
99 | GR-12P-3-LFA | JBE-S-2103 | Junction Box | MC- | JBE-S-2103 | JBE-S-2103 | ESD | ESD | FRS | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 320 | M40
100 | GR-1P-3-FA | BSOV-2132B | Solenoid Valve | IC- | BSOV-2132B | BSOV-2132B | JBE-S-2104 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
101 | GR-1P-3-FA | BSOV-2134B | Solenoid Valve | IC- | BSOV-2134B | BSOV-2134B | JBE-S-2104 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
102 | GR-1P-3-FA | ESOV-2121B | Solenoid Valve | IC- | ESOV-2121B | ESOV-2121B | JBE-S-2104 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
103 | GR-1P-3-FA | ESOV-2122B | Solenoid Valve | IC- | ESOV-2122B | ESOV-2122B | JBE-S-2104 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
104 | GR-1P-3-FA | ESOV-2131B | Solenoid Valve | IC- | ESOV-2131B | ESOV-2131B | JBE-S-2104 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
105 | GR-1P-3-FA | ESOV-2133B | Solenoid Valve | IC- | ESOV-2133B | ESOV-2133B | JBE-S-2104 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
106 | - | BSOV-2122B | Solenoid Valve | IC- | BSOV-2122B | BSOV-2122B | JBE-S-2104 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | - | M20 | Deleted
107 | GR-12P-3-LFA | JBE-S-2104 | Junction Box | MC- | JBE-S-2104 | JBE-S-2104 | ESD | ESD | FRS | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 340 | M40
108 | GR-1P-3-FA | BSOV-2132C | Solenoid Valve | IC- | BSOV-2132C | BSOV-2132C | JBE-S-2105 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
109 | GR-1P-3-FA | BSOV-2134C | Solenoid Valve | IC- | BSOV-2134C | BSOV-2134C | JBE-S-2105 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
110 | GR-1P-3-FA | ESOV-2121C | Solenoid Valve | IC- | ESOV-2121C | ESOV-2121C | JBE-S-2105 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
111 | GR-1P-3-FA | ESOV-2122C | Solenoid Valve | IC- | ESOV-2122C | ESOV-2122C | JBE-S-2105 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
112 | GR-1P-3-FA | ESOV-2131C | Solenoid Valve | IC- | ESOV-2131C | ESOV-2131C | JBE-S-2105 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
113 | GR-1P-3-FA | ESOV-2133C | Solenoid Valve | IC- | ESOV-2133C | ESOV-2133C | JBE-S-2105 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
114 | - | BSOV-2122C | Solenoid Valve | IC- | BSOV-2122C | BSOV-2122C | JBE-S-2105 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | - | M20 | Deleted
115 | GR-12P-3-LFA | JBE-S-2105 | Junction Box | MC- | JBE-S-2105 | JBE-S-2105 | ESD | ESD | FRS | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 370 | M40
116 | GR-1P-3-FA | BSOV-2141 | Solenoid Valve | IC- | BSOV-2141 | BSOV-2141 | JBE-S-2106 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
117 | GR-1P-3-FA | ESOV-2142 | Solenoid Valve | IC- | ESOV-2142 | ESOV-2142 | JBE-S-2106 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
118 | GR-1P-3-FA | ESOV-2143 | Solenoid Valve | IC- | ESOV-2143 | ESOV-2143 | JBE-S-2106 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
119 | GR-1P-3-FA | ESOV-2144 | Solenoid Valve | IC- | ESOV-2144 | ESOV-2144 | JBE-S-2106 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
120 | GR-1P-3-FA | BSOV-2151 | Solenoid Valve | IC- | BSOV-2151 | BSOV-2151 | JBE-S-2106 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 30 | M20
121 | GR-1P-3-FA | ESOV-3201 | Solenoid Valve | IC- | ESOV-3201 | ESOV-3201 | JBE-S-2106 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 50 | M20
122 | GR-12P-3-LFA | JBE-S-2106 | Junction Box | MC- | JBE-S-2106 | JBE-S-2106 | ESD | ESD | FRS | SWA | NIS | 12 | PAIR | 2.5 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 400 | M40
123 | GR-1P-3-FA | ESOV-2201 | Solenoid Valve | IC- | ESOV-2201 | ESOV-2201 | ESD | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 320 | M20 | Direct
124 | - | ESD-PK-2281 | Solenoid Valve | IC- | ESD-PK-2281 | PK-2281 | JBE-S-2107 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | - | M20 | Deleted
125 | - | JBE-S-2107 | Junction Box | MC- | JBE-S-2107 | JBE-S-2107 | ESD | ESD | FRS | SWA | NIS | 12 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | - | M40 | Deleted
126 | GR-1P-2-FA | ESD-PK-2207 | SHOUTDOWN | IC- | ESD-PK-2207 | ESD-PK-2207 | ESD | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 320 | M20 | Direct
127 | GR-1P-2-FA | FST-2201 | Start Command | IC- | FST-2201 | ESD | LOCAL MCC OR PDP IS IN VENDOR SCOPE OF WORK | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 300 | M20 | Added
128 | - | [5 empty] | SIGNALS BETWEEN ESD AND OTHER SYSTEMS | [12 empty] | -
129 | GR-7P-1-F | ESD-PK-C-2203 A | Trip Command | MC- | ESD-PK-AC-2203A | UCP-C-2203A | ESD | ESD | FRS | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32
130 | GR-7P-1-F | ESD-PK-C-2203 B | Trip Command | MC- | ESD-PK-AC-2203B | UCP-C-2203B | ESD | ESD | FRS | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32
131 | GR-7P-1-F | ESD-PK-G-2204 | Trip Command | IC- | ESD-PK-G-2204 | ESD | ESD-PK-G-2204 | ESD | FRS | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32 | Added
132 | GR-7P-1-F | ESD-PK-2101 | Trip Command | MC- | ESD-PK-2101 | ESD/BMS-PK-2101 | ESD | ESD | FRS | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32
133 |  | ESD3-PK-2101 | Trip Alarm
134 | GR-7P-1-F | ESDI 0- NEW | ESD 0 to Existing System (Just Status) | MC- | ESD-EX ESD | ESD | EXISTING SYSTEM | ESD | FRS | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32
135 |  | ESDI 1- NEW | NEW SYSTEM ESD 1 status | [18 empty] | Deleted
136 |  | ESDI 1A- NEW | NEW SYSTEM ESD 1A status
137 | GR-12P-1-F | ESDR2A-C-2101-A | Trip Command With Depressurizing | MC- | ESD-UCP-GC-2101A | UCP-GC-2101A | ESD | ESD | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M40
138 |  | ESDR2-C-2101-A | Trip Command Without Depressurizing
139 |  | ESD2A-C-2101-A | Trip Alarm With Depressurizing
140 |  | ESD2-C-2101-A | Trip Alarm Without Depressurizing
141 | GR-12P-1-F | ESDR2A-C-2101-B | Trip Command With Depressurizing | MC- | ESD-UCP-GC-2101B | UCP-GC-2101B | ESD | ESD | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M40
142 |  | ESDR2-C-2101-B | Trip Command Without Depressurizing
143 |  | ESD2A-C-2101-B | Trip Alarm With Depressurizing
144 |  | ESD2-C-2101-B | Trip Alarm Without Depressurizing
145 | GR-12P-1-F | ESDR2A-C-2101-C | Trip Command With Depressurizing | MC- | ESD-UCP-GC-2101C | UCP-GC-2101C | ESD | ESD | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M40
146 |  | ESDR2-C-2101-C | Trip Command Without Depressurizing
147 |  | ESD2A-C-2101-C | Trip Alarm With Depressurizing
148 |  | ESD2-C-2101-C | Trip Alarm Without Depressurizing
149 | GR-7P-1-F | ESDR 1-PCS | PCS FAILURE | IC- | DCS-ESD | ESD | DCS | ESD | FRS | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | 50
150 | - | ESDR 1-FLR | FLARE IGNITION FAILURE | IC- | FLARE-ESD | ESD | FLARE | ESD | FRS | - | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M32 | Deleted
151 | GR-7P-1-F | ESDR 0-F&G | CONFIRMED FLAMMABLE GAS IN HVAC INTAKE (COMMAND FROM FGS) | MC- | FGS-ESD | ESD | F&G | ESD | FRS | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32
152 |  | ESDR 1A-F&G | CONFIRMED FLAMMABLE GAS IN PROCESS AREA (COMMAND FROM FGS)
153 |  | ESD 1A-F&G | CONFIRMED FIRE IN FIRE ZONE (PROCESS) AREA (COMMAND FROM F&G)
154 | - | [6 empty] | SIGNALS BETWEEN ESD AND CONSOLE | [11 empty] | -
155 | GR-12P-1-F | ESD0-LAMP | TOTAL PLANT SHUT DOWN WITH AUTOMATIC DEPRESSURIZING (ESD0) | MC- | CON-ESD 1 | ESD | ED CONSOLE | ESD | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M40
156 |  | ESD1A-LAMP | PROCESS EMERGENCY SHUT DOWN WITH DEPRESSURIZING (ESD1A)
157 |  | ESD2A-A-LAMP | TRAIN A SHUT DOWN WITH DEPRESSURIZING
158 |  | ESD2A-B-LAMP | TRAIN B SHUT DOWN WITH DEPRESSURIZING
159 |  | ESD2A-C-LAMP | TRAIN C SHUT DOWN WITH DEPRESSURIZING
160 |  | LAMP-ESD-INH | ESD INHIBIT LAMP
161 |  | LAMP-ESD-RST | ESD RESET LAMP
162 |  | ESD1-LAMP | PROCESS EMERGENCY SHUT DOWN WITHOUT DEPRESSURIZING (ESD1)
163 |  | ESD2-A-LAMP | TRAIN A SHUT DOWN WITHOUT DEPRESSURIZING
164 | GR-12P-1-F | ESD2-B-LAMP | TRAIN B SHUT DOWN WITHOUT DEPRESSURIZING | MC- | CON-ESD 2 | ESD | ED CONSOLE | ESD | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M40
165 |  | ESD2-C-LAMP | TRAIN C SHUT DOWN WITHOUT DEPRESSURIZING
166 |  | ESD0-PB | TOTAL PLANT SHUT DOWN WITH AUTOMATIC DEPRESSURIZING (ESD0) P.B.
167 |  | ESD1A-PB | PROCESS EMERGENCY SHUT DOWN WITH DEPRESSURIZING (ESD1A) P.B.
168 |  | ESD2A-A-PB | TRAIN A SHUT DOWN WITH DEPRESSURIZING (ESD2A-A) P.B.
169 |  | ESD2A-B-PB | TRAIN B SHUT DOWN WITH DEPRESSURIZING (ESD2A-B) P.B.
170 |  | ESD2A-C-PB | TRAIN C SHUT DOWN WITH DEPRESSURIZING (ESD2A-C) P.B.
171 |  | ESD-INH-SEL | Selector Switch With key | [18 empty] | Added
172 |  | ESD-RST-PB | Momentary Yellow Push Button | [18 empty] | Added
173 | GR-12P-1-F | ESD1-PB | PROCESS EMERGENCY SHUT DOWN WITHOUT DEPRESSURIZING (ESD1) P.B. | MC- | CON-ESD 3 | ESD | ED CONSOLE | ESD | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M40 | Added
174 |  | ESD2-A-PB | TRAIN A SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-A) P.B.
175 |  | ESD2-B-PB | TRAIN B SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-B) P.B.
176 |  | ESD2-C-PB | TRAIN C SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-C) P.B.
177 |  | ESDI 0-EX | EXISTING SYSTEM ESD 0 status
178 |  | ESD-ACK-PB | Momentary Yellow Push Button | [18 empty] | Added
179 |  | LAMP-ESD-ACK | Signal Lamp | [18 empty] | Added
180 |  | ESDI 1-EX | EXISTING SYSTEM ESD 1 status | [18 empty] | Deleted
181 |  | ESDI 1A-EX | EXISTING SYSTEM ESD 1A status | [18 empty] | Deleted
182 |  | ESD 3-A-LAMP | COMPRESSOR C-2101-A SHUTDOWN LAMP | [18 empty] | Deleted
183 |  | ESD 3-B-LAMP | COMPRESSOR C-2101-B SHUTDOWN LAMP | [18 empty] | Deleted
184 |  | ESD 3-C-LAMP | COMPRESSOR C-2101-C SHUTDOWN LAMP | [18 empty] | Deleted
185 |  | ESD 3-A-PB | COMPRESSOR C-2101-A SHUTDOWN PUSH BOTTOM | [18 empty] | Deleted
186 |  | ESD 3-B-PB | COMPRESSOR C-2101-B SHUTDOWN PUSH BOTTOM | [18 empty] | Deleted
187 |  | ESD 3-C-PB | COMPRESSOR C-2101-C SHUTDOWN PUSH BOTTOM | [18 empty] | Deleted
188 | - | [5 empty] | SIGNALS BETWEEN ESD AND MCC | [12 empty] | -
189 | GR-19P-1-FA | ESD-P-2111-A | Trip Command-P-2101-A | MC- | IRP-ESD 1 | IRP | ESD | ESD | FRS | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 140 | M50
190 |  | ESD-P-2111-B | Trip Command-P-2101-B
191 |  | ESD-AE-2101-A-1 | Trip Command-AE-2101-A
192 |  | ESD-AE-2101-A-2 | Trip Command-AE-2101-A
193 |  | ESD-AE-2101-B-1 | Trip Command-AE-2101-B
194 |  | ESD-AE-2101-B-2 | Trip Command-AE-2101-B
195 |  | ESD-AE-2101-C-1 | Trip Command-AE-2101-C
196 |  | ESD-AE-2101-C-2 | Trip Command-AE-2101-C
197 |  | ESD-AE-2102-A-1 | Trip Command-AE-2102-A
198 |  | ESD-AE-2102-A-2 | Trip Command-AE-2102-A
199 |  | ESD-AE-2102-B-1 | Trip Command-AE-2102-B
200 |  | ESD-AE-2102-B-2 | Trip Command-AE-2102-B
201 |  | ESD-AE-2102-C-1 | Trip Command-AE-2102-C
202 |  | ESD-AE-2102-C-2 | Trip Command-AE-2102-C
203 | GR-19P-1-FA | ESD-P-2161-A | Trip Command-P-2103-A | MC- | IRP-ESD 2 | IRP | ESD | ESD | FRS | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 140 | M50
204 |  | ESD-P-2161-B | Trip Command-P-2103-B
205 |  | ESD-P-2221-A | Trip Command-P-2202-A
206 |  | ESD-P-2221-B | Trip Command-P-2202-B
207 |  | ESD-P-2222-A | Trip Command-P-2203-A
208 |  | ESD-P-2222-B | Trip Command-P-2203-B
209 |  | ESD-P-2251A | Trip Command-P-2201-A
210 |  | ESD-P-2251B | Trip Command-P-2201-B
211 |  | ESD 0-EL1A | 11/0.4 KV SWGR-Transformer Feeder-Q2 (EMERGENCY + NORMAL POWER ISOLATION) | [18 empty] | Added
212 |  | ESD 0-EL1B | 11/0.4 KV SWGR-Transformer Feeder-Q2 (EMERGENCY + NORMAL POWER ISOLATION) | [18 empty] | Added
213 |  | ESD-P-2206 | - | [18 empty] | Added
214 |  | ESD-P-2293 | - | [18 empty] | Added
215 |  | ESD-2131C | Trip Command | [18 empty] | Deleted
216 |  | ESD-2132C | Trip Command | [18 empty] | Deleted
217 |  | ESD 0-EL1 | EMERGENCY + NORMAL POWER ISOLATION | [18 empty] | Deleted
218 |  | ESD 1A-EL1 | POWER ISOLATION IN PROCESS AREA | [18 empty] | Deleted
219 |  | ESDR 1-EL1 | NETWORK POWER FAILURE SWITCH ACTIVATION | [18 empty] | Deleted
220 |  | ESD-P-3101 | - | [18 empty] | Deleted
221 | - | ESDI 0-DCS | ESD 0 status in DCS | MC- | DCS-ESD | ESD | DCS | ESD | FRS | - | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M50 | Deleted
222 |  | ESDI 1-DCS | ESD 1 status in DCS | [18 empty] | Deleted
223 |  | ESDI 1A-DCS | ESD 1A status in DCS | [18 empty] | Deleted
224 |  | ESDI 2-A-DCS | ESD 2 status in DCS (TRAIN A) | [18 empty] | Deleted
225 |  | ESDI 2-B-DCS | ESD 2 status in DCS (TRAIN B) | [18 empty] | Deleted
226 |  | ESDI 2-C-DCS | ESD 2 status in DCS (TRAIN C) | [18 empty] | Deleted
227 |  | ESDI 2A-A-DCS | ESD 2A status in DCS (TRAIN A) | [18 empty] | Deleted
228 |  | ESDI 2A-B-DCS | ESD 2A status in DCS (TRAIN B) | [18 empty] | Deleted
229 |  | ESDI 2A-C-DCS | ESD 2A status in DCS (TRAIN C) | [18 empty] | Deleted
230 |  | ESDI 3-A-DCS | ESD 3 status in DCS (TRAIN A) | [18 empty] | Deleted
231 |  | ESDI 3-B-DCS | ESD 3 status in DCS (TRAIN B) | [18 empty] | Deleted
232 |  | ESDI 3-C-DCS | ESD 3 status in DCS (TRAIN C) | [18 empty] | Deleted
233 |  | ESDI 3A-A-DCS | ESD 3A status in DCS (TRAIN A) | [18 empty] | Deleted
234 |  | ESDI 3A-B-DCS | ESD 3A status in DCS (TRAIN B) | [18 empty] | Deleted
235 |  | ESDI 3A-C-DCS | ESD 3A status in DCS (TRAIN C) | [18 empty] | Deleted
236 | GR-19P-1-FA | ESD R0-UPS-A | Trip Alarm (Request) | MC- | UPS-ESD | ESD | UPS CHARGER | ESD | FRS | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 140 | M50 | Modified
237 |  | ESD R0-UPS-B | Trip Alarm (Request)
238 |  | ESD 0-EL2A | 110V AC UPS, CH01 ISOLATION COMMAND
239 |  | ESD 0-EL2B | 110V AC UPS, CH02 ISOLATION COMMAND
240 |  | ESDR 1-DC | DC , CHARGER FAILURE
241 |  | ESD 0-EL3A | 24 V DC UPS-002-CH01 Isolation Command
242 |  | ESD 0-EL3B | 24 V DC UPS-002-CH02 Isolation Command
243 |  | ESD 0-EL4A | 110 V DC Charger-001-CH01 Isolation Command
244 |  | ESD 0-EL4B | 110 V DC Charger-001-CH02 Isolation Command
D04
TOTALLY REVIZED

## Cable list (F&G)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 |  | IN |  | LI | 0009 |  | D04
INSTRUMENT CABLE LIST FOR F&G SYSTEM
ITEM | Cable Code | Tag No. | Description | Cable No. |  | From | To. | SYSTEM | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | Lead Cover | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | CABLE LENGTH (M) | GLAND SIZE | Remark
1 | RD-1T-2-FA | FD-2003 | Flame Detector | IC- | FD-2003 | FD-2003 | JBF-A-2101 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
2 | RD-1T-2-FA | FGD-2001 | Flammable Gas Detector | IC- | FGD-2001 | FGD-2001 | JBF-A-2101 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
3 | RD-1T-2-FA | FGD-2003 | Flammable Gas Detector | IC- | FGD-2003 | FGD-2003 | JBF-A-2101 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
4 | RD-1T-2-FA | FGD-2004 | Flammable Gas Detector | IC- | FGD-2004 | FGD-2004 | JBF-A-2101 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
5 | RD-1T-2-FA | TGD-2001 | Toxic Gas Detector | IC- | TGD-2001 | TGD-2001 | JBF-A-2101 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
6 | RD-1T-2-FA | TGD-2003 | Toxic Gas Detector | IC- | TGD-2003 | TGD-2003 | JBF-A-2101 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
7 | RD-1T-2-FA | TGD-2004 | Toxic Gas Detector | IC- | TGD-2004 | TGD-2004 | JBF-A-2101 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
8 | RD-12T-1-LFA | JBF-A-2101 | Junction Box | MC- | JBF-A-2101 | JBF-A-2101 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 260 | M50
9 | RD-1T-2-FA | FD-2001 | Flame Detector | IC- | FD-2001 | FD-2001 | JBF-A-2102 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
10 | RD-1T-2-FA | FD-2002 | Flame Detector | IC- | FD-2002 | FD-2002 | JBF-A-2102 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
11 | RD-1T-2-FA | FGD-2002 | Flammable Gas Detector | IC- | FGD-2002 | FGD-2002 | JBF-A-2102 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
12 | RD-1T-2-FA | TGD-2002 | Toxic Gas Detector | IC- | TGD-2002 | TGD-2002 | JBF-A-2102 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
13 | RD-1T-2-FA | FD-3001 | Flame Detector | IC- | FD-3001 | FD-3001 | JBF-A-2102 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
14 | - | FGD-3001 | Flammable Gas Detector | IC- | FGD-3001 | FGD-3001 | JBF-A-2102 | FGS | FRS | SWA | - | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | Deleted
15 | - | TGD-3001 | Toxic Gas Detector | IC- | TGD-3001 | TGD-3001 | JBF-A-2102 | FGS | FRS | SWA | - | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | Deleted
16 | RD-7T-1-LFA | JBF-A-2102 | Junction Box | MC- | JBF-A-2102 | JBF-A-2102 | FGS | FGS | FRS | SWA | NIS | 7 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 280 | M32
17 | RD-1T-2-FA | FD-4001A | Flame Detector | IC- | FD-4001A | FD-4001A | JBF-A-2103 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
18 | RD-1T-2-FA | FD-4002A | Flame Detector | IC- | FD-4002A | FD-4002A | JBF-A-2103 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
19 | RD-1T-2-FA | FGD-4001A | Flammable Gas Detector | IC- | FGD-4001A | FGD-4001A | JBF-A-2103 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
20 | RD-1T-2-FA | FGD-4002A | Flammable Gas Detector | IC- | FGD-4002A | FGD-4002A | JBF-A-2103 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
21 | RD-1T-2-FA | FGD-4003A | Flammable Gas Detector | IC- | FGD-4003A | FGD-4003A | JBF-A-2103 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
22 | RD-1T-2-FA | TGD-4001A | Toxic Gas Detector | IC- | TGD-4001A | TGD-4001A | JBF-A-2103 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
23 | RD-1T-2-FA | TGD-4002A | Toxic Gas Detector | IC- | TGD-4002A | TGD-4002A | JBF-A-2103 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
24 | RD-1T-2-FA | TGD-4003A | Toxic Gas Detector | IC- | TGD-4003A | TGD-4003A | JBF-A-2103 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
25 | RD-12T-1-LFA | JBF-A-2103 | Junction Box | MC- | JBF-A-2103 | JBF-A-2103 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 330 | M50
26 | RD-1T-2-FA | FD-4003A | Flame Detector | IC- | FD-4003A | FD-4003A | JBF-A-2104 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
27 | RD-1T-2-FA | FD-4004A | Flame Detector | IC- | FD-4004A | FD-4004A | JBF-A-2104 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
28 | RD-1T-2-FA | FGD-4004A | Flammable Gas Detector | IC- | FGD-4004A | FGD-4004A | JBF-A-2104 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
29 | RD-1T-2-FA | TGD-4004A | Toxic Gas Detector | IC- | TGD-4004A | TGD-4004A | JBF-A-2104 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
30 | RD-1T-2-FA | FGD-5001A | Flammable Gas Detector | IC- | FGD-5001A | FGD-5001A | JBF-A-2104 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
31 | RD-1T-2-FA | TGD-5001A | Toxic Gas Detector | IC- | TGD-5001A | TGD-5001A | JBF-A-2104 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
32 | RD-12T-1-LFA | JBF-A-2104 | Junction Box | MC- | JBF-A-2104 | JBF-A-2104 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 320 | M50
33 | RD-1T-2-FA | FD-4001B | Flame Detector | IC- | FD-4001B | FD-4001B | JBF-A-2105 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
34 | RD-1T-2-FA | FD-4002B | Flame Detector | IC- | FD-4002B | FD-4002B | JBF-A-2105 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
35 | RD-1T-2-FA | FGD-4001B | Flammable Gas Detector | IC- | FGD-4001B | FGD-4001B | JBF-A-2105 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
36 | RD-1T-2-FA | FGD-4002B | Flammable Gas Detector | IC- | FGD-4002B | FGD-4002B | JBF-A-2105 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
37 | RD-1T-2-FA | FGD-4003B | Flammable Gas Detector | IC- | FGD-4003B | FGD-4003B | JBF-A-2105 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
38 | RD-1T-2-FA | TGD-4001B | Toxic Gas Detector | IC- | TGD-4001B | TGD-4001B | JBF-A-2105 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
39 | RD-1T-2-FA | TGD-4002B | Toxic Gas Detector | IC- | TGD-4002B | TGD-4002B | JBF-A-2105 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
40 | RD-1T-2-FA | TGD-4003B | Toxic Gas Detector | IC- | TGD-4003B | TGD-4003B | JBF-A-2105 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
41 | RD-12T-1-LFA | JBF-A-2105 | Junction Box | MC- | JBF-A-2105 | JBF-A-2105 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 350 | M50
42 | RD-1T-2-FA | FD-4003B | Flame Detector | IC- | FD-4003B | FD-4003B | JBF-A-2106 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
43 | RD-1T-2-FA | FD-4004B | Flame Detector | IC- | FD-4004B | FD-4004B | JBF-A-2106 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
44 | RD-1T-2-FA | FGD-4004B | Flammable Gas Detector | IC- | FGD-4004B | FGD-4004B | JBF-A-2106 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
45 | RD-1T-2-FA | TGD-4004B | Toxic Gas Detector | IC- | TGD-4004B | TGD-4004B | JBF-A-2106 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
46 | RD-1T-2-FA | TGD-5001B | Toxic Gas Detector | IC- | TGD-5001B | TGD-5001B | JBF-A-2106 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
47 | RD-1T-2-FA | FGD-5001B | Flammable Gas Detector | IC- | FGD-5001B | FGD-5001B | JBF-A-2106 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
48 | RD-12T-1-LFA | JBF-A-2106 | Junction Box | MC- | JBF-A-2106 | JBF-A-2106 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 370 | M50
49 | RD-1T-2-FA | FD-4001C | Flame Detector | IC- | FD-4001C | FD-4001C | JBF-A-2107 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
50 | RD-1T-2-FA | FD-4002C | Flame Detector | IC- | FD-4002C | FD-4002C | JBF-A-2107 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
51 | RD-1T-2-FA | FGD-4001C | Flammable Gas Detector | IC- | FGD-4001C | FGD-4001C | JBF-A-2107 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
52 | RD-1T-2-FA | FGD-4002C | Flammable Gas Detector | IC- | FGD-4002C | FGD-4002C | JBF-A-2107 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
53 | RD-1T-2-FA | FGD-4003C | Flammable Gas Detector | IC- | FGD-4003C | FGD-4003C | JBF-A-2107 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
54 | RD-1T-2-FA | TGD-4001C | Toxic Gas Detector | IC- | TGD-4001C | TGD-4001C | JBF-A-2107 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
55 | RD-1T-2-FA | TGD-4002C | Toxic Gas Detector | IC- | TGD-4002C | TGD-4002C | JBF-A-2107 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
56 | RD-1T-2-FA | TGD-4003C | Toxic Gas Detector | IC- | TGD-4003C | TGD-4003C | JBF-A-2107 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
57 | RD-12T-1-LFA | JBF-A-2107 | Junction Box | MC- | JBF-A-2107 | JBF-A-2107 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 380 | M50
58 | RD-1T-2-FA | FD-4003C | Flame Detector | IC- | FD-4003C | FD-4003C | JBF-A-2108 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
59 | RD-1T-2-FA | FD-4004C | Flame Detector | IC- | FD-4004C | FD-4004C | JBF-A-2108 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
60 | RD-1T-2-FA | FGD-4004C | Flammable Gas Detector | IC- | FGD-4004C | FGD-4004C | JBF-A-2108 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
61 | RD-1T-2-FA | TGD-4004C | Toxic Gas Detector | IC- | TGD-4004C | TGD-4004C | JBF-A-2108 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
62 | RD-1T-2-FA | TGD-5001C | Toxic Gas Detector | IC- | TGD-5001C | TGD-5001C | JBF-A-2108 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
63 | RD-1T-2-FA | FGD-5001C | Flammable Gas Detector | IC- | FGD-5001C | FGD-5001C | JBF-A-2108 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
64 | RD-12T-1-LFA | JBF-A-2108 | Junction Box | MC- | JBF-A-2108 | JBF-A-2108 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 370 | M50
65 | RD-1T-2-FA | FD-6001 | Flame Detector | IC- | FD-6001 | FD-6001 | JBF-A-2109 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
66 | RD-1T-2-FA | FGD-6001 | Flammable Gas Detector | IC- | FGD-6001 | FGD-6001 | JBF-A-2109 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
67 | RD-1T-2-FA | FGD-6002 | Flammable Gas Detector | IC- | FGD-6002 | FGD-6002 | JBF-A-2109 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
68 | RD-1T-2-FA | TGD-6001 | Toxic Gas Detector | IC- | TGD-6001 | TGD-6001 | JBF-A-2109 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
69 | RD-1T-2-FA | TGD-6002 | Toxic Gas Detector | IC- | TGD-6002 | TGD-6002 | JBF-A-2109 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
70 | RD-7T-1-LFA | JBF-A-2109 | Junction Box | MC- | JBF-A-2109 | JBF-A-2109 | FGS | FGS | FRS | SWA | NIS | 7 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 420 | M32
71 | RD-1T-2-FA | FGD-7001 | Flammable Gas Detector | IC- | FGD-7001 | FGD-7001 | JBF-A-2110 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
72 | RD-1T-2-FA | FGD-7002 | Flammable Gas Detector | IC- | FGD-7002 | FGD-7002 | JBF-A-2110 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
73 | RD-1T-2-FA | FGD-7003 | Flammable Gas Detector | IC- | FGD-7003 | FGD-7003 | JBF-A-2110 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
74 | RD-1T-2-FA | TGD-7001 | Toxic Gas Detector | IC- | TGD-7001 | TGD-7001 | JBF-A-2110 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
75 | RD-1T-2-FA | TGD-7002 | Toxic Gas Detector | IC- | TGD-7002 | TGD-7002 | JBF-A-2110 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
76 | RD-1T-2-FA | TGD-7003 | Toxic Gas Detector | IC- | TGD-7003 | TGD-7003 | JBF-A-2110 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
77 | RD-12T-1-LFA | JBF-A-2110 | Junction Box | MC- | JBF-A-2110 | JBF-A-2110 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 400 | M40
78 | RD-1T-2-FA | FD-6002 | Flame Detector | IC- | FD-6002 | FD-6002 | JBF-A-2111 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
79 | RD-1T-2-FA | FGD-6003 | Flammable Gas Detector | IC- | FGD-6003 | FGD-6003 | JBF-A-2111 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
80 | RD-1T-2-FA | TGD-6003 | Toxic Gas Detector | IC- | TGD-6003 | TGD-6003 | JBF-A-2111 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
81 | RD-7T-1-LFA | JBF-A-2111 | Junction Box | MC- | JBF-A-2111 | JBF-A-2111 | FGS | FGS | FRS | SWA | NIS | 7 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 450 | M32
82 | RD-1T-2-FA | FGD-1001 | Flammable Gas Detector | IC- | FGD-1001 | FGD-1001 | JBF-A-2112 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M20
83 | RD-1T-2-FA | TGD-1001 | Flammable Gas Detector | IC- | TGD-1001 | TGD-1001 | JBF-A-2112 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M20
84 | RD-7T-1-LFA | JBF-A-2112 | Junction Box | MC- | JBF-A-2112 | JBF-A-2112 | FGS | FGS | FRS | SWA | NIS | 7 | Triad | 1 | Yes | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 320 | M32 | Added
85 | RD-1P-2-FA | MAC-2001 | Manual Call Point | IC- | MAC-2001 | MAC-2001 | JBF-D-2101 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
86 | RD-1P-2-FA | MAC-2002 | Manual Call Point | IC- | MAC-2002 | MAC-2002 | JBF-D-2101 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
87 | RD-1P-2-FA | MAC-2003 | Manual Call Point | IC- | MAC-2003 | MAC-2003 | JBF-D-2101 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
88 | RD-1P-2-FA | PSH-2301 | Valve Status | IC- | PSH-2302 | PSH-2302 | JBF-D-2101 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
90 | RD-7P-1-LFA | JBF-D-2101 | Junction Box | MC- | JBF-D-2101 | JBF-D-2101 | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 260 | M32
91 | RD-1P-2-FA | MAC-3001 | Manual Call Point | IC- | MAC-3001 | MAC-3001 | JBF-D-2102 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
92 | RD-1P-2-FA | MAC-4001 | Manual Call Point | IC- | MAC-4001 | MAC-4001 | JBF-D-2102 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
93 | RD-1P-2-FA | PSH-2302 | Valve Status | IC- | PSH-2302 | PSH-2302 | JBF-D-2102 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
95 | RD-7P-1-LFA | JBF-D-2102 | Junction Box | MC- | JBF-D-2102 | JBF-D-2102 | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 330 | M32
96 | RD-1P-2-FA | MAC-4002 | Manual Call Point | IC- | MAC-4002 | MAC-4002 | JBF-D-2103 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
97 | RD-1P-2-FA | PSH-2303 | Valve Status | IC- | PSH-2303 | PSH-2303 | JBF-D-2103 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
99 | RD-1P-2-FA | PSH-2304 | Valve Status | IC- | PSH-2304 | PSH-2304 | JBF-D-2103 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
101 | RD-7P-1-LFA | JBF-D-2103 | Junction Box | MC- | JBF-D-2103 | JBF-D-2103 | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 380 | M32
102 | RD-1P-2-FA | MAC-1001 | Manual Call Point | IC- | MAC-1001 | MAC-1001 | JBF-D-2104 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
103 | RD-1P-2-FA | MAC-1002 | Manual Call Point | IC- | MAC-1002 | MAC-1002 | JBF-D-2104 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
104 | RD-1P-2-FA | MAC-5001 | Manual Call Point | IC- | MAC-5001 | MAC-5001 | JBF-D-2104 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
105 | RD-1P-2-FA | MAC-5002 | Manual Call Point | IC- | MAC-5002 | MAC-5002 | JBF-D-2104 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
106 | RD-1P-2-FA | MAC-6001 | Manual Call Point | IC- | MAC-6001 | MAC-6001 | JBF-D-2104 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
107 | RD-7P-1-LFA | JBF-D-2104 | Junction Box | MC- | JBF-D-2104 | JBF-D-2104 | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 370 | M32
108 | RD-1P-2-FA | MAC-6002 | Manual Call Point | IC- | MAC-6002 | MAC-6002 | JBF-D-2105 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
109 | RD-1P-2-FA | MAC-7001 | Manual Call Point | IC- | MAC-7001 | MAC-7001 | JBF-D-2105 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
110 | RD-1P-2-FA | MAC-7002 | Manual Call Point | IC- | MAC-7002 | MAC-7002 | JBF-D-2105 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
111 | RD-1P-2-FA | LHD-7001 | Linear Heat Detector | IC- | LHD-7001 | LHD-7001 | JBF-D-2105 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
112 | RD-1P-2-FA | LHD-7002 | Linear Heat Detector | IC- | LHD-7002 | LHD-7002 | JBF-D-2105 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
113 | - | LHD-7003 | Linear Heat Detector | IC- | LHD-7003 | LHD-7003 | JBF-D-2104 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | Deleted
114 | - | LHD-7004 | Linear Heat Detector | IC- | LHD-7004 | LHD-7004 | JBF-D-2104 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | Deleted
115 | - | MAC-9002 | Manual Call Point | IC- | MAC-9002 | MAC-9002 | JBF-D-2105 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | Deleted
116 | RD-7P-1-LFA | JBF-D-2105 | Junction Box | MC- | JBF-D-2105 | JBF-D-2105 | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 450 | M32
117 | RD-1P-2-FA | MAC-8001 | Manual Call Point | IC- | MAC-8001 | MAC-8001 | JBF-D-2106 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
118 | RD-1P-2-FA | MAC-8002 | Manual Call Point | IC- | MAC-8002 | MAC-8002 | JBF-D-2106 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20
119 | RD-1P-2-FA | MAC-8003 | Manual Call Point | IC- | MAC-8003 | MAC-8003 | JBF-D-2106 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
120 | RD-1P-2-FA | LSLL-2301 | Low Low Level Alarm | IC- | LSLL-2301 | LSLL-2301 | JBF-D-2106 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
121 | RD-1P-2-FA | LSLL-2302 | Low Low Level Alarm | IC- | LSLL-2302 | LSLL-2302 | JBF-D-2106 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 30 | M20
122 | RD-7P-1-LFA | JBF-D-2106 | Junction Box | MC- | JBF-D-2106 | JBF-D-2106 | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 210 | M32
89 | RD-1P-3-FA | DSOV-2301 | Valve Open Command | IC- | DSOV-2302 | DSOV-2302 | JBF-D-2101 | FGS | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
94 | RD-1P-3-FA | DSOV-2302 | Valve Open Command | IC- | DSOV-2302 | DSOV-2302 | JBF-D-2102 | FGS | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
98 | RD-1P-3-FA | DSOV-2303 | Valve Open Command | IC- | DSOV-2303 | DSOV-2303 | JBF-D-2103 | FGS | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
100 | RD-1P-3-FA | DSOV-2304 | Valve Open Command | IC- | DSOV-2304 | DSOV-2304 | JBF-D-2103 | FGS | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 40 | M20 | Added
122 | RD-7P-3-LFA | JBF-S-2101 | Junction Box | MC- | JBF-S-2101 | JBF-S-2101 | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 350 | M32 | Added
123 | RD-7P-3-LFA | HN-1001 | Horn | MC- | JBF-D-HN-1001 | JBF-D-HN-1001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 300 | M32
124 |  | BR-1001 | Beacon - Red
125 |  | BY-1001 | Beacon - Yellow
126 |  | BB-1001 | Beacon - Blue
127 | RD-7P-3-LFA | HN-2001 | Horn | MC- | JBF-D-HN-2001 | JBF-D-HN-2001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 250 | M32
128 |  | BR-2001 | Beacon - Red
129 |  | BY-2001 | Beacon - Yellow
130 |  | BB-2001 | Beacon - Blue
131 | RD-7P-3-LFA | HN-3001 | Horn | MC- | JBF-D-HN-3001 | JBF-D-HN-3001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 270 | M32
132 |  | BR-3001 | Beacon - Red
133 |  | BY-3001 | Beacon - Yellow
134 |  | BB-3001 | Beacon - Blue
135 | RD-7P-3-LFA | HN-4002 | Horn | MC- | JBF-D-HN-4002 | JBF-D-HN-4002 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 300 | M32
136 |  | BR-4002 | Beacon - Red
137 |  | BY-4002 | Beacon - Yellow
138 |  | BB-4002 | Beacon - Blue
139 | RD-7P-3-LFA | HN-4001 | Horn | MC- | JBF-D-HN-4001 | JBF-D-HN-4001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 420 | M32
140 |  | BR-4001 | Beacon - Red
141 |  | BY-4001 | Beacon - Yellow
142 |  | BB-4001 | Beacon - Blue
143 | RD-7P-3-LFA | HN-5001 | Horn | MC- | JBF-D-HN-5001 | JBF-D-HN-5001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 400 | M32
144 |  | BR-5001 | Beacon - Red
145 |  | BY-5001 | Beacon - Yellow
146 |  | BB-5001 | Beacon - Blue
147 | RD-7P-3-LFA | HN-6001 | Horn | MC- | JBF-D-HN-6001 | JBF-D-HN-6001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 420 | M32
148 |  | BR-6001 | Beacon - Red
149 |  | BY-6001 | Beacon - Yellow
150 |  | BB-6001 | Beacon - Blue
151 | RD-7P-3-LFA | HN-7001 | Horn | MC- | JBF-D-HN-7001 | JBF-D-HN-7001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 430 | M32
152 |  | BR-7001 | Beacon - Red
153 |  | BY-7001 | Beacon - Yellow
154 |  | BB-7001 | Beacon - Blue
155 | RD-7P-3-LFA | HN-8001 | Horn | MC- | JBF-D-HN-8001 | JBF-D-HN-8001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 270 | M32
156 |  | BR-8001 | Beacon - Red
157 |  | BY-8001 | Beacon - Yellow
158 |  | BB-8001 | Beacon - Blue
159 | RD-7P-3-LFA | HN-9001 | Horn | MC- | JBF-D-HN-9001 | JBF-D-HN-9001 (By vendor) | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 150 | M32
160 |  | BR-9001 | Beacon - Red
161 |  | BY-9001 | Beacon - Yellow
162 |  | BB-9001 | Beacon - Blue
163 | RD-7P-1-LFA | HSS-2301B | Pump Start Command | MC- | LCP-P-2301B | LCP-P-2301B | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 280 | M32
164 |  | XM-2301B | Pump Auto/Manual Status |  |  | Fire Water Network | [15 empty] | Rename
165 |  | XR-2301B | Pump Running/ Stopped Status
166 |  | XF-2301B | Pump Fault Status
167 |  | PAL-2301B | Low Pressure Alarm
168 | RD-7P-1-LFA | HSS-2302A | Pump Start Command | MC- | LCP-P-2302A | LCP-P-2302A | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 280 | M32
169 |  | XM-2302A | Pump Auto/Manual Status |  |  | Fire Water Network | [15 empty] | Rename
170 |  | XR-2302A | Pump Running/ Stopped Status
171 |  | XF-2302A | Pump Fault Status
172 |  | PALL-2302A | Low Low Pressure Alarm | [18 empty] | Rename
173 | RD-7P-1-LFA | HSS-2302B | Pump Start Command | MC- | LCP-P-2302B | LCP-P-2302B | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Red | NOTE 3 | 300/500 V | 230 | M32
174 |  | XM-2302B | Pump Auto/Manual Status |  |  | Fire Water Network | [15 empty] | Rename
175 |  | XR-2302B | Pump Running/ Stopped Status
176 |  | XF-2302B | Pump Fault Status
177 |  | PALL-2302B | Low Low Pressure Alarm | [18 empty] | Rename
178 | RD-1P-2-FA | MAC-9001 | Manual Call Point | IC- | MAC-9001 | MAC-9001 | MAC-9001 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 150 | M20 | Direct
179 | RD-1P-2-FA | PT-2301 | Pressure Transmitter | IC- | PT-2301 | PT-2301 | PT-2301 | FGS | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 220 | M20 | Added-Direct
180 | RD-1T-2-FA | FD-8001 | Flame Detector | IC- | FD-8001 | FD-8001 | FD-8001 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 250 | M20 | Added-Direct
181 | RD-1T-2-FA | FD-8002 | Flame Detector | IC- | FD-8002 | FD-8002 | FD-8001 | FGS | FRS | SWA | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 100 | M20 | Added-Direct
182 | - | [6 empty] | FOR BUILDING | [11 empty] | -
183 | RD-1T-2-F | FGD-1101 | Flammable Gas Detector | IC- | FGD-1101 | FGD-1101 | JBF-A-2115 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
184 | RD-1T-2-F | FGD-1102 | Flammable Gas Detector | IC- | FGD-1102 | FGD-1102 | JBF-A-2115 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
185 | RD-1T-2-F | FGD-1103 | Flammable Gas Detector | IC- | FGD-1103 | FGD-1103 | JBF-A-2115 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
186 | RD-1T-2-F | TGD-1101 | Toxic Gas Detector | IC- | TGD-1101 | TGD-1101 | JBF-A-2115 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
187 | RD-1T-2-F | TGD-1102 | Toxic Gas Detector | IC- | TGD-1102 | TGD-1102 | JBF-A-2115 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
188 | RD-1T-2-F | TGD-1103 | Toxic Gas Detector | IC- | TGD-1103 | TGD-1103 | JBF-A-2115 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
189 | RD-12T-1-FA | JBF-A-2115 | Junction Box (Control Building- west) Unclassified | MC- | JBF-A-2115 | JBF-A-2115 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | - | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 100 | M40 | unclassified
190 | RD-1T-2-F | FGD-1201 | Flammable Gas Detector | IC- | FGD-1201 | FGD-1201 | JBF-A-2116 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
191 | RD-1T-2-F | FGD-1202 | Flammable Gas Detector | IC- | FGD-1202 | FGD-1202 | JBF-A-2116 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
192 | RD-1T-2-F | FGD-1203 | Flammable Gas Detector | IC- | FGD-1203 | FGD-1203 | JBF-A-2116 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
193 | RD-1T-2-F | TGD-1201 | Toxic Gas Detector | IC- | TGD-1201 | TGD-1201 | JBF-A-2116 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
194 | RD-1T-2-F | TGD-1202 | Toxic Gas Detector | IC- | TGD-1202 | TGD-1202 | JBF-A-2116 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
195 | RD-1T-2-F | TGD-1203 | Toxic Gas Detector | IC- | TGD-1203 | TGD-1203 | JBF-A-2116 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
196 | RD-12T-1-FA | JBF-A-2116 | Junction Box (Electrical Building- East) Unclassified | MC- | JBF-A-2116 | JBF-A-2116 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | - | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 150 | M40
197 | RD-1T-2-F | HGD-1101 | Hydrogen Gas Detector | IC- | HGD-1101 | HGD-1101 | JBF-A-2117 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
198 | RD-1T-2-F | HGD-1102 | Hydrogen Gas Detector | IC- | HGD-1102 | HGD-1102 | JBF-A-2117 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
199 | RD-12T-1-FA | JBF-A-2117 | Junction Box (Control Building- Buttery Room) Unclassified | MC- | JBF-A-2117 | JBF-A-2117 | FGS | FGS | FRS | SWA | NIS | 12 | Triad | 1 | - | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M40
200 | RD-1P-2-F | HD-1101 | Heat Detector | IC- | HD-1101 | HD-1101 | JBF-D-2107 | FGS | FRS | - | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
201 | RD-1P-2-F | HD-1102 | Heat Detector | IC- | HD-1102 | HD-1102 | JBF-D-2107 | FGS | FRS | - | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 25 | M20
202 | RD-1P-2-F | MAC-1101 | Manual Call Point | IC- | MAC-1101 | MAC-1101 | JBF-D-2107 | FGS | FRS | - | NIS | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 25 | M20
203 | RD-7P-1-FA | JBF-D-2107 | Junction Box (Control Building- Buttery Room) Unclassified | MC- | JBF-D-2107 | JBF-D-2107 | FGS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32
204 | - | HGD-1103 | Hydrogen Gas Detector | IC- | HGD-1103 | HGD-1103 | JBF-A-2114 | FGS | FRS | - | NIS | 1 | Triad | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | Deleted
205 | - | HD-1103 | Heat Detector | IC- | HD-1103 | HD-1103 | FGS | FGS | FRS | - | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | Deleted
206 | - | HD-1104 | Heat Detector | IC- | HD-1104 | HD-1104 | FGS | FGS | FRS | - | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | Deleted
207 | - | [6 empty] | SIGNALS BETWEEN F&G AND ESD SYSTEM & OTHER SYSTEMS | [11 empty] | -
208 | GR-7P-1-F | ESDR 0-F&G | CONFIRMED FLAMMABLE GAS IN HVAC INTAKE (COMMAND FROM FGS) | MC- | FGS-ESD | FGS | ESD | FGS | FRS | - | NIS | 7 | PAIR | 1 | - | Overall Screen | Grey / Red Strip | NOTE 3 | 300/500 V | - | M32 |  | طوب این کابل در بخش ESD دیده شده است
209 |  | ESDR 1A-F&G | CONFIRMED FLAMMABLE GAS IN PROCESS AREA (COMMAND FROM FGS)
210 |  | ESD 1A-F&G | CONFIRMED FIRE IN FIRE ZONE (PROCESS) AREA (COMMAND FROM F&G)
211 |  | ESD2A-FG-1101B | ESD 2A(Train B) Request
212 |  | ESD2A-FG-1101C | ESD 2A(Train C) Request
213 | RD-7P-1-FA | INB-FG-1101 | Inhibit to Boost for UPS Charger 1 | MC- | UPS-F&G | FGS | UPS | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 140 | M32 | added
214 |  | INB-FG-1102 | Inhibit to Boost for UPS Charger 2
215 |  | INB-FG-1103 | Inhibit to Boost for UPS Charger 3
216 |  | PISO-FG-1101 | Power Isolation of Battery Bank 1
217 |  | PISO-FG-1102 | Power Isolation of Battery Bank 2
218 |  | PISO-FG-1103 | Power Isolation of Battery Bank 3
219 | RD-7P-1-FA | HVAC-FG-G-1101 | Control building HVAC shut down & damper closed for gas detection | MC- | HVAC-F&G | F&G | HAVC | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | added
220 |  | HVAC-FG-F-1101 | Control building HVAC shut down & damper closed for fire detection
221 | RD-7P-1-FA | DAMP-FG-1101 | Battery Room Damper1 closed | MC- | IRP-FGS 1 | FGS | IRP | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 140 | M32 | added
222 |  | DAMP-FG-1102 | Battery Room Damper 2 closed
223 |  | DAMP-FG-G-1101 | Electrical building air intake damper closed for gas detection
224 |  | FAN-FG-1101 | Battery Room stand by Fan Activation Command
225 | RD-7P-1-FA | HSS-2301A | Pump Start Command | MC- | IRP-FGS 2 | FGS | IRP | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 140 | M32 | added
226 |  | XM-2301A | Pump Auto/Manual Status
227 |  | XR-2301A | Pump Running/ Stopped Status
228 |  | XF-2301A | Pump Fault Status
229 |  | PAL-2301A | Low Pressure Alarm
230 | RD-19P-1-F | Ex-FG-G-1101 | FGS System confirmed Gas Alarm to Existing FGS | MC- | EX FGS-FGS | FGS | EXISTING FGS | FGS | FRS | - | NIS | 19 | PAIR | 1 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32
231 |  | Ex-FG-F-1101 | FGS System confirmed Fire Alarm to Existing FGS System
232 |  | Ex-FG-G-1102 | Existing FGS confirmed Gas Alarm to FGS System
233 |  | Ex-FG-F-1102 | Existing FGS confirmed Fire Alarm to FGS System
234 | RD-7P-1-FA | XA-CO2-1101 | MANUAL/AUTO SELECTOR SWITCH STATUS (FOR PROTECTED AREA) | MC- | CO2-F&G | CO2-F&G | CO2 PACKAGE | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | - | Overall Screen | Red | NOTE 3 | 300/500 V | 140 | M32
235 |  | XRE-CO2-1101 | RELEASED STATUS (FOR PROTECTED AREA)
236 |  | XI-CO2-1101 | INHIBIT STATUS (FOR PROTECTED AREA)
237 |  | XF-CO2-1101 | GENERAL FAULT
238 |  | HS-CO2-1101 | AUTOMAT RELEASE COMMAND (FOR PROTECTED AREA)
239 | - | [6 empty] | SIGNALS TO F&G Matrix PANEL | [11 empty] | -
240 | RD-19P-1-F | LP-AR1-FD | Fire Alarm For Area 1 Lamp | MC- | MXT-F&G 1 | F&G | FGS Matrix | FGS | FRS | - | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | Rename
241 |  | LP-AR1-FGD | Flammable Gas Alarm For Area 1 Lamp | [18 empty] | Rename
242 |  | LP-AR1-TGD | Toxic Gas Alarm For Area 1 Lamp | [18 empty] | Rename
243 |  | LP-AR2-FD | Fire Alarm For Area 2 Lamp | [18 empty] | Rename
244 |  | LP-AR2-FGD | FlammableGas Alarm For Area 2 Lamp | [18 empty] | Rename
245 |  | LP-AR2-TGD | Toxic Gas Alarm For Area 2 Lamp | [18 empty] | Rename
246 |  | LP-AR3-FD | Fire Alarm For Area 3 Lamp | [18 empty] | Rename
247 |  | LP-AR4A-FD | Fire Alarm For Area 4A Lamp | [18 empty] | Rename
248 |  | LP-AR4A-FGD | FlammableGas Alarm For Area 4 A Lamp | [18 empty] | Rename
249 |  | LP-AR4A-TGD | Toxic Gas Alarm For Area 4A Lamp | [18 empty] | Rename
250 |  | LP-AR4B-FD | Fire Alarm For Area 4B Lamp | [18 empty] | Rename
251 |  | LP-AR4B-FGD | FlammableGas Alarm For Area 4 B Lamp | [18 empty] | Rename
252 |  | LP-AR4B-TGD | Toxic Gas Alarm For Area 4B Lamp | [18 empty] | Rename
253 |  | LP-AR4C-FD | Fire Alarm For Area 4C Lamp | [18 empty] | Rename
254 | RD-19P-1-F | LP-AR4C-FGD | FlammableGas Alarm For Area 4C Lamp | MC- | MXT-F&G 2 | F&G | FGS Matrix | FGS | FRS | - | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | Rename
255 |  | LP-AR4C-TGD | Toxic Gas Alarm For Area 4C Lamp | [18 empty] | Rename
256 |  | LP-AR5-FD | Fire Alarm For Area 5 Lamp | [18 empty] | Rename
257 |  | LP-AR5-FGD | FlammableGas Alarm For Area 5 Lamp | [18 empty] | Rename
258 |  | LP-AR5-TGD | Toxic Gas Alarm For Area 5 Lamp | [18 empty] | Rename
259 |  | LP-AR6-FD | Fire Alarm For Area 6 Lamp | [18 empty] | Rename
260 |  | LP-AR6-FGD | FlammableGas Alarm For Area 6 Lamp | [18 empty] | Rename
261 |  | LP-AR6-TGD | Toxic Gas Alarm For Area 6 Lamp | [18 empty] | Rename
262 |  | LP-AR7-FD | Fire Alarm For Area 7 Lamp | [18 empty] | Rename
263 |  | LP-AR7-FGD | FlammableGas Alarm For Area 7 Lamp | [18 empty] | Rename
264 |  | LP-AR7-TGD | Toxic Gas Alarm For Area 7 Lamp | [18 empty] | Rename
265 |  | LP-AR8-FD | Fire Alarm For Area 8 Lamp | [18 empty] | Rename
266 |  | LP-AR9-FD | Fire Alarm For Area 9 Lamp | [18 empty] | Rename
267 |  | LP-CB-FD | Fire Alarm For Control Building Lamp | [18 empty] | Rename
268 | RD-19P-1-F | LP-CB-FGD | FlammableGas Alarm For Control Building Lamp | MC- | MXT-F&G 3 | F&G | FGS Matrix | FGS | FRS | - | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | Rename
269 |  | LP-CB-TGD | Toxic Gas Alarm For Control Building Lamp | [18 empty] | Rename
270 |  | LP-EB-FD | Fire Alarm For Electrical Building Lamp | [18 empty] | Rename
271 |  | LP-EB-FGD | FlammableGas Alarm For Electrical Building Lamp | [18 empty] | Rename
272 |  | LP-EB-TGD | Toxic Gas Alarm For Electrical Building Lamp | [18 empty] | Rename
273 |  | LP-PSH-2302 | Deluge Valve 2302 Opened Lamp | [18 empty] | Rename
274 |  | LP-PSH-2303 | Deluge Valve 2303 Opened Lamp | [18 empty] | Rename
275 |  | LP-PSH-2304 | Deluge Valve 2304 Opened Lamp | [18 empty] | Rename
276 |  | LP-PSH-2301 | Deluge Valve 2301 Opened Lamp | [18 empty] | Rename
277 |  | LP-P-2301B | Diesel Pump Status Lamp | [18 empty] | Rename
278 |  | LP-P-2301A | Electrical Pump Status Lamp | [18 empty] | Rename
279 |  | LP-CO2-RE | CO2 Release Status Lamp | [18 empty] | Rename
280 |  | PB-DV-2302 | Deluge Valve 2302 Open Command Push button | [18 empty] | Rename
281 |  | PB-DV-2303 | Deluge Valve 2303 Open Command Push button | [18 empty] | Rename
282 | RD-19P-1-F | PB-DV-2304 | Deluge Valve 2304 Open Command Push button | MC- | MXT-F&G 4 | F&G | FGS Matrix | FGS | FRS | - | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | Rename
283 |  | PB-DV-2301 | Deluge Valve 2301 Open Command Push button | [18 empty] | Rename
284 |  | PB-P-2301B | Diesel Pump Start Command Push button | [18 empty] | Rename
285 |  | PB-P-2301A | Electrical Pump Start Command Push button | [18 empty] | Rename
286 |  | PB-CO2-CO | CO2 Release Command Push button | [18 empty] | Rename
287 |  | PB-RST | RESET Push button | [18 empty] | Rename
288 |  | PB-ACK-HO | ACK HORN Push button | [18 empty] | Rename
289 |  | PB-ACK | ACK Push button | [18 empty] | Rename
290 |  | PB-INHIBIT | Inhibit to maitenance Push button | [18 empty] | Rename
291 |  | LP-INHIBIT | Inhibit to maitenance Lamp | [18 empty] | Rename
292 |  | BUZZER | Audible Alarm | [18 empty] | Rename
293 | - | [6 empty] | FOR BUILDING ( FACP ) | [11 empty] | -
294 | RD-1P-2-FA | FACP-LOOP1 | Output Port of Loop 1 (Extension of Control Building) | IC- | FACP-LOOP1 | FACP | MAC-1102 | FGS | FRS | SWA | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 50 | M20
295 | RD-1P-2-F | SD-1104 | Smoke Detector | IC- | SD-1104 | MAC-1102 | SD-1104 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
296 | RD-1P-2-F | SD-1103 | Smoke Detector | IC- | SD-1103 | SD-1104 | SD-1103 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
297 | RD-1P-2-F | MAC-1103 | Manual Call Point | IC- | MAC-1103 | SD-1103 | MAC-1103 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
298 | RD-1P-2-F | SD-1102 | Smoke Detector | IC- | SD-1102 | MAC-1103 | SD-1102 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
299 | RD-1P-2-F | SD-1101 | Smoke Detector | IC- | SD-1101 | SD-1102 | SD-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
300 | RD-1P-2-F | SD-1121 | Smoke Detector | IC- | SD-1121 | SD-1101 | SD-1121 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
301 | RD-1P-2-F | SD-1122 | Smoke Detector | IC- | SD-1122 | SD-1121 | SD-1122 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
302 | RD-1P-2-F | SD-1123 | Smoke Detector | IC- | SD-1123 | SD-1122 | SD-1123 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
303 | RD-1P-2-F | SD-1124 | Smoke Detector | IC- | SD-1124 | SD-1123 | SD-1124 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
304 | RD-1P-2-F | SD-1135 | Smoke Detector | IC- | SD-1135 | SD-1124 | SD-1135 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
305 | RD-1P-2-F | SD-1136 | Smoke Detector | IC- | SD-1136 | SD-1135 | SD-1136 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
306 | RD-1P-2-F | SD-1128 | Smoke Detector | IC- | SD-1128 | SD-1136 | SD-1128 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
307 | RD-1P-2-F | SD-1126 | Smoke Detector | IC- | SD-1126 | SD-1128 | SD-1126 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
308 | RD-1P-2-F | SD-1108 | Smoke Detector | IC- | SD-1108 | SD-1126 | SD-1108 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
309 | RD-1P-2-F | SD-1110 | Smoke Detector | IC- | SD-1110 | SD-1108 | SD-1110 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
310 | RD-1P-2-F | SD-1112 | Smoke Detector | IC- | SD-1112 | SD-1110 | SD-1112 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
311 | RD-1P-2-F | SD-1114 | Smoke Detector | IC- | SD-1114 | SD-1112 | SD-1114 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
312 | RD-1P-2-F | SD-1115 | Smoke Detector | IC- | SD-1115 | SD-1114 | SD-1115 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
313 | RD-1P-2-F | MAC-1104 | Manual Call Point | IC- | MAC-1104 | SD-1115 | MAC-1104 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
314 | RD-1P-2-F | BL-1101 | Bell | IC- | BL-1101 | MAC-1104 | BL-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
315 | RD-1P-2-F | BR-1103 | Beacon - Red | IC- | BR-1103 | BL-1101 | BR-1103 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
316 | RD-1P-2-F | MAC-1105 | Manual Call Point | IC- | MAC-1105 | BR-1103 | MAC-1105 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
317 | RD-1P-2-F | SD-1118 | Smoke Detector | IC- | SD-1118 | MAC-1105 | SD-1118 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
318 | RD-1P-2-F | SD-1120 | Smoke Detector | IC- | SD-1120 | SD-1118 | SD-1120 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
319 | RD-1P-2-F | HN-1101 | Horn | IC- | HN-1101 | SD-1120 | HN-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
320 | RD-1P-2-F | BR-1101 | Beacon - Red | IC- | BR-1101 | HN-1101 | BR-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
321 | RD-1P-2-F | BB-1101 | Beacon - Blue | IC- | BB-1101 | BR-1101 | BB-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
322 | RD-1P-2-F | BY-1101 | Beacon - Yellow | IC- | BY-1101 | BB-1101 | BY-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
323 | - | HN-1102 | Horn | IC- | HN-1102 | HN-1102 | BR-1102 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
324 | - | BR-1102 | Beacon - Red | IC- | BR-1102 | BR-1102 | BB-1102 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
325 | - | BB-1102 | Beacon - Blue | IC- | BB-1102 | BB-1102 | BY-1102 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
326 | - | BY-1102 | Beacon - Yellow | IC- | BY-1102 | BY-1102 | MAC-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
327 | RD-1P-2-FA | FACP-LOOP2 | Output Port of Loop 2 (Extension of Control Building-False Floor) | IC- | FACP-LOOP2 | FACP | SD-1105 | FGS | FRS | SWA | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 50 | M20
328 | RD-1P-2-F | SD-1106 | Smoke Detector | IC- | SD-1106 | SD-1105 | SD-1106 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
329 | RD-1P-2-F | SD-1130 | Smoke Detector | IC- | SD-1130 | SD-1106 | SD-1130 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
330 | RD-1P-2-F | SD-1131 | Smoke Detector | IC- | SD-1131 | SD-1130 | SD-1131 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
331 | RD-1P-2-F | SD-1132 | Smoke Detector | IC- | SD-1132 | SD-1131 | SD-1132 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
332 | RD-1P-2-F | SD-1129 | Smoke Detector | IC- | SD-1129 | SD-1132 | SD-1129 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
333 | RD-1P-2-F | SD-1134 | Smoke Detector | IC- | SD-1134 | SD-1129 | SD-1134 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
334 | RD-1P-2-F | SD-1133 | Smoke Detector | IC- | SD-1133 | SD-1134 | SD-1133 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
335 | RD-1P-2-F | SD-1127 | Smoke Detector | IC- | SD-1127 | SD-1133 | SD-1127 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
336 | RD-1P-2-FA | FACP-LOOP3 | Output Port of Loop 3 (Control Building-False Ceiling) | IC- | FACP-LOOP3 | FACP | SD-1107 | FGS | FRS | SWA | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 50 | M20
337 | RD-1P-2-F | SD-1109 | Smoke Detector | IC- | SD-1109 | SD-1107 | SD-1109 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
338 | RD-1P-2-F | SD-1111 | Smoke Detector | IC- | SD-1111 | SD-1109 | SD-1111 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
339 | RD-1P-2-F | SD-1113 | Smoke Detector | IC- | SD-1113 | SD-1111 | SD-1113 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
340 | RD-1P-2-F | SD-1116 | Smoke Detector | IC- | SD-1116 | SD-1113 | SD-1116 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
341 | RD-1P-2-F | SD-1117 | Smoke Detector | IC- | SD-1117 | SD-1116 | SD-1117 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
342 | RD-1P-2-F | SD-1119 | Smoke Detector | IC- | SD-1119 | SD-1117 | SD-1119 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
343 | RD-1P-2-FA | FACP-LOOP4 | Output Port of Loop 4 (Extension of Existing Elect. Building) | IC- | FACP-LOOP4 | FACP | HN-1201 | FGS | FRS | SWA | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 100 | M20
344 | RD-1P-2-F | BR-1201 | Beacon - Red | IC- | BR-1201 | HN-1201 | BR-1201 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
345 | RD-1P-2-F | BB-1201 | Beacon - Blue | IC- | BB-1201 | BR-1201 | BB-1201 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
346 | RD-1P-2-F | BY-1201 | Beacon - Yellow | IC- | BY-1201 | BB-1201 | BY-1201 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
347 | RD-1P-2-F | MAC-1201 | Manual Call Point | IC- | MAC-1201 | BY-1201 | MAC-1201 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
348 | RD-1P-2-F | SD-1201 | Smoke Detector | IC- | SD-1201 | MAC-1201 | SD-1201 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
349 | RD-1P-2-F | SD-1202 | Smoke Detector | IC- | SD-1202 | SD-1201 | SD-1202 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
350 | RD-1P-2-F | MAC-1202 | Manual Call Point | IC- | MAC-1202 | SD-1202 | MAC-1202 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
351 | RD-1P-2-FA | FACP-LOOP5 | Output Port of Loop 5 (Extension of Existing Elect. Building-False Floor) | IC- | FACP-LOOP5 | FACP | SD-1203 | FGS | FRS | SWA | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 100 | M20
352 | RD-1P-2-F | SD-1204 | Smoke Detector | IC- | SD-1204 | SD-1203 | SD-1204 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
353 | RD-1P-2-FA | FACP-LOOP6 | Output Port of Loop 6 (Extension of Existing Elect. Building) | IC- | FACP-LOOP6 | FACP | HN-1202 | FGS | FRS | SWA | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 100 | M20
354 | RD-1P-2-F | BR-1202 | Beacon - Red | IC- | BR-1202 | HN-1202 | BR-1202 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
355 | RD-1P-2-F | BB-1202 | Beacon - Blue | IC- | BB-1202 | BR-1202 | BB-1202 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
356 | RD-1P-2-F | BY-1202 | Beacon - Yellow | IC- | BY-1202 | BB-1202 | BY-1202 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
357 | RD-1P-2-F | MAC-1203 | Manual Call Point | IC- | MAC-1203 | BY-1202 | MAC-1203 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
358 | RD-1P-2-F | LHD-1201 | Linear Heat Detector | IC- | LHD-1201 | MAC-1203 | LHD-1201 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
359 | RD-1P-2-F | LHD-1202 | Linear Heat Detector | IC- | LHD-1202 | LHD-1201 | LHD-1202 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
360 | RD-1P-2-F | LHD-1203 | Linear Heat Detector | IC- | LHD-1203 | LHD-1202 | LHD-1203 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
361 | RD-1P-2-FA | FACP-LOOP7 | Output Port of Loop 7 (CCTV Control Room) | IC- | FACP-LOOP7 | FACP | SD-1301 | FGS | FRS | SWA | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 220 | M20
362 | RD-1P-2-F | SD-1302 | Smoke Detector | IC- | SD-1302 | SD-1301 | SD-1302 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
363 | RD-1P-2-F | MAC-1302 | Manual Call Point | IC- | MAC-1302 | SD-1302 | MAC-1302 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
364 | RD-1P-2-F | SD-1304 | Smoke Detector | IC- | SD-1304 | MAC-1302 | SD-1304 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
365 | RD-1P-2-F | SD-1303 | Smoke Detector | IC- | SD-1303 | SD-1304 | SD-1303 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
366 | RD-1P-2-F | HD-1301 | Heat Detector | IC- | HD-1301 | SD-1303 | HD-1301 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
367 | RD-1P-2-F | MAC-1301 | Manual Call Point | IC- | MAC-1301 | HD-1301 | MAC-1301 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
368 | RD-1P-2-F | HN-1301 | Horn | IC- | HN-1301 | MAC-1301 | HN-1301 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
369 | RD-1P-2-F | BR-1301 | Beacon - Red | IC- | BR-1301 | HN-1301 | BR-1301 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
370 | RD-1P-2-F | BB-1301 | Beacon - Blue | IC- | BB-1301 | BR-1301 | BB-1301 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
371 | RD-1P-2-F | BY-1301 | Beacon - Yellow | IC- | BY-1301 | BB-1301 | BY-1301 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20
372 | RD-1P-2-FA | FACP-LOOP8 | Output Port of Loop 8 (GCS Warehouse) | IC- | FACP-LOOP8 | FACP | SD-1401 | FGS | FRS | SWA | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 220 | M20
373 | RD-1P-2-F | SD-1402 | Smoke Detector | IC- | SD-1402 | SD-1401 | SD-1402 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
374 | RD-1P-2-F | SD-1403 | Smoke Detector | IC- | SD-1403 | SD-1402 | SD-1403 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
375 | RD-1P-2-F | MAC-1401 | Manual Call Point | IC- | MAC-1401 | SD-1403 | MAC-1401 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
376 | RD-1P-2-F | HN-1401 | Horn | IC- | HN-1401 | MAC-1401 | HN-1401 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
377 | RD-1P-2-F | BR-1401 | Beacon - Red | IC- | BR-1401 | HN-1401 | BR-1401 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
378 | RD-1P-2-F | BB-1401 | Beacon - Blue | IC- | BB-1401 | BR-1401 | BB-1401 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
379 | RD-1P-2-F | BY-1401 | Beacon - Yellow | IC- | BY-1401 | BB-1401 | BY-1401 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | 10 | M20 | Added
380 | - | BR-1104 | Beacon - Red | IC- | BR-1104 | BR-1104 | BL-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
381 | - | MAC-1107 | Manual Call Point | IC- | MAC-1107 | MAC-1107 | HN-1101 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
382 | - | BY-1102 | Beacon - Yellow | IC- | BY-1102 | BY-1102 | SD-1115 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
383 | - | MAC-1108 | Manual Call Point | IC- | MAC-1108 | MAC-1108 | MAC-1109 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
384 | - | MAC-1109 | Manual Call Point | IC- | MAC-1109 | MAC-1109 | BR-1103 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
385 | - | BL-1102 | Bell | IC- | BL-1102 | BL-1102 | MAC-1103 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
386 | - | MAC-1106 | Manual Call Point | IC- | MAC-1106 | MAC-1106 | SD-1121 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
387 | - | SD-1181 | Smoke Detector | IC- | SD-1181 | SD-1181 | SD-1182 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
388 | - | SD-1182 | Smoke Detector | IC- | SD-1182 | SD-1182 | SD-1183 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
389 | - | SD-1183 | Smoke Detector | IC- | SD-1183 | SD-1183 | SD-1184 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
390 | - | SD-1184 | Smoke Detector | IC- | SD-1184 | SD-1184 | SD-1185 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
391 | - | SD-1185 | Smoke Detector | IC- | SD-1185 | SD-1185 | SD-1186 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
392 | - | SD-1186 | Smoke Detector | IC- | SD-1186 | SD-1186 | SD-1187 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
393 | - | SD-1187 | Smoke Detector | IC- | SD-1187 | SD-1187 | SD-1188 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
394 | - | SD-1188 | Smoke Detector | IC- | SD-1188 | SD-1188 | SD-1189 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
395 | - | SD-1189 | Smoke Detector | IC- | SD-1189 | SD-1189 | SD-1190 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
396 | - | SD-1190 | Smoke Detector | IC- | SD-1190 | SD-1190 | SD-1191 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
397 | - | SD-1191 | Smoke Detector | IC- | SD-1191 | SD-1191 | SD-1192 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
398 | - | SD-1192 | Smoke Detector | IC- | SD-1192 | SD-1192 | SD-1193 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
399 | - | SD-1193 | Smoke Detector | IC- | SD-1193 | SD-1193 | SD-1194 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
400 | - | SD-1194 | Smoke Detector | IC- | SD-1194 | SD-1194 | SD-1195 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
401 | - | SD-1195 | Smoke Detector | IC- | SD-1195 | SD-1195 | SD-1196 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
402 | - | SD-1196 | Smoke Detector | IC- | SD-1196 | SD-1196 | SD-1197 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
403 | - | SD-1197 | Smoke Detector | IC- | SD-1197 | SD-1197 | FACP | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
404 | - | SD-1150 | Smoke Detector | IC- | SD-1150 | SD-1150 | SD-1151 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
405 | - | SD-1151 | Smoke Detector | IC- | SD-1151 | SD-1151 | SD-1152 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
406 | - | SD-1152 | Smoke Detector | IC- | SD-1152 | SD-1152 | SD-1153 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
407 | - | SD-1153 | Smoke Detector | IC- | SD-1153 | SD-1153 | SD-1154 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
408 | - | SD-1154 | Smoke Detector | IC- | SD-1154 | SD-1154 | SD-1155 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
409 | - | SD-1155 | Smoke Detector | IC- | SD-1155 | SD-1155 | SD-1156 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
410 | - | SD-1156 | Smoke Detector | IC- | SD-1156 | SD-1156 | SD-1157 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
411 | - | SD-1157 | Smoke Detector | IC- | SD-1157 | SD-1157 | SD-1158 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
412 | - | SD-1158 | Smoke Detector | IC- | SD-1158 | SD-1158 | SD-1159 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
413 | - | SD-1159 | Smoke Detector | IC- | SD-1159 | SD-1159 | SD-1160 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
414 | - | SD-1160 | Smoke Detector | IC- | SD-1160 | SD-1160 | SD-1161 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
415 | - | SD-1161 | Smoke Detector | IC- | SD-1161 | SD-1161 | SD-1162 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
416 | - | SD-1162 | Smoke Detector | IC- | SD-1162 | SD-1162 | SD-1163 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
417 | - | SD-1163 | Smoke Detector | IC- | SD-1163 | SD-1163 | SD-1164 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
418 | - | SD-1164 | Smoke Detector | IC- | SD-1164 | SD-1164 | SD-1165 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
419 | - | SD-1165 | Smoke Detector | IC- | SD-1165 | SD-1165 | SD-1166 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
420 | - | SD-1166 | Smoke Detector | IC- | SD-1166 | SD-1166 | SD-1167 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
421 | - | SD-1167 | Smoke Detector | IC- | SD-1167 | SD-1167 | SD-1168 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
422 | - | SD-1168 | Smoke Detector | IC- | SD-1168 | SD-1168 | SD-1169 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
423 | - | SD-1169 | Smoke Detector | IC- | SD-1169 | SD-1169 | SD-1170 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
424 | - | SD-1170 | Smoke Detector | IC- | SD-1170 | SD-1170 | FACP | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
425 | - | MAC-1303 | Manual Call Point | IC- | MAC-1303 | MAC-1303 | #REF! | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
426 | - | SD-1305 | Smoke Detector | IC- | SD-1305 | SD-1305 | SD-1306 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
427 | - | SD-1306 | Smoke Detector | IC- | SD-1306 | SD-1306 | SD-1307 | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
428 | - | SD-1307 | Smoke Detector | IC- | SD-1307 | SD-1307 | FACP | FGS | FRS | - | - | 1 | Pair | 1.5 | - | Overall Screen | Red | Note 3 | 300/500 V | - | M20 | Deleted
D04
TOTALLY REVIZED

## Cable list (UCP GAS Comp)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 |  | IN |  | LI | 0009 |  | D04
INSTRUMENT CABLE LIST FOR UCP-GC-2101A/B/C SYSTEM ( GAS COMPRESSOR PACKAGE)
ITEM | Cable Code | Tag No. | Description | Cable No. |  | From | To. | SYSTEM | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | Lead Cover | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | 40 | GLAND SIZE | Remark
1 | BL-1P-2-A | FIT-2121A | Flow Transmitter | IC- | FIT-2121A | FIT-2121A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
2 | BL-1P-2-A | TIT-2122A | Temperature Transmitter | IC- | TIT-2122A | TIT-2122A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
3 | BL-1P-2-A | PDIT-2122A | Diff. Pressure Transmitter | IC- | PDIT-2122A | PDIT-2122A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
4 | BL-1P-2-A | PIT-2123A | Pressure Transmitter | IC- | PIT-2123A | PIT-2123A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
5 | BL-1P-2-A | TIT-2123A | Temperature Transmitter | IC- | TIT-2123A | TIT-2123A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
6 | BL-1P-2-A | PIT-2124A | Pressure Transmitter | IC- | PIT-2124A | PIT-2124A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
7 | BL-1P-2-A | FIT-2131A | Flow Transmitter | IC- | FIT-2131A | FIT-2131A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
8 | BL-1P-2-A | TIT-2132A | Temperature Transmitter | IC- | TIT-2132A | TIT-2132A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
9 | BL-1P-2-A | PIT-2132A | Pressure Transmitter | IC- | PIT-2132A | PIT-2132A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
10 | BL-1P-2-A | PDIT-2132A | Diff. Pressure Transmitter | IC- | PDIT-2132A | PDIT-2132A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
11 | BL-1P-2-A | TIT-2133A | Temperature Transmitter | IC- | TIT-2133A | TIT-2133A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
12 | BL-1P-2-A | PIT-2133A | Pressure Transmitter | IC- | PIT-2133A | PIT-2133A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
13 | BL-1P-2-A | PV-2123A | Pressure Control Valve | IC- | PV-2123A | PV-2123A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
14 | BL-1P-2-A | PVZ-2123A | Positioner Transmitter | IC- | PVZ-2123A | PVZ-2123A | C-JBU-A-2105A | UCP-GC-2101A | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
15 | BL-19P-1-LA | C-JBU-A-2105A | Junction Box | MC- | C-JBU-A-2105A | C-JBU-A-2105A | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M50
16 | BL-1P-2-A | FIT-2121B | Flow Transmitter | IC- | FIT-2121B | FIT-2121B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | Hold | M20
17 | BL-1P-2-A | TIT-2122B | Temperature Transmitter | IC- | TIT-2122B | TIT-2122B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | Hold | M20
18 | BL-1P-2-A | PDIT-2122B | Diff. Pressure Transmitter | IC- | PDIT-2122B | PDIT-2122B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | Hold | M20
19 | BL-1P-2-A | PIT-2123B | Pressure Transmitter | IC- | PIT-2123B | PIT-2123B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
20 | BL-1P-2-A | TIT-2123B | Temperature Transmitter | IC- | TIT-2123B | TIT-2123B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
21 | BL-1P-2-A | PIT-2124B | Pressure Transmitter | IC- | PIT-2124B | PIT-2124B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
22 | BL-1P-2-A | FIT-2131B | Flow Transmitter | IC- | FIT-2131B | FIT-2131B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
23 | BL-1P-2-A | TIT-2132B | Temperature Transmitter | IC- | TIT-2132B | TIT-2132B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
24 | BL-1P-2-A | PIT-2132B | Pressure Transmitter | IC- | PIT-2132B | PIT-2132B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
25 | BL-1P-2-A | PDIT-2132B | Diff. Pressure Transmitter | IC- | PDIT-2132B | PDIT-2132B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
26 | BL-1P-2-A | TIT-2133B | Temperature Transmitter | IC- | TIT-2133B | TIT-2133B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
27 | BL-1P-2-A | PIT-2133B | Pressure Transmitter | IC- | PIT-2133B | PIT-2133B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
28 | BL-1P-2-A | PV-2123B | Pressure Control Valve | IC- | PV-2123B | PV-2123B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
29 | BL-1P-2-A | PVZ-2123B | Positioner Transmitter | IC- | PVZ-2123B | PVZ-2123B | C-JBU-A-2105B | UCP-GC-2101B | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
30 | BL-19P-1-LA | C-JBU-A-2105B | Junction Box | MC- | C-JBU-A-2105B | C-JBU-A-2105B | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 350 | M50
31 | BL-1P-2-A | FIT-2121C | Flow Transmitter | IC- | FIT-2121C | FIT-2121C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
32 | BL-1P-2-A | TIT-2122C | Temperature Transmitter | IC- | TIT-2122C | TIT-2122C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
33 | BL-1P-2-A | PDIT-2122C | Diff. Pressure Transmitter | IC- | PDIT-2122C | PDIT-2122C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
34 | BL-1P-2-A | PIT-2123C | Pressure Transmitter | IC- | PIT-2123C | PIT-2123C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
35 | BL-1P-2-A | TIT-2123C | Temperature Transmitter | IC- | TIT-2123C | TIT-2123C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
36 | BL-1P-2-A | PIT-2124C | Pressure Transmitter | IC- | PIT-2124C | PIT-2124C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
37 | BL-1P-2-A | FIT-2131C | Flow Transmitter | IC- | FIT-2131C | FIT-2131C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
38 | BL-1P-2-A | TIT-2132C | Temperature Transmitter | IC- | TIT-2132C | TIT-2132C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
39 | BL-1P-2-A | PIT-2132C | Pressure Transmitter | IC- | PIT-2132C | PIT-2132C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
40 | BL-1P-2-A | PDIT-2132C | Diff. Pressure Transmitter | IC- | PDIT-2132C | PDIT-2132C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
41 | BL-1P-2-A | TIT-2133C | Temperature Transmitter | IC- | TIT-2133C | TIT-2133C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
42 | BL-1P-2-A | PIT-2133C | Pressure Transmitter | IC- | PIT-2133C | PIT-2133C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
43 | BL-1P-2-A | PV-2123C | Pressure Control Valve | IC- | PV-2123C | PV-2123C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
44 | BL-1P-2-A | PVZ-2123C | Positioner Transmitter | IC- | PVZ-2123C | PVZ-2123C | C-JBU-A-2105C | UCP-GC-2101C | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 30 | M20
45 | BL-19P-1-LA | C-JBU-A-2105C | Junction Box | MC- | C-JBU-A-2105C | C-JBU-A-2105C | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 380 | M50
46 | - | PDI-2201 | Dif. Pressure Indicator Transmitter | IC- | PDI-2201 | PDI-2201 | C-JBU-A-2104 | UCP-PK-C-2203 | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | - | - | Deleted
47 | - | PDI-2202 | Dif. Pressure Indicator Transmitter | IC- | PDI-2202 | PDI-2202 | C-JBU-A-2104 | UCP-PK-C-2203 | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | - | - | Deleted
48 | - | AIA-2201 | Humidity Analyzer | IC- | AIA-2201 | AIA-2201 | C-JBU-A-2104 | UCP-PK-C-2203 | FRT | SWA | IS | 1 | PAIR | 1.5 | - | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | - | - | Deleted
49 | - | C-JBU-A-2104 | Junction Box | MC- | C-JBU-D-2104 | C-JBU-D-2104 | UCP-PK-C-2203 | UCP-PK-C-2203 | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | - | -
50 | GR-1P-2-FA | XZSC-2123A | Limit Switch Open | IC- | XZSC-2123A | XZSC-2123A | C-JBU-D-2103A | UCP-GC-2101A | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
51 | GR-1P-2-FA | XZSO-2123A | Limit Switch Close | IC- | XZSO-2123A | XZSO-2123A | C-JBU-D-2103A | UCP-GC-2101A | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
52 | GR-7P-1-LFA | C-JBU-D-2103A | Junction Box | MC- | C-JBU-D-2103A | C-JBU-D-2103A | UCP-GC-2101A | UCP-GC-2101A | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 330 | M40
53 | GR-1P-3-FA | PSOV-2123A | Solenoid Valve | IC- | PSOV-2123A | PSOV-2123A | UCP-GC-2101A | UCP-GC-2101A | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 350 | M20 | Direct
54 | GR-1P-2-FA | XZSO-2123B | Limit Switch Open | IC- | XZSO-2123B | XZSO-2123B | C-JBU-D-2103B | UCP-GC-2101B | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
55 | GR-1P-2-FA | XZSC-2123B | Limit Switch Close | IC- | XZSC-2123B | XZSC-2123B | C-JBU-D-2103B | UCP-GC-2101B | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
56 | GR-7P-1-LFA | C-JBU-D-2103B | Junction Box | MC- | C-JBU-D-2103B | C-JBU-D-2103B | UCP-GC-2101B | UCP-GC-2101B | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 350 | M40
57 | GR-1P-3-FA | PSOV-2123B | Solenoid Valve | IC- | PSOV-2123B | PSOV-2123B | UCP-GC-2101B | UCP-GC-2101B | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 380 | M20 | Direct
58 | GR-1P-2-FA | XZSO-2123C | Limit Switch Open | IC- | XZSO-2123C | XZSO-2123C | C-JBU-D-2103C | UCP-GC-2101C | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
59 | GR-1P-2-FA | XZSC-2123C | Limit Switch Close | IC- | XZSC-2123C | XZSC-2123C | C-JBU-D-2103C | UCP-GC-2101C | FRS | SWA | NIS | 1 | PAIR | 1.5 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 30 | M20
60 | GR-7P-1-LFA | C-JBU-D-2103C | Junction Box | MC- | C-JBU-D-2103C | C-JBU-D-2103C | UCP-GC-2101C | UCP-GC-2101C | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 380 | M40
61 | GR-1P-3-FA | PSOV-2123C | Solenoid Valve | IC- | PSOV-2123C | PSOV-2123C | UCP-GC-2101C | UCP-GC-2101C | FRS | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 420 | M20 | Direct
62 | - | PSOV-2134A | Solenoid Valve | IC- | PSOV-2134A | PSOV-2134A | C-JBU-S-2101 | UCP-GC-2101A | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | - | - | Deleted
63 | - | PSOV-2110 | Solenoid Valve | IC- | PSOV-2110 | PSOV-2110 | C-JBU-S-2101 | UCP-GC-2101A | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | - | - | Deleted
64 | - | PSOV-2134B | Solenoid Valve | IC- | PSOV-2134B | PSOV-2134B | C-JBU-S-2102 | UCP-GC-2101B | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | - | - | Deleted
65 | - | C-JBU-S-2102 | Junction Box | MC- | C-JBU-S-2102 | C-JBU-S-2102 | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Gray | NOTE 3 | 600/1000 V | - | - | Deleted
66 | - | PSOV-2134C | Solenoid Valve | IC- | PSOV-2134C | PSOV-2134C | C-JBU-S-2103 | UCP-GC-2101C | FRT | SWA | NIS | 1 | PAIR | 2.5 | - | Overall Screen | Gray | NOTE 3 | 600/1000 V | - | - | Deleted
67 | - | C-JBU-S-2103 | Junction Box | MC- | C-JBU-S-2103 | C-JBU-S-2103 | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 7 | PAIR | 2.5 | Yes | Overall Screen | Gray | NOTE 3 | 600/1000 V | - | - | Deleted
68 | - | [18 empty] | -
69 | BL-12P-1-LA | C-JBU-A-2101A | Junction Box (BY VENDOR) | MC- | C-JBU-A-2101A | C-JBU-A-2101A | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | IS | 12 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
70 | BL-7T-1-LA | C-JBU-A-2102A | Junction Box (BY VENDOR) | MC- | C-JBU-A-2102A | C-JBU-A-2102A | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | IS | 7 | Triad | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
71 | BR-19P-1-LFA | C-JBU-A-2103A | Junction Box (BY VENDOR) | MC- | C-JBU-A-2103A | C-JBU-A-2103A | UCP-GC-2101A | UCP-GC-2101A | FRS | SWA | IS | 19 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 330 | M50
72 | BL-12P-1-LA | C-JBU-A-2104A | Junction Box (BY VENDOR) | MC- | C-JBU-A-2104A | C-JBU-A-2104A | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | IS | 12 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
73 | GR-12P-3-LFA | C-JBU-S-2101A | Junction Box (BY VENDOR) | MC- | C-JBU-S-2101A | C-JBU-S-2101A | UCP-GC-2101A | UCP-GC-2101A | FRS | SWA | NIS | 12 | PAIR | 2.5 | YES | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 330 | M40
74 | GR-7P-1-LFA | C-JBU-D-2101A | Junction Box (BY VENDOR) | MC- | C-JBU-D-2101A | C-JBU-D-2101A | UCP-GC-2101A | UCP-GC-2101A | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 330 | M32
75 | GY-7P-1-LA | C-JBU-D-2102A | Junction Box (BY VENDOR) | MC- | C-JBU-D-2102A | C-JBU-D-2102A | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M32
76 | GY-19P-1-LA | LCP-2101A1 | - | MC- | LCP-2101A1 | LCP-2101A1 | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
77 | GY-19P-1-LA | LCP-2101A2 | - | MC- | LCP-2101A2 | LCP-2101A2 | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
78 | GY-19P-1-LA | LCP-2101A3 | - | MC- | LCP-2101A3 | LCP-2101A3 | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
79 | GY-19P-1-LA | LCP-2101A4 | - | MC- | LCP-2101A4 | LCP-2101A4 | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
80 | GY-19P-1-LA | LCP-2101A5 | - | MC- | LCP-2101A5 | LCP-2101A5 | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
81 | GY-19P-1-A | IRP-UCP-GS-2101A1 | - | MC- | IRP-UCP-GS-2101A1 | IRP | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
82 | GY-19P-1-A | IRP-UCP-GS-2101A2 | - | MC- | IRP-UCP-GS-2101A2 | IRP | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
83 | GY-19P-1-A | IRP-UCP-GS-2101A3 | - | MC- | IRP-UCP-GS-2101A.3 | IRP | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
84 | GY-19P-1-A | IRP-UCP-GS-2101A4 | - | MC- | IRP-UCP-GS-2101A4 | IRP | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
85 | GY-19P-1-A | IRP-UCP-GS-2101A5 | - | MC- | IRP-UCP-GS-2101A5 | IRP | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
86 | GR-19P-1-FA | IRP-UCP-GS-2101A6 | - | MC- | IRP-UCP-GS-2101A6 | IRP | UCP-GC-2101A | UCP-GC-2101A | FRS | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 140 | M50
87 | - | ESD-2101A | - | MC- | ESD-UCP-GC-2101A | ESD | UCP-GC-2101A | UCP-GC-2101A | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M40 |  | در بخش ESD این کابل دیده شده است
88 | - | DCS-2101A | - | MC- | DCS-UCP-GC-2101A | DCS | UCP-GC-2101A | UCP-GC-2101A | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M40 |  | در بخش DCS این کابل دیده شده است
89 | - | PI-2121A | - | MC- | PI-2121A | DCS | UCP-GC-2101A | UCP-GC-2101A | FRT | - | NIS | 1 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | SPILL BACK | در بخش DCS این کابل دیده شده است
90 | 12T*1.5mm2 | M-2101-A | - | MC- | M-2101-A | M-2101-A Motor Aux JB | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 12 | Triad | 1.5 | - | - | Black | NOTE 3 | - | 330 | M50 | by electrical
91 | 3*2.5 mm2 | II-2234A | - | MC- | II-2234A | MCC | II-2234A | UCP-GC-2101A | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
92 | 3*2.5 mm2 | II-2235A | - | MC- | II-2235A | MCC | II-2235A | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
93 | 3*2.5 mm2 | II-2236A | - | MC- | II-2236A | MCC | II-2236A | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
94 | 3*2.5 mm2 | II-2237A | - | MC- | II-2237A | MCC | II-2237A | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
95 | 3*2.5 mm2 | II-2238A | - | MC- | II-2238A | MCC | II-2238A | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
96 | 3*2.5 mm2 | II-2239A | - | MC- | II-2239A | MCC | II-2239A | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
97 | - | [18 empty] | -
98 | BL-12P-1-LA | C-JBU-A-2101B | Junction Box (BY VENDOR) | MC- | C-JBU-A-2101B | C-JBU-A-2101B | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | IS | 12 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
99 | BL-7T-1-LA | C-JBU-A-2102B | Junction Box (BY VENDOR) | MC- | C-JBU-A-2102B | C-JBU-A-2102B | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | IS | 7 | Triad | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
100 | BR-19P-1-LFA | C-JBU-A-2103B | Junction Box (BY VENDOR) | MC- | C-JBU-A-2103B | C-JBU-A-2103B | UCP-GC-2101B | UCP-GC-2101B | FRS | SWA | IS | 19 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 330 | M50
101 | BL-12P-1-LA | C-JBU-A-2104B | Junction Box (BY VENDOR) | MC- | C-JBU-A-2104B | C-JBU-A-2104B | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | IS | 12 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
102 | GR-12P-3-LFA | C-JBU-S-2101B | Junction Box (BY VENDOR) | MC- | C-JBU-S-2101B | C-JBU-S-2101B | UCP-GC-2101B | UCP-GC-2101B | FRS | SWA | NIS | 12 | PAIR | 2.5 | YES | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 330 | M40
103 | GR-7P-1-LFA | C-JBU-D-2101B | Junction Box (BY VENDOR) | MC- | C-JBU-D-2101B | C-JBU-D-2101B | UCP-GC-2101B | UCP-GC-2101B | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 330 | M32
104 | GY-7P-1-LA | C-JBU-D-2102B | Junction Box (BY VENDOR) | MC- | C-JBU-D-2102B | C-JBU-D-2102B | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M32
105 | GY-19P-1-LA | LCP-2101B1 | - | MC- | LCP-2101B1 | LCP-2101B1 | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
106 | GY-19P-1-LA | LCP-2101B2 | - | MC- | LCP-2101B2 | LCP-2101B2 | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
107 | GY-19P-1-LA | LCP-2101B3 | - | MC- | LCP-2101B3 | LCP-2101B3 | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
108 | GY-19P-1-LA | LCP-2101B4 | - | MC- | LCP-2101B4 | LCP-2101B4 | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
109 | GY-19P-1-LA | LCP-2101B5 | - | MC- | LCP-2101B5 | LCP-2101B5 | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
110 | GY-19P-1-A | IRP-UCP-GS-2101B1 | - | MC- | IRP-UCP-GS-2101B1 | IRP | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
111 | GY-19P-1-A | IRP-UCP-GS-2101B2 | - | MC- | IRP-UCP-GS-2101B2 | IRP | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
112 | GY-19P-1-A | IRP-UCP-GS-2101B3 | - | MC- | IRP-UCP-GS-2101B3 | IRP | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
113 | GY-19P-1-A | IRP-UCP-GS-2101B4 | - | MC- | IRP-UCP-GS-2101B4 | IRP | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
114 | GY-19P-1-A | IRP-UCP-GS-2101B5 | - | MC- | IRP-UCP-GS-2101B5 | IRP | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
115 | GR-19P-1-FA | IRP-UCP-GS-2101B6 | - | MC- | IRP-UCP-GS-2101B6 | IRP | UCP-GC-2101B | UCP-GC-2101B | FRS | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 140 | M50
116 | - | ESD-2101B | - | MC- | ESD-UCP-GC-2101B | ESD | UCP-GC-2101B | UCP-GC-2101B | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M40 |  | در بخش ESD این کابل دیده شده است
117 | - | DCS-2101B | - | MC- | DCS-UCP-GC-2101B | DCS | UCP-GC-2101B | UCP-GC-2101B | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M40 |  | در بخش DCS این کابل دیده شده است
118 | - | PI-2121B | - | MC- | PI-2121B | DCS | UCP-GC-2101B | UCP-GC-2101B | FRT | - | NIS | 1 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | SPILL BACK | در بخش DCS این کابل دیده شده است
119 | 12T*1.5mm2 | M-2101-B | - | MC- | M-2101-B | M-2101-B Motor Aux JB | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 12 | Triad | 1.5 | - | - | Black | NOTE 3 | - | 330 | M50 | by electrical
120 | 3*2.5 mm2 | II-2234B | - | MC- | II-2234B | MCC | II-2234B | UCP-GC-2101B | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
121 | 3*2.5 mm2 | II-2235B | - | MC- | II-2235B | MCC | II-2235B | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
122 | 3*2.5 mm2 | II-2236B | - | MC- | II-2236B | MCC | II-2236B | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
123 | 3*2.5 mm2 | II-2237B | - | MC- | II-2237B | MCC | II-2237B | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
124 | 3*2.5 mm2 | II-2238B | - | MC- | II-2238B | MCC | II-2238B | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
125 | 3*2.5 mm2 | II-2239B | - | MC- | II-2239B | MCC | II-2239B | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
126 | - | [18 empty] | -
127 | BL-12P-1-LA | C-JBU-A-2101C | Junction Box (BY VENDOR) | MC- | C-JBU-A-2101C | C-JBU-A-2101C | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | IS | 12 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
128 | BL-7T-1-LA | C-JBU-A-2102C | Junction Box (BY VENDOR) | MC- | C-JBU-A-2102C | C-JBU-A-2102C | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | IS | 7 | Triad | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
129 | BR-19P-1-LFA | C-JBU-A-2103C | Junction Box (BY VENDOR) | MC- | C-JBU-A-2103C | C-JBU-A-2103C | UCP-GC-2101C | UCP-GC-2101C | FRS | SWA | IS | 19 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 330 | M50
130 | BL-12P-1-LA | C-JBU-A-2104C | Junction Box (BY VENDOR) | MC- | C-JBU-A-2104C | C-JBU-A-2104C | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | IS | 12 | PAIR | 1 | YES | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M40
131 | GR-12P-3-LFA | C-JBU-S-2101C | Junction Box (BY VENDOR) | MC- | C-JBU-S-2101C | C-JBU-S-2101C | UCP-GC-2101C | UCP-GC-2101C | FRS | SWA | NIS | 12 | PAIR | 2.5 | YES | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 330 | M40
132 | GR-7P-1-LFA | C-JBU-D-2101C | Junction Box (BY VENDOR) | MC- | C-JBU-D-2101C | C-JBU-D-2101C | UCP-GC-2101C | UCP-GC-2101C | FRS | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 330 | M32
133 | GY-7P-1-LA | C-JBU-D-2102C | Junction Box (BY VENDOR) | MC- | C-JBU-D-2102C | C-JBU-D-2102C | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M32
134 | GY-19P-1-LA | LCP-2101C1 | - | MC- | LCP-2101C1 | LCP-2101C1 | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
135 | GY-19P-1-LA | LCP-2101C2 | - | MC- | LCP-2101C2 | LCP-2101C2 | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
136 | GY-19P-1-LA | LCP-2101C3 | - | MC- | LCP-2101C3 | LCP-2101C3 | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
137 | GY-19P-1-LA | LCP-2101C4 | - | MC- | LCP-2101C4 | LCP-2101C4 | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
138 | GY-19P-1-LA | LCP-2101C5 | - | MC- | LCP-2101C5 | LCP-2101C5 | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | YES | Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
139 | GY-19P-1-A | IRP-UCP-GS-2101C1 | - | MC- | IRP-UCP-GS-2101C1 | IRP | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
140 | GY-19P-1-A | IRP-UCP-GS-2101C2 | - | MC- | IRP-UCP-GS-2101C2 | IRP | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
141 | GY-19P-1-A | IRP-UCP-GS-2101C3 | - | MC- | IRP-UCP-GS-2101C3 | IRP | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
142 | GY-19P-1-A | IRP-UCP-GS-2101C4 | - | MC- | IRP-UCP-GS-2101C4 | IRP | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
143 | GY-19P-1-A | IRP-UCP-GS-2101C5 | - | MC- | IRP-UCP-GS-2101C5 | IRP | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
144 | GR-19P-1-FA | IRP-UCP-GS-2101C6 | - | MC- | IRP-UCP-GS-2101C6 | IRP | UCP-GC-2101C | UCP-GC-2101C | FRS | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 140 | M50
145 | - | ESD-2101C | - | MC- | ESD-UCP-GC-2101C | ESD | UCP-GC-2101C | UCP-GC-2101C | FRS | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M40 |  | در بخش ESD این کابل دیده شده است
146 | - | DCS-2101C | - | MC- | DCS-UCP-GC-2101C | DCS | UCP-GC-2101C | UCP-GC-2101C | FRT | - | NIS | 12 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M40 |  | در بخش DCS این کابل دیده شده است
147 | - | PI-2121C | - | MC- | PI-2121C | DCS | UCP-GC-2101C | UCP-GC-2101C | FRT | - | NIS | 1 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | M20 | SPILL BACK | در بخش DCS این کابل دیده شده است
148 | 12T*1.5mm2 | M-2101-C | - | MC- | M-2101-C | M-2101-C Motor Aux JB | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 12 | Triad | 1.5 | - | - | Black | NOTE 3 | - | 330 | M50 | by electrical
149 | 3*2.5 mm2 | II-2234C | - | MC- | II-2234C | MCC | II-2234C | UCP-GC-2101C | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
150 | 3*2.5 mm2 | II-2235C | - | MC- | II-2235C | MCC | II-2235C | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
151 | 3*2.5 mm2 | II-2236C | - | MC- | II-2236C | MCC | II-2236C | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
152 | 3*2.5 mm2 | II-2237C | - | MC- | II-2237C | MCC | II-2237C | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
153 | 3*2.5 mm2 | II-2238C | - | MC- | II-2238C | MCC | II-2238C | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
154 | 3*2.5 mm2 | II-2239C | - | MC- | II-2239C | MCC | II-2239C | MCC | FRT | SWA | NIS | 3 | Core | 2.5 | - | - | Black | NOTE 3 | - | 330 | by electrical | by electrical
155 | - | [8 empty] | SIGNALS BETWEEN IRP AND UCP (A, B C ) | [9 empty] | -
156 | - | XST-2224A | Start Command | MC- | IRP-UCP-GS-2101A5 | IRP | UCP-GC-2101A | UCP-GC-2101A | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | - | Added
157 |  | XSP-2224A | Stop Command | [18 empty] | Added
158 |  | XL-2224A | Running Status | [18 empty] | Added
159 |  | XA-2224A | Fault Status | [18 empty] | Added
160 | - | XST-2224B | Start Command | MC- | IRP-UCP-GS-2101B5 | IRP | UCP-GC-2101B | UCP-GC-2101B | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | - | Added
161 |  | XSP-2224B | Stop Command | [18 empty] | Added
162 |  | XL-2224B | Running Status | [18 empty] | Added
163 |  | XA-2224B | Fault Status | [18 empty] | Added
164 | - | XST-2224C | Start Command | MC- | IRP-UCP-GS-2101C5 | IRP | UCP-GC-2101C | UCP-GC-2101C | FRT | SWA | NIS | 19 | PAIR | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | - | - | Added
165 |  | XSP-2224C | Stop Command | [18 empty] | Added
166 |  | XL-2224C | Running Status | [18 empty] | Added
167 |  | XA-2224C | Fault Status | [18 empty] | Added
D04
TOTALLY REVIZED

## Cable list (Dehydration PK.)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 |  | IN |  | LI | 0009 |  | D04
INSTRUMENT CABLE LIST FOR UCP-PK-2101 & ESD/BMS-PK-2101 SYSTEM ( DEHYDRATION PACKAGE)
ITEM | Cable Code | Tag No. | Description | Cable No. |  | From | To. | SYSTEM | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | Lead Cover | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | CABLE LENGTH (M) | GLAND SIZE | Remark
1 | BL-19P-1-LA | JBU-A-2131 | Junction Box (BY VENDOR) | MC- | JBU-A-2131 | JBU-A-2131 | UCP-PK-2101 | UCP-PK-2101 | FRT | SWA | IS | 19 | Pair | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 420 | M50
2 | BL-12P-1-LA | JBU-A-2132 | Junction Box (BY VENDOR) | MC- | JBU-A-2132 | JBU-A-2132 | UCP-PK-2101 | UCP-PK-2101 | FRT | SWA | IS | 12 | Pair | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 420 | M40
3 | BR-19P-1-LFA | JBU-A-2133 | Junction Box (BY VENDOR) | MC- | JBU-A-2133 | JBU-A-2133 | ESD/BMS-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | IS | 19 | Pair | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 420 | M50
4 | BR-12P-1-LFA | JBU-A-2134 | Junction Box (BY VENDOR) | MC- | JBU-A-2134 | JBU-A-2134 | ESD/BMS-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | IS | 12 | Pair | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 420 | M40
5 | GR-12P-3-LFA | JBU-S-2131 | Junction Box (BY VENDOR) | MC- | JBU-S-2131 | JBU-S-2131 | ESD/BMS-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | NIS | 12 | Pair | 2.5 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 420 | M40
6 | GR-12P-1-LFA | JBU-D-2131 | Junction Box (BY VENDOR) | MC- | JBU-D-2131 | JBU-D-2131 | ESD/BMS-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | NIS | 12 | Pair | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 420 | M50
7 | GR-12P-1-LFA | JBU-D-2132 | Junction Box (BY VENDOR) | MC- | JBU-D-2132 | JBU-D-2132 | ESD/BMS-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | NIS | 12 | Pair | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 420 | M50
8 | GR-12P-1-LFA | JBU-D-2133 | Junction Box (BY VENDOR) | MC- | JBU-D-2133 | JBU-D-2133 | ESD/BMS-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | NIS | 12 | Pair | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 420 | M50
9 | GR-12P-1-LFA | LCP-PK-2101/1 | Local Control Panel (BY VENDOR) | MC- | LCP-PK-2101/1 | ESD/BMS-PK-2101 | LCP-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | NIS | 12 | Pair | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 420 | M50
10 | GR-12P-1-LFA | LCP-PK-2101/2 | Local Control Panel (BY VENDOR) | MC- | LCP-PK-2101/2 | ESD/BMS-PK-2101 | LCP-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | NIS | 12 | Pair | 1 | Yes | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 420 | M50
11 | GR-19P-1-FA | IRP-ESD-PK-2101 | IRP SIGNALS | MC- | IRP-ESD-PK-2101 | MCC/IRP | ESD/BMS-PK-2101 | ESD/BMS-PK-2101 | FRS | SWA | NIS | 19 | Pair | 1 | - | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 140 | M50
12 | GY-19P-1-A | IRP-UCP-PK-2101/1 | IRP SIGNALS | MC- | IRP-UCP-PK-2101/1 | MCC/IRP | UCP-PK-2101 | UCP-PK-2101 | FRT | SWA | NIS | 19 | Pair | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
13 | GY-19P-1-A | IRP-UCP-PK-2101/2 | IRP SIGNALS | MC- | IRP-UCP-PK-2101/2 | MCC/IRP | UCP-PK-2101 | UCP-PK-2101 | FRT | SWA | NIS | 19 | Pair | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
14 | GY-19P-1-A | IRP-UCP-PK-2101/3 | IRP SIGNALS | MC- | IRP-UCP-PK-2101/3 | MCC/IRP | UCP-PK-2101 | UCP-PK-2101 | FRT | SWA | NIS | 19 | Pair | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
15 | GY-19P-1-A | IRP-UCP-PK-2101/4 | IRP SIGNALS | MC- | IRP-UCP-PK-2101/4 | MCC/IRP | UCP-PK-2101 | UCP-PK-2101 | FRT | SWA | NIS | 19 | Pair | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50
D04
TOTALLY REVIZED

## Cable list (N2)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  | 120 |  | IN |  | LI | 0009 |  | D04
INSTRUMENT CABLE LIST FOR UCP-G-2204 SYSTEM ( NITROGEN PACKAGE)
ITEM | Cable Code | Tag No. | Description | Cable No. |  | From | To. | SYSTEM | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | Lead Cover | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | CABLE LENGTH (M) | GLAND SIZE | Remark
1 | BL-19P-1-LA | JBU-A-2151 | Junction Box (By vendor) | MC- | JBU-A-2151 | JBU-A-2151 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M50 | NOTE 1
2 | BL-19P-1-LA | JBU-A-2152 | Junction Box (By vendor) | MC- | JBU-A-2152 | JBU-A-2152 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M50 | NOTE 1
3 | BL-19P-1-LA | JBU-A-2153 | Junction Box (By vendor) | MC- | JBU-A-2153 | JBU-A-2153 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M50 | NOTE 1
4 | BL-19P-1-LA | JBU-A-2154 | Junction Box (By vendor) | MC- | JBU-A-2154 | JBU-A-2154 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M50 | NOTE 1
5 | BL-19P-1-LA | JBU-A-2155 | Junction Box (By vendor) | MC- | JBU-A-2155 | JBU-A-2155 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M50 | NOTE 1
6 | BL-19P-1-LA | JBU-A-2156 | Junction Box (By vendor) | MC- | JBU-A-2156 | JBU-A-2156 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M50 | NOTE 1
7 | BL-19P-1-LA | JBU-A-2157 | Junction Box (By vendor) | MC- | JBU-A-2157 | JBU-A-2157 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | IS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 330 | M50 | NOTE 1
8 | GY-19P-1-LA | JBU-D-2151 | Junction Box (By vendor) | MC- | JBU-D-2151 | JBU-D-2113 | JBU-D-2151 | UCP-Nitrogen | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
9 | GY-19P-1-LA | JBU-D-2151 | Junction Box (By vendor) | MC- | JBU-D-2151 | JBU-D-2114 | JBU-D-2151 | UCP-Nitrogen | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
10 | GY-19P-1-LA | JBU-D-2151 | Junction Box (By vendor) | MC- | JBU-D-2151 | JBU-D-2115 | JBU-D-2151 | UCP-Nitrogen | FRT | SWA | NIS | 19 | PAIR | 1 | Yes | Individual & Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M50
11 | GY-12P-3-LA | JBU-S-2151 | Junction Box (By vendor) | MC- | JBU-S-2151 | JBU-S-2151 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | NIS | 12 | PAIR | 2.5 | Yes | Individual & Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M40 | NOTE 1
12 | GY-12P-3-LA | JBU-S-2152 | Junction Box (By vendor) | MC- | JBU-S-2152 | JBU-S-2152 | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | NIS | 12 | PAIR | 2.5 | Yes | Individual & Overall Screen | Gray | NOTE 3 | 300/500 V | 330 | M40 | NOTE 1
13 | GY-19P-1-A | IRP-UCP-G-2204/1 | IRP SIGNALS | MC- | IRP-UCP-G-2204/1 | MCC/IRP | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | NIS | 19 | Pair | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50 | Added
14 | GY-19P-1-A | IRP-UCP-G-2204/2 | IRP SIGNALS | MC- | IRP-UCP-G-2204/2 | MCC/IRP | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | NIS | 19 | Pair | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50 | Added
15 | GY-19P-1-A | IRP-UCP-G-2204/3 | IRP SIGNALS | MC- | IRP-UCP-G-2204/3 | MCC/IRP | UCP-G-2204 | UCP-Nitrogen | FRT | SWA | NIS | 19 | Pair | 1 | - | Overall Screen | Gray | NOTE 3 | 300/500 V | 140 | M50 | Added
D04
TOTALLY REVIZED