## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-MT-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2657 |  |  | Transmital Date: 13/APR/2024
Document Title: MTO For HVAC & Plumbing For Extension of Existing Elect. Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-2657 |  |  | Transmital Date: 13/APR/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-MT-0002-D01 |  |  | CRS Status: | CM
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | تعداد و مشخصات فنی فنی مربوط به کولرهای SPLIT و FAN ها در MTO درج گردد. |  | 03-2294-154168 | 1403/04/24 | تعداد و مشخصات فنی دستگاه های اسپلیت یونیت در مدارک HVAC System Layout و Data Sheets For Main HVAC Equipment ساختمان مربوطه ارائه شده است. فرآیند خرید تجهیزات بر اساس اطلاعات در مدارک پیشگفت پیگیری خواهد شد.
1 | لوله ای PP موردذ اشاره در MTO در صورتی که مربوط به خروجی درین کولرهای اسپلیت می باشد مورد پذیرش است، در صورتی که برای مصارف آشامیدنی باشد مورد پذیرش نبوده و مطابق با اسناد پیمان می بایست از لوله های PEX-AL-PEX(5 لایه) استفاده شود. |  | 03-2294-154168 | 1403/04/24 | لوله و اتصالات PP صرفا جهت تخلیه آب چگالیده دستگاه های اسپلیت یونیت مورد استفاده قرار خواهند گرفت.
1 | مزید تاکید اعلام می گردد از آنجا که مسئولیت طراحی تفصیلی پروژه جزو تعهدات پیمانکار پروژه است و همچنان با استناد به وضعیت (IFI) مدرک ارسالی، مسئولیت کامل عدم تطابق مشخصات فنی، متریال و یا تعداد اقلام در مرحله سفارش گذاری و خرید بر عهده آن پیمانکار است. |  | 03-2294-154168 | 1403/04/24 | مورد تایید است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date:1403/04/24 |  |  |  |  | Date: