## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-TE-PY-0008 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2633 |  |  | Transmital Date: Mar-11th-2024
Document Title: Telecomm. Equipment Layout For GCS Warehouse |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0212-TE-TR-2633 |  |  | Transmital Date: Mar-11th-2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-TE-PY-0008_D01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جهت WARE HOUSE اینترکام و اسپیکر اضافه گردد در بخش لجند و نقشه ، کابل تلفن بیرون ساختمانی 10X2X0.6 میلیمتر در نظر گرفته شود تعداد پریزهای اتاق 101 افزایش یابد |  | 03-2294-326778 | 1403-08-19 | به درخواست کارفرمای محترم اسپیکر و اینترکام برای محوطه workshop اضافه گردید(هر چند ساختمان دارای گوشی تلفن و ارتباط با اتاق کنترل میباشد و اینترکام در محیطهای فرایندی بیشتر کاربرد خواهد داشت ) کابل تلفن 2 زوج 0.6 نمایش گردید تعداد سوکت تلفن در ناحیه workshop اضافه گردید . اما لازم به توضیح است محیط WORKSHOPصنعتی بوده و بر روی دیوار ، نصب سوکت RJ11 روکار توصیه نمیگردد. علی ایهال اضافه گردید تلفن صنعتی دیواری برای محیط WORKSHOP بیشتر کاربرد خواهد داشت
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: AP.Golrang | Signature |  |  |  | Clarified By: | Signature
| Date: Sep-21th-2022 |  |  |  |  | Date: