## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 15
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0004 | D06
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR F&G SYSTEMS نگهداشت و افزایش تولید میدان نفتی بینک
D06 |  | FEB.2025 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D05 |  | NOV.2024 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Sadeghian
D04 |  | FEB.2024 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D03 |  | NOV.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number:F0Z-708970
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 15
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 |  | IN | LI | 0004 |  | D06
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 | D05 | D06 | Page |  | D00 |  | D01 |  | D02 | D03 | D04 | D05 | D06
1 | X | X | X |  | X |  | X | X | X | 65
2 | X | X | X |  | X |  | X | X | X | 66
3 | X | X | [5 empty] | X |  | 67
4 | X | X | X |  | X |  | X | X | X | 68
5 | X | X | X |  | X |  | X | X |  | 69
6 | X | X | X |  | X |  | X | X | X | 70
7 | X | X | X |  | X |  | X | X | X | 71
8 | X | X | X |  | X |  | X | X | X | 72
9 |  | X | X |  | X |  | X | X | X | 73
10 |  | X | X |  | X |  | X | X | X | 74
11 |  | X | X |  | X |  | X | X | X | 75
12 |  | X | X |  | X |  | X | X | X | 76
13 |  | X | X |  | X |  | X | X |  | 77
14 |  | X | X |  | X |  | X | X |  | 78
15 |  |  | X |  | X |  |  | X |  | 79
16 |  |  | X |  | X |  |  |  |  | 80
17 |  |  | X |  | X |  |  |  |  | 81
18 |  |  | X |  | X |  |  |  |  | 82
19 | [9 empty] | 83
20 | [9 empty] | 84
21 | [9 empty] | 85
22 | [9 empty] | 86
23 | [9 empty] | 87
24 | [9 empty] | 88
25 | [9 empty] | 89
26 | [9 empty] | 90
27 | [9 empty] | 91
28 | [9 empty] | 92
29 | [9 empty] | 93
30 | [9 empty] | 94
31 | [9 empty] | 95
32 | [9 empty] | 96
33 | [9 empty] | 97
34 | [9 empty] | 98
35 | [9 empty] | 99
36 | [9 empty] | 100
37 | [9 empty] | 101
38 | [9 empty] | 102
39 | [9 empty] | 103
40 | [9 empty] | 104
41 | [9 empty] | 105
42 | [9 empty] | 106
43 | [9 empty] | 107
44 | [9 empty] | 108
45 | [9 empty] | 109
46 | [9 empty] | 110
47 | [9 empty] | 111
48 | [9 empty] | 112
49 | [9 empty] | 113
50 | [9 empty] | 114
51 | [9 empty] | 115
52 | [9 empty] | 116
53 | [9 empty] | 117
54 | [9 empty] | 118
55 | [9 empty] | 119
56 | [9 empty] | 120
57 | [9 empty] | 121
58 | [9 empty] | 122
59 | [9 empty] | 123
60 | [9 empty] | 124
61 | [9 empty] | 125
62 | [9 empty] | 126
63 | [9 empty] | 127
64 | [9 empty] | 128

## NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 15
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0004 | D06
REFERENCES(NOTE 2):
| F&G LOCATION LAYOUT FOR PROCESS Area | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0005
| F&G LOCATION LAYOUT FOR BUILDINGS | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0006
| DATA SHEET FOR MATRIX PANEL | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017
| ESD LEVEL HIERARCHY | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003
| FIRE & GAS DETECTION DESIGN CRITERIA | [7 empty] | BK-GCS-PEDCO-120-IN-DC-0001
GENERAL NOTE
| 1 | ALL LISTED FACP'S SIGNALS SHALL BE MONITORED IN F&G SYSTEM BY MODBUS CONNECTION.
| 2 | REFER TO LATEST VERSION OF REFERENCE DOCUMENTS.
| 3 | ALL RELAYS & I.S. BARRIERS INSTALLED IN F&G PANEL SHALL BE SIL CERTIFIED. ALL RELAYS SHALL BE LINE-MONITORED
| 4 | GALVANIC ISOLATION BARRIER SHALL BE CONSIDERED FOR INTRINSICALLY SAFE (EEXia) LOOPS.
| 5 | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 15
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 | D06
F&G I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+25% SPARE) | REMARKS
| 1 |  | AI-NIS-R |  | NIS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 87 |  | 109 | NOTES 4,5 | 108.75
| 2 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 61 |  | 77 | NOTES 4,5 | 76.25
| 3 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 119 |  | 149 | NOTES 4,5 | 148.75
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS: |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS: |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
|  | MAC: |  | MANUAL CALL POINT | [7 empty] | BR: | BLUE BEACON
|  | HN: |  | HORN | [7 empty] | BB: | RED BEACON
|  | LHD: |  | LINEAER HEAT DETECTOR | [7 empty] | FGD: | FLAMMABLE GAS DETECTOR
|  | SD: |  | SMOKE DETECTOR | [7 empty] | TGD: | TOXIC GAS DETECTOR
|  | BL: |  | BELL | [7 empty] | FD: | FLAME DETECTOR
|  | FACP: |  | FIRE ALARM CONTROL PANEL | [7 empty] | IRP: | INTERFACE RELAY PANEL
D06
D06

## IO List for F&G System
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  |  | رشته |  | نوع مدرک | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO |  | 120 |  |  | IN |  | LI | 0004 |  |  | D06
SIGNALS TO F&G SYSTEM
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE |  | FROM |  | TO |  | JB NO. | POWER SUPPLY | Cable Type | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[17 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR PROCESS AREA
1 | MAC-1001 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
2 | MAC-1002 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
3 | HN-1001 | Horn | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
4 | BR-1001 | Beacon - Red | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
5 | BB-1001 | Beacon - Blue | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
6 | BY-1001 | Beacon - Yellow | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
7 | MAC-2001 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
8 | MAC-2002 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
9 | MAC-2003 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
10 | HN-2001 | Horn | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
11 | BR-2001 | Beacon - Red | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
12 | BB-2001 | Beacon - Blue | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
13 | BY-2001 | Beacon - Yellow | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
14 | MAC-3001 | Manual Call Point | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
15 | HN-3001 | Horn | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
16 | BR-3001 | Beacon - Red | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
17 | BB-3001 | Beacon - Blue | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
18 | BY-3001 | Beacon - Yellow | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
19 | MAC-4001 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
20 | MAC-4002 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
21 | HN-4001 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 OF 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
22 | BR-4001 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
23 | BB-4001 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
24 | BY-4001 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
25 | HN-4002 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
26 | BR-4002 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
27 | BB-4002 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
28 | BY-4002 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
29 | MAC-5001 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
30 | MAC-5002 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
31 | HN-5001 | Horn | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
32 | BR-5001 | Beacon - Red | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
33 | BB-5001 | Beacon - Blue | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
34 | BY-5001 | Beacon - Yellow | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
35 | MAC-6001 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
36 | MAC-6002 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
37 | HN-6001 | Horn | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
38 | BR-6001 | Beacon - Red | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
39 | BB-6001 | Beacon - Blue | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
40 | BY-6001 | Beacon - Yellow | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
41 | MAC-7001 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
42 | MAC-7002 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
43 | HN-7001 | Horn | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
44 | BR-7001 | Beacon - Red | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
45 | BB-7001 | Beacon - Blue | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
46 | BY-7001 | Beacon - Yellow | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
47 | MAC-8001 | Manual Call Point | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
48 | MAC-8002 | Manual Call Point | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
49 | MAC-8003 | Manual Call Point | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
50 | HN-8001 | Horn | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
51 | BR-8001 | Beacon - Red | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
52 | BB-8001 | Beacon - Blue | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
53 | BY-8001 | Beacon - Yellow | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
54 | MAC-9001 | Manual Call Point | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
55 | HN-9001 | Horn | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
56 | BR-9001 | Beacon - Red | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
57 | BB-9001 | Beacon - Blue | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
58 | BY-9001 | Beacon - Yellow | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
59 | FGD-1001 | Flammable Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
60 | TGD-1001 | Toxic Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
61 | FD-2001 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
62 | FD-2002 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
63 | FD-2003 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
64 | FGD-2001 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
65 | FGD-2002 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
66 | FGD-2003 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
67 | FGD-2004 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
68 | TGD-2001 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
69 | TGD-2002 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
70 | TGD-2003 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
71 | TGD-2004 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
72 | FD-3001 | Flame Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
73 | FD-4001A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
74 | FD-4002A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
75 | FD-4003A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
76 | FD-4004A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
77 | FGD-4001A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
78 | FGD-4002A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
79 | FGD-4003A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
80 | FGD-4004A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
81 | TGD-4001A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
82 | TGD-4002A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
83 | TGD-4003A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
84 | TGD-4004A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
85 | FD-4001B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
86 | FD-4002B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
87 | FD-4003B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
88 | FD-4004B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
89 | FGD-4001B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
90 | FGD-4002B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
91 | FGD-4003B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
92 | FGD-4004B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
93 | TGD-4001B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
94 | TGD-4002B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
95 | TGD-4003B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
96 | TGD-4004B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
97 | FD-4001C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
98 | FD-4002C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
99 | FD-4003C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
100 | FD-4004C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
101 | FGD-4001C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
102 | FGD-4002C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
103 | FGD-4003C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
104 | FGD-4004C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
105 | TGD-4001C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
106 | TGD-4002C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
107 | TGD-4003C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
108 | TGD-4004C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
109 | FGD-5001A | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
110 | FGD-5001B | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
111 | FGD-5001C | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
112 | TGD-5001A | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
113 | TGD-5001B | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
114 | TGD-5001C | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
115 | FD-6001 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
116 | FD-6002 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
117 | FGD-6001 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
118 | FGD-6002 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
119 | FGD-6003 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
120 | TGD-6001 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
121 | TGD-6002 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
122 | TGD-6003 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexd Zone1, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
123 | LHD-7001 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
124 | LHD-7002 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
125 | FGD-7001 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
126 | FGD-7002 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
127 | FGD-7003 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
128 | TGD-7001 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
129 | TGD-7002 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
130 | TGD-7003 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
131 | FD-8001 | Flame Detector | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (11 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
132 | FD-8002 | Flame Detector | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (12 OF 12) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
133 | PT-2301 | Pressure Transmitter | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexia Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 2Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D06
134 | LSLL-2301 | Low Low Level Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(1/8) |  | Eexia Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
135 | LSLL-2302 | Low Low Level Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(1/8) |  | Eexia Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D05
FOR BUILDING
1 | FGD-1101 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D06
2 | FGD-1102 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
3 | FGD-1103 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
4 | TGD-1101 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
5 | TGD-1102 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
6 | TGD-1103 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
7 | FGD-1201 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
8 | FGD-1202 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
9 | FGD-1203 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
10 | TGD-1201 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
11 | TGD-1202 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
12 | TGD-1203 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/7) |  | Eexd Zone2, IIB T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
13 | HGD-1101 | Hydrogen Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd 'Zone1, IIC T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
14 | HGD-1102 | Hydrogen Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd 'Zone1, IIC T4 | AI-NIS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D06
15 | HD-1101 | Heat Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
16 | HD-1102 | Heat Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
17 | MAC-1101 | Manual Call Point | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
SIGNALS BETWEEN F&G AND ESD SYSTEM & OTHER SYSTEMS
1 | ESDR0-FG-1101 | ESD 0 Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 12 PAIRx 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
2 | ESDR1A-FG-1101 | ESD 1A Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
3 | ESDR1A-FD-1101 | ESD 1A Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
4 | HVAC-FG-G-1101 | Control building HVAC shut down & damper closed for gas detection | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | HVAC |  | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
5 | HVAC-FG-F-1101 | Control building HVAC shut down & damper closed for fire detection | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | HVAC |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
6 | DAMP-FG-1101 | Battery Room Damper1 closed | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
7 | DAMP-FG-1102 | Battery Room Damper 2 closed | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP | Battery Room Fan | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
8 | DAMP-FG-G-1101 | Electrical building air intake damper closed for gas detection | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
9 | FAN-FG-1101 | Battery Room stand by Fan Activation Command | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
10 | INB-FG-1101 | Inhibit to Boost for UPS Charger 1 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC | 19 PAIRx 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
11 | INB-FG-1102 | Inhibit to Boost for UPS Charger 2 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
12 | INB-FG-1103 | Inhibit to Boost for UPS Charger 3 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
13 | PISO-FG-1101 | Power Isolation of Battery Bank 1 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
14 | PISO-FG-1102 | Power Isolation of Battery Bank 2 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
15 | PISO-FG-1103 | Power Isolation of Battery Bank 3 | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
16 | Ex-FG-G-1101 | F&G System confirmed Gas Alarm to Existing F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Existing F&G |  | - | - | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | to be finalized based on existing f&g system
17 | Ex-FG-F-1101 | F&G System confirmed Fire Alarm to Existing F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Existing F&G |  | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
18 | Ex-FG-G-1102 | Existing F&G System confirmed Gas Alarm to F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DI-NIS-R |  | Existing F&G |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
19 | Ex-FG-F-1102 | Existing F&G System confirmed Fire Alarm to F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DI-NIS-R |  | Existing F&G |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
20 | HSS-2301A | Pump Start Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | IRP | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
21 | XR-2301A | Pump Running/ Stopped Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2 IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
22 | XF-2301A | Pump Fault Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
23 | PAL-2301 | Low Pressure Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | Battery Room Fan | IRP | FGS | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
24 | XM-2301A | Pump Auto/Manual Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS | - |  |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
25 | HSS-2301B | Pump Start Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2301B | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
26 | XM-2301B | PumpAuto/ Manual Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
27 | XR-2301B | Pump Running/ Stopped Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
28 | XF-2301B | Pump Fault Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
29 | PAL-2301B | Low Pressure Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
30 | HSS-2302A | Pump Start Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302A | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
31 | XM-2302A | PumpAuto/ Manual Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
32 | XR-2302A | Pump Running/ Stopped Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
33 | XF-2302A | Pump Fault Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
34 | PALL-2302A | Low Low Pressure Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
35 | HSS-2302B | Pump Start Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302B | Battery Room Fan | - | 24 VDC | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
36 | XM-2302B | PumpAuto/ Manual Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
37 | XR-2302B | Pump Running/ Stopped Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
38 | XF-2302B | Pump Fault Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
39 | PALL-2302B | Low Low Pressure Alarm | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(2/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
40 | XA-CO2-1101 | MANUAL/AUTO SELECTOR SWITCH STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS | - | - | 7 PAIR x 1 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
41 | XRE-CO2-1101 | RELEASED STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
42 | XI-CO2-1101 | INHIBIT STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
43 | XF-CO2-1101 | GENERAL FAULT | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS | - | - |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
44 | HS-CO2-1101 | AUTOMAT RELEASE COMMAND (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | Unclassified | DO-NIS-R |  | FGS | FGS | CO2 Control Panel |  | - | 24 VDC |  | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
45 | PSH-2302 | Valve Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2302 |  | FGS | FGS | - | - | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
46 | DSOV-2302 | Valve Open Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2302 |  | - | 24 VDC | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
47 | PSH-2303 | Valve Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2303 |  | FGS | FGS | - | - | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
48 | DSOV-2303 | Valve Open Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2303 |  | - | 24 VDC | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
49 | PSH-2304 | Valve Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2304 |  | FGS | FGS | - | - | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
50 | DSOV-2304 | Valve Open Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2304 |  | - | 24 VDC | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
51 | PSH-2301 | Valve Status | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone2, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2305 |  | FGS | FGS | - | - | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
52 | DSOV-2301 | Valve Open Command | Fire Water Network |  | BK-GCS-PEDCO-120-SA-PI-0001(4/8) |  | Eexd 'Zone2, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2305 |  | - | 24 VDC | 1 PAIRx 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D06
SIGNALS TO F&G Matrix PANEL
1 | LP-AR1-FD | Fire Alarm For Area 1 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 19 PAIR x 1 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | low frequency pulse for prealarm and high frequency pulse for alarm
2 | LP-AR1-FGD | Flammable Gas Alarm For Area 1 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
3 | LP-AR1-TGD | Toxic Gas Alarm For Area 1 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
4 | LP-AR2-FD | Fire Alarm For Area 2 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
5 | LP-AR2-FGD | FlammableGas Alarm For Area 2 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
6 | LP-AR2-TGD | Toxic Gas Alarm For Area 2 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
7 | LP-AR3-FD | Fire Alarm For Area 3 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
8 | LP-AR4A-FD | Fire Alarm For Area 4A Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
9 | LP-AR4A-FGD | FlammableGas Alarm For Area 4 A Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
10 | LP-AR4A-TGD | Toxic Gas Alarm For Area 4A Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
11 | LP-AR4B-FD | Fire Alarm For Area 4B Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
12 | LP-AR4B-FGD | FlammableGas Alarm For Area 4 B Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
13 | LP-AR4B-TGD | Toxic Gas Alarm For Area 4B Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
14 | LP-AR4C-FD | Fire Alarm For Area 4C Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
15 | LP-AR4C-FGD | FlammableGas Alarm For Area 4C Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
16 | LP-AR4C-TGD | Toxic Gas Alarm For Area 4C Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
17 | LP-AR5-FD | Fire Alarm For Area 5 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 19 PAIR x 1 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
18 | LP-AR5-FGD | FlammableGas Alarm For Area 5 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
19 | LP-AR5-TGD | Toxic Gas Alarm For Area 5 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
20 | LP-AR6-FD | Fire Alarm For Area 6 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
21 | LP-AR6-FGD | FlammableGas Alarm For Area 6 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
22 | LP-AR6-TGD | Toxic Gas Alarm For Area 6 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
23 | LP-AR7-FD | Fire Alarm For Area 7 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
24 | LP-AR7-FGD | FlammableGas Alarm For Area 7 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
25 | LP-AR7-TGD | Toxic Gas Alarm For Area 7 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
26 | LP-AR8-FD | Fire Alarm For Area 8 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
27 | LP-AR9-FD | Fire Alarm For Area 9 Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
28 | LP-CB-FD | Fire Alarm For Control Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
29 | LP-CB-FGD | FlammableGas Alarm For Control Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
30 | LP-CB-TGD | Toxic Gas Alarm For Control Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
31 | LP-EB-FD | Fire Alarm For Electrical Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
32 | LP-EB-FGD | FlammableGas Alarm For Electrical Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
33 | LP-EB-TGD | Toxic Gas Alarm For Electrical Building Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 19 PAIR x 1 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
34 | LP-PSH-2302 | Deluge Valve 2302 Opened Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
35 | LP-PSH-2303 | Deluge Valve 2303 Opened Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
36 | LP-PSH-2304 | Deluge Valve 2304 Opened Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
37 | LP-PSH-2301 | Deluge Valve 2301 Opened Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
38 | LP-P-2301B | Diesel Pump Status Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
39 | LP-P-2301A | Electrical Pump Status Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
40 | LP-CO2-RE | CO2 Release Status Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
41 | PB-DV-2302 | Deluge Valve 2302 Open Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
42 | PB-DV-2303 | Deluge Valve 2303 Open Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
43 | PB-DV-2304 | Deluge Valve 2304 Open Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
44 | PB-DV-2301 | Deluge Valve 2301 Open Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
45 | PB-P-2301B | Diesel Pump Start Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
46 | PB-P-2301A | Electrical Pump Start Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
47 | PB-CO2-CO | CO2 Release Command Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
48 | PB-RST | RESET Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
49 | PB-ACK-HO | ACK HORN Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - | 19 PAIR x 1 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
50 | PB-ACK | ACK Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | - |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
51 | PB-INHIBIT | Inhibit to maitenance Push button | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DI-NIS-R |  | F&G Matrix |  | FGS |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
52 | LP-INHIBIT | Inhibit to maitenance Lamp | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
53 | BUZZER | Audible Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | Unclassified | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC |  | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06
D06

## IO List for FACP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO | 120 |  | IN | LI | 0004 | D06
SIGNALS TO FACP
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE | FROM | TO |  | POWER SUPPLY | Cable Type | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[14 empty] | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR BUILDING
FACP LOOP 1
1 | FACP | Output Port of Loop 1 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | MAC-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | MAC-1102 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | MAC-1102 | SD-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | SD-1104 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1104 | SD-1108 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | SD-1103 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1103 | SD-1110 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | MAC-1103 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | MAC-1103 | MAC-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | SD-1102 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1102 | SD-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | SD-1101 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1101 | MAC-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | SD-1121 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1121 | SD-1122 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | SD-1122 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1122 | SD-1123 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
10 | SD-1123 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1123 | SD-1124 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
11 | SD-1124 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1124 | SD-1112 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
12 | SD-1135 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1135 | SD-1136 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
13 | SD-1136 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1136 | SD-1115 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
14 | SD-1128 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1128 | MAC-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
15 | SD-1126 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1126 | BL-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
16 | SD-1108 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1108 | SD-1110 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
17 | SD-1110 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1110 | SD-1112 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
18 | SD-1112 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1112 | SD-1114 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
19 | SD-1114 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1114 | SD-1115 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
20 | SD-1115 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1115 | MAC-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
21 | MAC-1104 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | MAC-1104 | BL-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
22 | BL-1101 | Bell | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BL-1101 | BR-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
23 | BR-1103 | Beacon - Red | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BR-1103 | MAC-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
24 | MAC-1105 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | MAC-1105 | SD-1118 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
25 | SD-1118 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1118 | SD-1120 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
26 | SD-1120 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1120 | HN-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
27 | HN-1101 | Horn | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | HN-1101 | BR-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
28 | BR-1101 | Beacon - Red | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BR-1101 | BB-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
29 | BB-1101 | Beacon - Blue | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BB-1101 | BY-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
30 | BY-1101 | Beacon - Yellow | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | BY-1101 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 2
1 | FACP | Output Port of Loop 2 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | SD-1105 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1105 | SD-1127 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | SD-1106 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1106 | SD-1130 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | SD-1130 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1130 | SD-1131 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | SD-1131 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1131 | SD-1132 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | SD-1132 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1132 | SD-1129 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | SD-1129 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1129 | SD-1134 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | SD-1134 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1134 | SD-1133 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | SD-1133 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1133 | SD-1128 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
10 | SD-1128 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1128 | SD-1127 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
11 | SD-1127 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1127 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 3
1 | FACP | Output Port of Loop 3 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1107 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | SD-1107 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1107 | SD-1109 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | SD-1109 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1109 | SD-1111 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | SD-1111 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1111 | SD-1113 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | SD-1113 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1113 | SD-1116 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | SD-1116 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1116 | SD-1117 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | SD-1117 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1117 | SD-1119 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | SD-1119 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1119 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 4
1 | FACP | Output Port of Loop 4 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | HN-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | HN-1201 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | HN-1201 | BR-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | BR-1201 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | BR-1201 | BB-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | BB-1201 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | BB-1201 | BY-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | BY-1201 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | BY-1201 | MAC-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | MAC-1201 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | MAC-1201 | SD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | SD-1201 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | SD-1201 | SD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | SD-1202 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | SD-1202 | MAC-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | MAC-1202 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | MAC-1202 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 5
1 | FACP | Output Port of Loop 5 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | SD-1203 | Smoke Detector | Extension of Existing Elect. Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | SD-1203 | SD-1204 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | SD-1204 | Smoke Detector | Extension of Existing Elect. Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/7) |  | Note 1 | Note1 | SD-1204 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 6
1 | FACP | Output Port of Loop 6 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | HN-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | HN-1202 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | HN-1202 | BR-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | BR-1202 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | BR-1202 | BB-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | BB-1202 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | BB-1202 | BY-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | BY-1202 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | BY-1202 | MAC-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | MAC-1203 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | MAC-1203 | LHD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | LHD-1201 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | LHD-1201 | LHD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | LHD-1202 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | LHD-1202 | LHD-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | LHD-1203 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/7) |  | Note 1 | Note1 | LHD-1203 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 7
1 | FACP | Output Port of Loop 7 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | SD-1301 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | SD-1301 | SD-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | SD-1302 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | SD-1302 | MAC-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | MAC-1302 | Manual Call Point | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | MAC-1302 | SD-1304 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | SD-1304 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | SD-1304 | SD-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | SD-1303 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | SD-1303 | HD-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | HD-1301 | Heat Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | HD-1301 | MAC-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | MAC-1301 | Manual Call Point | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | MAC-1301 | HN-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | HN-1301 | Horn | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | HN-1301 | BR-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
10 | BR-1301 | Beacon - Red | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | BR-1301 | BB-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
11 | BB-1301 | Beacon - Blue | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | BB-1301 | BY-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
12 | BY-1301 | Beacon - Yellow | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/7) |  | Note 1 | Note1 | BY-1301 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 8
1 | FACP | Output Port of Loop 8 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/7) |  | Note 1 | Note1 | FACP | SD-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | SD-1401 | Smoke Detector | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | SD-1401 | SD-1402 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | SD-1402 | Smoke Detector | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | SD-1402 | SD-1403 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | SD-1403 | Smoke Detector | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | SD-1403 | MAC-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | MAC-1401 | Manual Call Point | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | MAC-1401 | HN-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | HN-1401 | Horn | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | HN-1401 | BR-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | BR-1401 | Beacon - Red | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | BR-1401 | BB-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | BB-1401 | Beacon - Blue | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | BB-1401 | BY-1401 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | BY-1401 | Beacon - Yellow | GCS Warehouse |  | BK-GCS-PEDCO-120-IN-PY-0006 (7/7) |  | Note 1 | Note1 | BY-1401 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
Notes:
1- Non-IS Detector is on the Loop. Level of Alarm is N.A. for such Loop-powered.