## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-LI-0004 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2854 |  |  | Transmital Date: 2-DEC-2024
Document Title: I/O List For F&G Systems |  |  |  |  | NISOC Tr. No.: BK-PEDCO-NISOC-0309-IN-TR-2854 |  |  | Transmital Date: 2-DEC-2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-LI-0004_D05 |  |  | CRS Status: | AN
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در حال حاضر نظر خاصی مطرح نمی باشد. در صورت تغییر در مدارک مرجع لارم است این مدرک بروز رسانی گردد. |  | 03/2294/386405 | 1403/09/27 | تغیرات مدرک در زیر توضیح داده شده اند: - به دلیل اینکه تجهزات آنالوگ Flame & Gas detectors از نوع EEXD در نظر گرفته شده اند ، نوع سیگنال این تجهیزات بایستی بصورت Non-intrinsically safe در نظر گرفته شود که این تغییر در مدرک انجام و اصلاح گردید. - spare part ها برای I/O در این نسخه ، مطابق مدرک SPECIFICATION FOR FIRE & GAS SYSTEM بصورت 25% در نظر گرفته شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: s.Akbari | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 10 Mar 2024 |  |  |  |  | Date: