## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ST-DW-0082 |  |  |  |  | EPC Contractor Tr. No. : BK-HD-PEDCO-T-2797 |  |  | Transmital Date:10/6/2024
Document Title: Structural Drawing For Extension of Existing Control Building |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0307-ST-TR-2797 |  |  | Transmital Date:10/6/2024
[5 empty] | CRS No:NISOC-CRS-BK-GCS-PEDCO-120-ST-DW-0082_D00 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 |  |  | 1403/2294/448730 | 1403/11/9 | ------
2 |  |  | 1403/2294/448730 | 1403/11/9 | لیستوفر به نقشه های فونداسیون و استراکچر اضافه گردید
3 |  |  | 1403/2294/448730 | 1403/11/9 | با توجه به عدم وجود ستون در دیوارهای برشی ، نیازی به در نظر گرفتن ضوابط مربوط به میلگرد گذاری ستون در دراخل فونداسیون نمی باشد
4 |  |  | 1403/2294/448730 | 1403/11/9 | دیتایل مربوط به اتصال سقف بتنی به دیوار های بتنی به نقشه ها اضافه گردید
5 |  |  | 1403/2294/448730 | 1403/11/9 | با عنایت به این نکته که جهت تعیین اسلامپ ، انتخاب سنگدانه ها ، مقدارآب مورد نیاز بر اساس استفاده افزودنی ها به جهت کارایی و کاهش نفوذپذیری و مقادیر مشخص شده سیمان بر اساس مقاوت فشاری بتن شایسته است طرح اختلاط و مشخصات توسط سازنده بتن ارائه و در صورت تایید نظارت مورد استفاده قرار گیرد
6 |  |  | 1403/2294/448730 | 1403/11/9
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: