## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0004 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-TR-2763 |  |  | Transmital Date: 03-SEP-2024
Document Title: Calculation Note For UPS System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0306-EL-TR-2763 |  |  | Transmital Date: 03-SEP-2024
[5 empty] | CRS No: NISOC-CRS- BK-GCS-PEDCO-120-EL-CN-0004_D06 |  |  | CRS Status: | AN
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | دلیل محاسبه ظرفیت شارژ بصورت Charger rated current: 2X355.2A نامشخص است با توجه به اینکه هر شارژر به صورت 100 در صد طراحی شده اند نیازی به اعمال ضریب 2 در محاسبات جریان شارژر نیست،موضوع بررسی و اصلاحات لازم انجام پذیرد. |  | 03/2290/280162 | 2024-10-12 | اصلاحات لازم انجام گرفت.
2 | پیرو بند ۲ صورتجلسه مورخ ۱۴۰۳/۰۵/۱۴ (نامه شماره ۱۴۰۳/۲۲۹۱/۱۸۶۴۰ مورخ ۱۴۰۳/۰۵/۱۷) و پذیرش سازندگان در پروژه مشابه (ناشی از عدم وجود بیان فرایند خرید با اطلاعات پیشفرض و بر اساس کاتالوگ اطلاعات سازندگان تابلوهای ابزار دقیق) توسط پیمانکار، لازم است در صورت هر گونه تغییر در لیست بارهای سیستم ابزار دقیق (پس از نهایی شدن مدارک طراحی سازنده)، ضمن اخذ تأیید از بخش ابزار دقیق این امور، نسبت به اصلاح محاسبات اقدام گردد. |  | 03/2290/280162 | 2024-10-12 | مصارف بر اساس آخرین اطلاعات دریافتی از سازندگان توسط واحد ابزار دقیق بروزرسانی و در اختیار این واحد قرار گرفته و محاسبات UPS جهت اخذ تایید از کارفرمای محترم ارسال میگردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: M.Karimi | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 10-Feb-24 |  |  |  |  | Date: