| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Design Criteria | Vendor To confirm That All supplied material all in full compliance with Project site condition : - Min/Max air temperature = -5°C / 52°C - Relative humidity = 100% max at 52°C - Altitude = 12 m a.s.l. - Climate = Class 4 (Very High) Vendor shall submitted temperature de‐rating factors of equipment such as CB, etc. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated rated current be equal or higher than rate current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. | Confirmed | Closed. | All equipment like ACB ,MCCB, MPCB, Contractor ,...rating shall be sized at site condition and mentioned the true size in this offer as below example : 2000A ACB @ site condition Derated about 1650A so vendor shall offer 2500A ACB to Meet the project condition. Confirmed |  |  |
|  | Documents Priority | All The equipment’s shall be engineered, designed, manufactured, tested and installed in accordance with the following standards: - Local Codes & Standards - Iranian Petroleum Standard (IPS) - International Codes & Standards - IEC (International Electro technical Commission) - BS (British Standard) - IEEE (Institute of Electrical and Electronics Engineers) - API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards and codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes and Standards. 4-Vendor technical offer | Confirmed Closed. |  |  |  |  |
|  | Scope of Supply | Minimum Scope of work and supply are in full compliance with Project MR (BK-GCS-PEDCO-120-EL-MR-0002). It has been Listed but not Limited to the following Items: - Full Engineering Services. - LV Switchgear 400V. - LV Capacitor Bank. - Inspection & Test ACC to ITP/QCP. - Site Supervisory Servicers (Optional). | Confirmed | 6-Relay setting and coordination table study should be added to Scope of work and supply. | Confirmed |  |  |
|  | Deviation List | Technical requirements shall be according to project specification in as minimum except those clearly specified in “deviation form”. BK-GNRAL-PEDCO-000-EL-DC-0001 (Electrical System Design Criteria) BK-GNRAL-PEDCO-000-EL-SP-0001 (Specification for LV Switchgear) BK-GNRAL-PEDCO-000-EL-SP-0012 (Specification for Capacitor Bank) | Confirmed | Not Acceptable Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR. ( project format attachment 3 page 14 ) | Confirmed Please modify deviation form acc. to attached file comments. (Extracted pages from BK-GCS-PEDCO-120-EL-MR-0002_D02) |  |  |
|  | General | Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR, TCL and codes & standards referred in the documents by issuing a New Deviation/Exception List With the respect to latest Modification and revised technical offer for purchaser's review and approval. Otherwise, the vendor must declare full compliance between all documents attached to the Inquiry package. (Native completed deviation form shall be filled by vendor) | Confirmed | Not Acceptable Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR. ( project format attachment 3 page 14 ) | Confirmed Please modify deviation form acc. to attached file comments. Extracted pages from BK-GCS-PEDCO-120-EL-MR-0002_D02 |  |  |
|  | General | Project Datasheet & TBE Table Shall be fill Out and return to purchaser. | Confirmed | Project document shall be stamp and return. | Confirmed Closed. |  |  |
|  | Vendor List | Vendor list & sub vendor list of manufacture shall be according to project AVL. Sub-vendor List for Electrical Equipment shall be submitted for review and approval in bid stage. These below items shall be specified: -Manufacture -Country of origin -Model | Confirmed | Not Acceptable we can’t find it pls resent again. | Confirmed Closed. |  |  |
|  | Spare Part | Spare Part for Commissioning and 2 Years Operation shall be Covered all requirement in Project Specification. Based on the E&C-QC-SP-1, Spare parts for pre-commissioning, commissioning/start up and spare parts for two years shall be submitted separately based on Spare Parts Specification. The supplied spare parts shall comply with the same specifications as the original parts and shall be interchangeable with the original parts without any modification. | Confirmed ( as an optional) | Not Acceptable Spare Part for Commissioning and 2 Years Operation shall be submitted in bid stage. | Confirmed pl. also add items as per attached SPARE PART LIST that are missed in blew list for ex. Trip coil for ACB and .... Confirmed |  |  |
|  | Special Tools | Any Special Tools for Life time Operation shall be included in technical offer. | Confirmed | Not Acceptable we can’t find it pls resent again. | Confirmed. Closed. |  |  |
|  | Specification | Vendor shall submit the reference and experience list (as a separate file) for design & manufacturing of LV switchgear. | Confirmed |  | Closed. |  |  |
|  | Shipment | Vendor shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification. | Confirmed |  | Closed. |  |  |
|  | catalogue | Catalogue for all proposed equipment shall be submitted. | Confirmed |  | Closed. |  |  |
|  | Specification | All of documents such as MR, data sheets and technical specification that received from purchaser shall be stamped and returned for client | Confirmed | Not Acceptable we can’t find it pls resent again. | Confirmed. Closed. |  |  |
|  | Specification | No more than two wires shall be connected to a terminal. please confirm. | Confirmed |  | Closed. |  |  |
|  | Specification | Signaling lamp shall be LED type. Please confirm | Confirmed |  | Closed. |  |  |
|  | Specification | Indoor lighting and also anti-condensation heater (with thermostat/hygrostat) shall be considered for all panels. Heater/s shall be protected by a miniature circuit breaker and an earth leakage protection device of 30mA sensitivity. | Confirmed Hygrostat is not considered |  | Hygrostat is considered. Closed. |  |  |
|  | Specification | Please specify heat dissipation for all switchgears. | Confirmed At detail stage |  | Closed. |  |  |
|  | Specification | All the following items shall be considered in proposal for all Air Circuit Breakers: Anti-pumping device, Mechanical operations counter, Shutter, Test & service status, Manual mechanical trip facility Closed/open position indication, Start/Stop & Emergency Stop push button, Charged/discharged spring indication, Emergency shutdown interposing relay and Minimum 4 numbers make contacts. | Confirmed |  | Under Voltage Release is added for ACB. Closed. |  |  |
|  | Specification | Each cubicle shall have a tag numbers for front and rear sides. | Confirmed |  | Closed. |  |  |
|  | Specification | Each circuit breaker shall be provided with a trip circuit supervision system complete with indicating lamp. | Protection relay have been considered as built-in type | Not Acceptable Vendor should be follow project document. | Confirmed Trip Circuit Supervision is added for incomings. Closed. |  |  |
|  | Specification | All LV motor starter feeders shall be equipped according to schematic typical drawing. | Confirmed |  | Closed. |  |  |
|  | Specification | Test blocks shall be considered for metering and protection equipment on front of panel. | Protection relay have been considered as built-in type | Not Acceptable Test blocks shall be considered for metering and protection equipment on front of panel. Vendor should be follow project document. | Confirmed. Closed. |  |  |
|  | Specification | Shape of main bus bars shall be flat. | Confirmed |  | Closed. |  |  |
|  | Specification | Epoxy cast resin shall be considered for voltage transformers. | NO, as Zafar Trans or Azmoon trans standard | Pls added in project deviation form. | OK Confirmed. Will be finalized based on client opinion. |  |  |
|  | Specification | Power consumption of 110VDC shall be specified by vendor for all switchgear. | Confirmed At detail stage |  | Closed. |  |  |
|  | Tests | Certificate or license, test reports and type test shall be submitted based on latest revision of related standard such as IP, short circuit level, temperature rise and etc by vendor after PO. | Confirmed |  | As per MC comment the mentioned Certificate or license shall be submitted at this stage. Please Refer to Appendix o |  |  |
|  | Arrangement | Vendor shall prepare preliminary substation arrangement drawing in this stage. | Confirmed | Closed. | pl. modify substation arrangement drawing as per attached file. Confirmed |  |  |
|  | Part List | Exact part list of the Switchgear including equipment name, brand, model and origin shall be submitted by vendor. Vendor is responsible for exact part list of the SWG | Confirmed |  | Closed. |  |  |
|  | I/O List | All required signals and mapping shall be submitted and considered From/To DCS base on "Electrical I/O Signal List BK-GCS-PEDCO-120-EL-LI-0005". Manufacture shall consider suitable relays / auxiliary contacts for this reason. Vendor shall confirm necessary facilities. Please follow Electrical I/O Signal List. | Confirmed |  | Closed. |  |  |
|  | Calculation | Burden of CT’ & PT’s will be finalized after purchase order based on the related calculation that will be submitted by Vendor and shall be approved by Purchaser. | Confirmed At detail stage |  | Closed. |  |  |
|  | Software | The software of the protection relay shall be provided with original license. | Protection relay have been considered as built-in type | Not Acceptable Vendor should be follow project document. | OK Confirmed Closed. |  |  |
|  | Protection Relay | All protection relays are equipped with key pan and LCD display, and 7 Numbers Digital input /7 Numbers Dry Output Contacts as minimum which is should be re-checked with schematic diagram. | Protection relay have been considered as built-in type | Not Acceptable Vendor should be follow project document. | OK, At detail stage. Closed. |  |  |
|  | Protection Relay | All relays supplied with LV switchgear shall be microprocessor based, which will facilitate a connection to DCS. Please confirm. | Protection relay have been considered as built-in type | Not Acceptable Vendor should be follow project document. | OK, At detail stage. Closed. |  |  |
|  | Protection Relay | Vendor shall perform programming of the relays based on requirements of typical & logic diagram. Related documents shall be submitted. | Protection relay have been considered as built-in type | Not Acceptable Vendor should be follow project document. | OK, At detail stage Closed. |  |  |
|  | Protection Relay | Vendor shall perform relay setting and relay coordination based on project relay coordination and setting study. | Protection relay have been considered as built-in type | Not Acceptable Vendor should be follow project document. | OK, At detail stage. Relay setting and coordination table study should be added to Scope of work and supply. Confirmed |  |  |
|  | Relay Connection | All digital multi meters and protection relays shall have Mod Bus (RS 485) communication protocol. | Protection relay have been considered as built-in type, So these item have been considered based on I/O list | Not Acceptable Vendor should be follow project document. | OK, At detail stage. Closed. |  |  |
|  | PT | Control circuit voltage for outgoing is 230 VAC which will be supplied for each LV cubicle. In other words for each LV cubicle one isolated dry type transformer shall be considered by vendor. | Confirmed | Closed. | Closed. |  |  |
|  | Notes | All notes in the page 2 of document “BK-GCS-PEDCO-120-EL-SL-0002” shall be considered by vendor. | Confirmed | Closed. | Closed. |  |  |
|  | Notes | Vendor shall consider "Control Logic Diagram for LV Incomers and Bus Tie" (BK-GCS-PEDCO-120-EL-LD-0001)" & "LV Switchgear/MCC Single Line Diagram (BK-GCS-PEDCO-120-EL-sl-0002)" as references for metering & schematic diagram of incomings. | Confirmed | Closed. | Closed. |  |  |
|  | Notes | All notes in the page 3 of document “BK-GCS-PEDCO-120-EL-DG-0002” shall be considered by vendor. | Confirmed | Closed. | Closed. |  |  |
|  | Arrangement | Rear access proposal shall be added to this offer as alternative 2 due to space limitation in switchgear building. | Confirmed | Both rear and front access shall be added to technical offer and substation arrangement layout. Confirmed |  |  |  |
|  | PEDCO Comments | Regarding issued deviation list for Fuse proposal: | -- |  | Closed. |  |  |
|  | PEDCO Comments | Item 1 is not acceptable: Design temperature shall be considered 52⁰C. | -- |  | Closed. |  |  |
|  | PEDCO Comments | Item 3 is acceptable in case of use of flash mounted earth fault relay. | -- |  | Closed. |  |  |
|  | PEDCO Comments | Item 4 is not acceptable. Built in protection relay are not acceptable. At the other hand protection functions 25, 50G, 86, 86T shall be considered separately. | -- |  | Closed. |  |  |
|  | PEDCO Comments | Item 5 is not acceptable, lamp test to be added. | -- |  | Closed. |  |  |
|  | PEDCO Comments | Item 6 is not acceptable, each cell shall have its control voltage transformer. | -- |  | Closed. |  |  |
|  | PEDCO Comments | Regarding issued deviation list for MPCB proposal: | -- |  | Closed. |  |  |
|  | PEDCO Comments | Item 1 is not acceptable: Design temperature shall be considered 52⁰C. | Confirmed |  | All equipment like ACB ,MCCB, MPCB, Contractor ,...rating shall be sized at site condition and mentioned the true size in this offer as below example : 2000A ACB @ site condition Derated about 1650A so vendor shall offer 2500A ACB to Meet the project condition. Confirmed |  |  |
|  | PEDCO Comments | Item 4 will be considered as alternative, in case of approval by NISOC this alternative will be accepted | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Item 5 is not acceptable, lamp test to be added. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Sub vendor list shall be submitted and following items shall be specified in sub vendor list: -Country of origin -Brand name | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Manufacturer and model No. for each feeder main equipment shall be added to issued part list. For example "Air Circuit Breaker ABB E3N-2000-x-x-x". | Confirmed | Repeated comment : Model No. for each feeder main equipment shall be added to issued part list . For example "Air Circuit Breaker ABB E3N-2000-x-x-x".INN Co Reply: our type for ABB :Emax E2.2 For Siemens : 3WL | I |  |  |
|  | PEDCO Comments | 2 years and Pre-Comm. & Commissioning Spare part shall be submitted based on project spare part instruction for below items separately: -LV switchgear -LV capacitor bank -MCC (2101A/2101B/2101C) | Confirmed | pl. also add items as per attached SPARE PART LIST that are missed in blew list for ex. Trip coil for ACB and .... Confirmed |  |  |  |
|  | PEDCO Comments | All catalogues of electrical equipment such as MPCB, protection relay, capacitor bank, Measuring center, alarm window, etc. shall be submitted at the Bid stage. | Confirmed | Repeated comment : All catalogues of electrical equipment such as MPCB, protection relay, capacitor bank, Measuring center, alarm window, etc. shall be submitted at the Bid stage. Confirmed |  |  |  |
|  | PEDCO Comments | Equipment list of each feeder (for incomings and couplers) and each type of outgoing feeders (for example Type M1, M2, F3, etc.) for GCS-400-NSWG-001 and MCC 2201A/B/C shall be added to technical offer in order to check each feeder separately in next revision. | At detail stage | Repeated comment : Equipment list of each feeder (for incomings and couplers) and each type of outgoing feeders (for example Type M1, M2, F3, etc.) for GCS-400-NSWG-001 and MCC 2201A/B/C shall be added to technical offer in order to check each feeder separately in next revision. INN Co Reply: after P.O at detail stage |  |  |  |
|  | PEDCO Comments | Some items has been missed in technical offer based on latest revision of project SLD such as transducer for P,Q and V, function 94 for incomings 1&2, function 81 for incoming 3. Protection functions shall be considered based on project SLD. For example tow lock out relay shall be considered for normal incoming (86 and 86T) or 50BF and 74TCS shall be added to protection relay. | Confirmed | Vendor is fully responsible to consider project requirement as per latest project document such as : SLD, datasheet and … Confirmed |  |  |  |
|  | NISOC Comments | دمای طراحی در این پیشنهاد بر اساس ۴۰ درجه مغایر با نیازمندیهای پروژه و مورد تایید نیست لذا اصلاحات لازم انجام گردد . | Confirmed | As per item 49. Confirmed |  |  |  |
|  | NISOC Comments | بررسی گردد آیا تجهیزات درون تابلو از قبیل ZAFAR/AZMOON جهت ساخت PT در لیست سازندگان قرار دارد. | OK Confirmed |  | Closed. |  |  |
|  | NISOC Comments | صرفا درصورت لحاظ استرایکرپین جهت پلههای بانک خازنی عدم استفاده از کنترل فاز جهت پله های بانک خازنی مورد تایید خواهد بود. | Confirmed | How do you perform this item in your technical offer? | Control phase Have been considered. |  |  |
|  | NISOC Comments | تست براساس الزامات 143-IPS-M-ELجهت تابلوها مدنظر قرار گیرد. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | استفاده از کلیدهای MPCB به جای ترکیب Disconnector Switch و رله Over Load جهت کلیه فیدرهای موتوری در صورتیکه برای فیدرهای با توان ۳۰ کیلووات و بالاتر (در صورت وجود) ، MPR در نظر گرفته شود مورد پذیرش می باشد. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | رله LOCK OUT RELAY & TRIP RELAY بصورت مجزا میبایست لحاظ گردد. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | مطابق الزامات استاندارد 143-IPS-M-EL برای هر سلول یک عدد thermostat/hygrostat جهت عملکرد گرم کننده های تابلوها ضروری است. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | بدلیل محدودیتهای فضای نصب ، OPENINGهای موجود سوئیچگیر فشار ضعیف ( ارتباط با گالری کابل ( مقتضی است اطلاعات ابعاد تابلوهای سازندگان براین اساس اصلاح و باجزئیات مکفی مستندات ارائه گردد ( نیاز به Dummy Panel و ...) | Please refer to General Arrangement |  | Closed. |  |  |
|  | NISOC Comments | جهت جلوگیری از وصل مکانیکی کلیدهای اصلی و ایجاد تداخل ، کلیدهای ACB مجهز به رله UNDR VOLTAGE RELEASE باشند. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | ظرفیت و مشخصات فنی تجهیزات درون تابلوها باید براساس شرایط حداکثر دمایی طراحی و تامین گردد. | Confirmed | As per item 49. Confirmed |  |  |  |
|  | NISOC Comments | جهت درک ابعاد دقیق تابلوهای پیشنهاد شده لازم است که ابعاد تابلوهای MCC و بانک خازنی پروژه بصورت یک نقشه منسجم ترسیم و ارائه شود و آیتم TBE-1-11 خلاصه پیشنهاد دهندگان جهت کلیه سازندگان ابعاد تابلوها قید شود لذا عبارت Acc The Offer مورد پذیرش نیست . | Please refer to General Arrangement | As per item 27. Confirmed |  |  |  |
|  | NISOC Comments | مطابق اظهار نظرات پیشین در کلیه مدارک TBE کالاهای ،پروژه تصویر صفحه مربوط به شرکت های پیشنهاد دهنده مندرج در لیست سازندگان مجاز AVL شامل اطلاعات کامل شرح محصول سازنده در لیست سازندگان (مجاز به مستندات ارسالی اضافه شود همواره شرح محصولات منطبق با کالای مربوطه توسط تیم بازرگانی مهندسی کنترل گردد و در صورت عدم تطابق کامل با شرح محصول از ارسال مدارک سازنده مذکور خودداری گردد در غیر اینصورت تبعات مربوطه بعهده پیمانکار است. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | ITP تابلوها براساس دستورالعمل جامع بازرسی خرید و ساخت کالا و ملاحضات IPS کالای مذکور میبایست توسط سازندگان مدنظر قرار گیرد لذا در این مقطع باید مدارک مذکور ملاک عمل و مورد پذیرش سازندگان قرارگیرد و جزئیات مربوطه پس از عقد قرارداد و با تائید کارفرما تعیین خواهد گردید. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | مطابق اظهار نظرات پیشین قطعات یدکی راه اندازی و راهبری دوسالانه براساس پیوست ۱۱ پیمان باید مورد صحه گذاری سازندگان قرار گیرد . لذادراین مقطع الزام به رعایت و ارائه قطعات یدکی پیشنهاد دهندگان براساس پیوست ۱۱ کفایت خواهد نمود . براین اساس ملاک پذیرش آیتم های مرتبط TBE به دستورالعمل تامین قطعات يدكي -1-E&C-QC-SP اشاره گردد. | Confirmed | pl. also add items as per attached SPARE PART LIST that are missed in blew list for ex. Trip coil for ACB and .... Confirmed |  |  |  |