| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Design Criteria | Vendor To confirm That All supplied material all in full compliance with Project site condition : - Min/Max air temperature = -5°C / 52°C - Relative humidity = 100% max at 52°C - Altitude = 12 m a.s.l. - Climate = Class 4 (Very High) Vendor shall submitted temperature de‐rating factors of equipment such as CB, etc. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated rated current be equal or higher than rate current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. | Confirmed |  | All equipment like ACB ,MCCB, MPCB, Contractor ,...rating shall be sized at site condition and mentioned the true size in this offer as below example : 2000A ACB @ site condition Derated about 1650A so vendor shall offer 2500A ACB to Meet the project condition. |  | Confirmed Closed. |
|  | Documents Priority | All The equipment’s shall be engineered, designed, manufactured, tested and installed in accordance with the following standards: - Local Codes & Standards - Iranian Petroleum Standard (IPS) - International Codes & Standards - IEC (International Electro technical Commission) - BS (British Standard) - IEEE (Institute of Electrical and Electronics Engineers) - API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards and codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes and Standards. 4-Vendor technical offer | Confirmed |  | Closed. |  |  |
|  | Scope of Supply | Minimum Scope of work and supply are in full compliance with Project MR (BK-GCS-PEDCO-120-EL-MR-0002). It has been Listed but not Limited to the following Items: - Full Engineering Services. - LV Switchgear 400V. - LV Capacitor Bank. - Inspection & Test ACC to ITP/QCP. - Site Supervisory Servicers (Optional). | Confirmed | 6-Relay setting and coordination table study should be added to Scope of work and supply |  |  | Confirmed Closed. |
|  | Deviation List | Technical requirements shall be according to project specification in as minimum except those clearly specified in “deviation form”. BK-GNRAL-PEDCO-000-EL-DC-0001 (Electrical System Design Criteria) BK-GNRAL-PEDCO-000-EL-SP-0001 (Specification for LV Switchgear) BK-GNRAL-PEDCO-000-EL-SP-0012 (Specification for Capacitor Bank) | Confirmed | Not Accseptable Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR. ( project format attachment 3 page 14 ) | Confirmed | Pl. resend deviation form, in project format. | Confirmed Closed. |
|  | General | Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR, TCL and codes & standards referred in the documents by issuing a New Deviation/Exception List With the respect to latest Modification and revised technical offer for purchaser's review and approval. Otherwise, the vendor must declare full compliance between all documents attached to the Inquiry package. (Native completed deviation form shall be filled by vendor) | Confirmed | Not Accseptable Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR. ( project format attachment 3 page 14 ) | Confirmed | Pl. resend deviation form, in project format. | Confirmed Closed. |
|  | General | Project Datasheet & TBE Table Shall be fill Out and return to purchaser. | Confirmed |  | Closed. |  |  |
|  | Vendor List | Vendor list & sub vendor list of manufacture shall be according to project AVL. Sub-vendor List for Electrical Equipment shall be submitted for review and approval in bid stage. These below items shall be specified: -Manufacture -Country of origin -Model | Confirmed |  | Closed. |  |  |
|  | Spare Part | Spare Part for Commissioning and 2 Years Operation shall be Covered all requirement in Project Specification. Based on the E&C-QC-SP-1, Spare parts for pre-commissioning, commissioning/start up and spare parts for two years shall be submitted separately based on Spare Parts Specification. The supplied spare parts shall comply with the same specifications as the original parts and shall be interchangeable with the original parts without any modification. | Confirmed |  | Closed. |  |  |
|  | Special Tools | Any Special Tools for Life time Operation shall be included in technical offer. | Confirmed |  | Closed. |  |  |
|  | Specification | Vendor shall submit the reference and experience list (as a separate file) for design & manufacturing of LV switchgear. | Confirmed |  | Closed. |  |  |
|  | Shipment | Vendor shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification. | Confirmed |  | Closed. |  |  |
|  | catalogue | Catalogue for all proposed equipment shall be submitted. | Confirmed For Main equipment |  |  |  |  |
|  | Specification | All of documents such as MR, data sheets and technical specification that received from purchaser shall be stamped and returned for client | Confirmed |  | Closed. |  |  |
|  | Specification | No more than two wires shall be connected to a terminal. please confirm. | Confirmed |  | Closed. |  |  |
|  | Specification | Signaling lamp shall be LED type. Please confirm | Confirmed |  | Closed. |  |  |
|  | Specification | Indoor lighting and also anti-condensation heater (with thermostat/hygrostat) shall be considered for all panels. Heater/s shall be protected by a miniature circuit breaker and an earth leakage protection device of 30mA sensitivity. | Confirmed |  | Closed. |  |  |
|  | Specification | Please specify heat dissipation for all switchgears. | Confirmed |  | Closed. |  |  |
|  | Specification | All the following items shall be considered in proposal for all Air Circuit Breakers: Anti-pumping device, Mechanical operations counter, Shutter, Test & service status, Manual mechanical trip facility Closed/open position indication, Start/Stop & Emergency Stop push button, Charged/discharged spring indication, Emergency shutdown interposing relay and Minimum 4 numbers make contacts. | Confirmed |  | Closed. |  |  |
|  | Specification | Each cubicle shall have a tag numbers for front and rear sides. | Confirmed |  | Closed. |  |  |
|  | Specification | Each circuit breaker shall be provided with a trip circuit supervision system complete with indicating lamp. | Confirmed |  | Closed. |  |  |
|  | Specification | All LV motor starter feeders shall be equipped according to schematic typical drawing. | Confirmed |  | Closed. |  |  |
|  | Specification | Test blocks shall be considered for metering and protection equipment on front of panel. | Confirmed |  | Closed. |  |  |
|  | Specification | Shape of main bus bars shall be flat. | Confirmed |  | Closed. |  |  |
|  | Specification | Epoxy cast resin shall be considered for voltage transformers. | Confirmed |  | Closed. |  |  |
|  | Specification | Power consumption of 110VDC shall be specified by vendor for all switchgear. | Confirmed |  | Closed. |  |  |
|  | Tests | Certificate or license, test reports and type test shall be submitted based on latest revision of related standard such as IP, short circuit level, temperature rise and etc by vendor after PO. | Confirmed | we can’t find it pls resent again. | Confirmed Closed. |  |  |
|  | Arrangement | Vendor shall prepare preliminary substation arrangement drawing in this stage. | After PO | Not Accseptable Vendor shall prepare preliminary substation arrangement drawing in this stage. | Confirmed we can’t find it pls send it. |  | Confirmed Closed. |
|  | Part List | Exact part list of the Switchgear including equipment name, brand, model and origin shall be submitted by vendor. Vendor is responsible for exact part list of the SWG | Confirmed |  | Closed. |  |  |
|  | I/O List | All required signals and mapping shall be submitted and considered From/To DCS base on "Electrical I/O Signal List BK-GCS-PEDCO-120-EL-LI-0005". Manufacture shall consider suitable relays / auxiliary contacts for this reason. Vendor shall confirm necessary facilities. Please follow Electrical I/O Signal List. | Confirmed |  | Closed. |  |  |
|  | Calculation | Burden of CT’ & PT’s will be finalized after purchase order based on the related calculation that will be submitted by Vendor and shall be approved by Purchaser. | Confirmed |  | Closed. |  |  |
|  | Software | The software of the protection relay shall be provided with original license. | Confirmed |  | Closed. |  |  |
|  | Protection Relay | All protection relays are equipped with key pan and LCD display, and 7 Numbers Digital input /7 Numbers Dry Output Contacts as minimum which is should be re-checked with schematic diagram. | Confirmed |  | Closed. |  |  |
|  | Protection Relay | All relays supplied with LV switchgear shall be microprocessor based, which will facilitate a connection to DCS. Please confirm. | Confirmed |  | Closed. |  |  |
|  | Protection Relay | Vendor shall perform programming of the relays based on requirements of typical & logic diagram. Related documents shall be submitted. | Confirmed |  | Closed. |  |  |
|  | Protection Relay | Vendor shall perform relay setting and relay coordination based on project relay coordination and setting study. | Confirmed |  | Closed. |  |  |
|  | Relay Connection | All digital multi meters and protection relays shall have Mod Bus (RS 485) communication protocol. | Confirmed |  | Closed. |  |  |
|  | PT | Control circuit voltage for outgoing is 230 VAC which will be supplied for each LV cubicle. In other words for each LV cubicle one isolated dry type transformer shall be considered by vendor. | Confirmed |  | Closed. |  |  |
|  | Notes | All notes in the page 2 of document “BK-GCS-PEDCO-120-EL-SL-0002” shall be considered by vendor. | Confirmed |  | Closed. |  |  |
|  | Notes | Vendor shall consider "Control Logic Diagram for LV Incomers and Bus Tie" (BK-GCS-PEDCO-120-EL-LD-0001)" & "LV Switchgear/MCC Single Line Diagram (BK-GCS-PEDCO-120-EL-sl-0002)" as references for metering & schematic diagram of incomings. | Confirmed |  | Closed. |  |  |
|  | Notes | All notes in the page 3 of document “BK-GCS-PEDCO-120-EL-DG-0002” shall be considered by vendor. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Switchgear arrangement layout in switchgear building shall be submitted at this stage by vendor to check free space, because of space limit in switchgear building. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Due to space limitation in switchgear building, proposal shall be submitted in two options: - Option one with Front access switchgears. - Option Two with Rear access switchgears. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Type test, test report and certificate has not been submitted. These documents shall be submitted at the Bid stage. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Deviation list shall be submitted in next revision. In case of Even if there is no deviation, it shall be clearly mentioned in deviation list and submitted by vendor. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | 2 years and Pre-Comm. & Commissioning Spare part lists shall be submitted based on project spare part instruction for below items separately: -LV switchgear -LV capacitor bank -MCC (2101A/2101B/2101C) | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Capacitor bank data sheet shall be filled completely and submitted at the Bid stage. For example items 12.1 to 12.3 shall be filled by vendor. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | All catalogues of electrical equipment such as ACB, MCCB, switch fuse, protection relay, capacitor bank, Measuring center, alarm window, etc. shall be submitted at the Bid stage. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | All descriptions about MV and GIS panels shall be deleted from submitted catalogue. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Some functions or equipment missed from technical offer, some of these items mentioned bellow, Vendor shall be considered all requested items as per MR attachments and no claim will be accepted after contract: | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Transducer for P,Q and V are required as per SLD, but these items have not been mentioned in the technical offer. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Accuracy class for voltmeter/ammeter and measuring unit shall be mentioned as per requisition. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | function 94 for incomings 1&2 shall be added to technical offer | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Function 81 for incoming 3 shall be added to the technical offer. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Function 25 shall be considered separately. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Ammeter shall be considered with selector switch for incomings 1,2and 3. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | motor starter modules shall be equipped with fuse disconector switch as per SLD but in the issued technical offer just fuses have been considered without disconnector switch. Therefor disconnector switch shall be added. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Regarding item 6-9-7 above replacing fuse disconnector switch with MPCB or MCCB can be proposed by Vendor as options. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Undervoltage release shall be considered for all ACB's based on NISOC comment. (Letter NO. 03/2294/291780 date 1403/07/29). Please clarify about mentioned "MN" in the items 2.8 of proposed part list tables for incomings and couplers. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Rating voltage of capacitor bank shall be considered 440V. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | 48X48 ammeter for incoming MCC (2101A/2101B/2101C) shall be replaced with 72X72mm or 98x98mm. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Motor starters for MCC-2110A/B/C shall be equipped with core balance CT and 50G relay as per SLD, these items have not been considered in the issued technical offer. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Each capacitor bank dimensions shall be specified in the technical proposal for capacitor banks. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Capacitor bank cooling shall be of natural air cooled design and using fan and filter is not permitted. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | مطابق اظهار نظرات پیشین داده برگ تکمیل شده سازنده باید براساس تعهدات پیمانکار توسط پیمانکار بررسی شود و نتیجه ارزیابی پیمانکار جهت هر آیتم (اشاره شده بصورت Acc To Tech Offer ) براساس ملاحضات استاندارد و پیمان جهت نهایی سازی به کارفرما ارائه شود | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | لیست انحرافات روئت نگردید مقتضی است بدلیل اهمیت موضوع در این مقطع ارائه شود . | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | نقشه lay out یکپارچه تابلوها جهت صحه گذاری ابعاد تابلوها با فضای موجود توسط سازنده میبایست ارائه شود و در غیر اینصورت پیشنهاد فنی قابل بررسی نیست | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | Inrush Reactor در فرم TBEبا اختصار C با مفهوم Clarification is Required مبهم است در این خصوص توضیح گردد . | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | وجود Capacitor Manufacturer ساخت شرکت Hydra و ولتمتر ساخت سازندگان Voltmeter: BEW Selecte RS در شرح محصولات AVL وزارت نفت بررسی و مستندات ارائه گردد. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | استفاده از کلیدهای MPCB به جای ترکیب Disconnector Switch و رله Over Load جهت کلیه فیدرهای موتوری در صورتیکه برای فیدرهای با توان ۳۰ کیلووات و بالاتر (در صورت وجود) ، MPR در نظر گرفته شود مورد پذیرش می باشد | Confirmed |  | Closed. |  |  |