| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Design Criteria | Vendor To confirm That All supplied material all in full compliance with Project site condition : - Min/Max air temperature = -5°C / 52°C - Relative humidity = 100% max at 52°C - Altitude = 12 m a.s.l. - Climate = Class 4 (Very High) Vendor shall submitted temperature de‐rating factors of equipment such as CB, etc. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated rated current be equal or higher than rate current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. | Design temperature: 40°C | Not Accseptable Vendor should be follow project document. | Confirmed. Closed. | All equipment like ACB ,MCCB, MPCB, Contractor ,...rating shall be sized at site condition and mentioned the true size in this offer as below example : 2000A ACB @ site condition Derated about 1650A so vendor shall offer 2500A ACB to Meet the project condition. | Confirmed It was considered for equipment except ACB according to catalog (ATTACH. 5) |
|  | Documents Priority | All The equipment’s shall be engineered, designed, manufactured, tested and installed in accordance with the following standards: - Local Codes & Standards - Iranian Petroleum Standard (IPS) - International Codes & Standards - IEC (International Electro technical Commission) - BS (British Standard) - IEEE (Institute of Electrical and Electronics Engineers) - API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards and codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes and Standards. 4-Vendor technical offer | Confirmed |  | Closed. |  |  |
|  | Scope of Supply | Minimum Scope of work and supply are in full compliance with Project MR (BK-GCS-PEDCO-120-EL-MR-0002). It has been Listed but not Limited to the following Items: - Full Engineering Services. - LV Switchgear 400V. - LV Capacitor Bank. - Inspection & Test ACC to ITP/QCP. - Site Supervisory Servicers (Optional). | Confirmed |  |  | 6-Relay setting and coordination table study should be added to Scope of work and supply. | Confirmed |
|  | Deviation List | Technical requirements shall be according to project specification in as minimum except those clearly specified in “deviation form”. BK-GNRAL-PEDCO-000-EL-DC-0001 (Electrical System Design Criteria) BK-GNRAL-PEDCO-000-EL-SP-0001 (Specification for LV Switchgear) BK-GNRAL-PEDCO-000-EL-SP-0012 (Specification for Capacitor Bank) | Confirmed | Not Acceptable Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR. ( project format attachment 3 page 14 ) | Please refer to Attach 1. | Please consider the comments on attached deviation form and reply them. | Confirmed Please refer to Attach 1. |
|  | General | Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR, TCL and codes & standards referred in the documents by issuing a New Deviation/Exception List With the respect to latest Modification and revised technical offer for purchaser's review and approval. Otherwise, the vendor must declare full compliance between all documents attached to the Inquiry package. (Native completed deviation form shall be filled by vendor) | Confirmed | Not Acceptable Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR. ( project format attachment 3 page 14 ) | Please refer to Attach 1. | Please consider the comments on attached deviation form and reply them | Confirmed Please refer to Attach 1. |
|  | General | Project Datasheet & TBE Table Shall be fill Out and return to purchaser. | Confirmed | Not Acceptable Project Data sheet Shall be fill Out and return to purchaser. | Please refer to Attach 2. Closed. |  |  |
|  | Vendor List | Vendor list & sub vendor list of manufacture shall be according to project AVL. Sub-vendor List for Electrical Equipment shall be submitted for review and approval in bid stage. These below items shall be specified: -Manufacture -Country of origin -Model | Please refer to clause 3 of technical proposal. |  | Closed. |  |  |
|  | Spare Part | Spare Part for Commissioning and 2 Years Operation shall be Covered all requirement in Project Specification. Based on the E&C-QC-SP-1, Spare parts for pre-commissioning, commissioning/start up and spare parts for two years shall be submitted separately based on Spare Parts Specification. The supplied spare parts shall comply with the same specifications as the original parts and shall be interchangeable with the original parts without any modification. | Confirmed |  | Closed. |  |  |
|  | Special Tools | Any Special Tools for Life time Operation shall be included in technical offer. | Confirmed |  | Closed. |  |  |
|  | Specification | Vendor shall submit the reference and experience list (as a separate file) for design & manufacturing of LV switchgear. | Confirmed |  | Closed. |  |  |
|  | Shipment | Vendor shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification. | Confirmed |  | Closed. |  |  |
|  | catalogue | Catalogue for all proposed equipment shall be submitted. | After Contract |  | Closed. |  |  |
|  | Specification | All of documents such as MR, data sheets and technical specification that received from purchaser shall be stamped and returned for client | Confirmed | Considering that the MR has been stamped, it is assumed that all the attachments are approved by vendor. | Confirmed | All MR and its attachment Shall be stamped and returned for client. | Confirmed Please refer to Attach 6. |
|  | Specification | No more than two wires shall be connected to a terminal. please confirm. | Confirmed |  | Closed. |  |  |
|  | Specification | Signaling lamp shall be LED type. Please confirm | Confirmed | Closed. | Closed. |  |  |
|  | Specification | Indoor lighting and also anti-condensation heater (with thermostat/hygrostat) shall be considered for all panels. Heater/s shall be protected by a miniature circuit breaker and an earth leakage protection device of 30mA sensitivity. | Confirmed | Closed. | Closed. |  |  |
|  | Specification | Please specify heat dissipation for all switchgears. | After Contract | Closed. | Closed. |  |  |
|  | Specification | All the following items shall be considered in proposal for all Air Circuit Breakers: Anti-pumping device, Mechanical operations counter, Shutter, Test & service status, Manual mechanical trip facility Closed/open position indication, Start/Stop & Emergency Stop push button, Charged/discharged spring indication, Emergency shutdown interposing relay and Minimum 4 numbers make contacts. | Anti-pumping device was not considered | Not Acceptable Vendor shall be followed client requirement. | Confirmed Closed. |  |  |
|  | Specification | Each cubicle shall have a tag numbers for front and rear sides. | Confirmed |  | Closed. |  |  |
|  | Specification | Each circuit breaker shall be provided with a trip circuit supervision system complete with indicating lamp. | Based on SLD | Not Acceptable Vendor shall be followed client requirement. | It is considered for incoming circuit breaker. Closed. |  |  |
|  | Specification | All LV motor starter feeders shall be equipped according to schematic typical drawing. | Confirmed | Closed. |  |  |  |
|  | Specification | Test blocks shall be considered for metering and protection equipment on front of panel. | Confirmed | Closed. |  |  |  |
|  | Specification | Shape of main bus bars shall be flat. | Confirmed | Closed. |  |  |  |
|  | Specification | Epoxy cast resin shall be considered for voltage transformers. | Confirmed | Closed. |  |  |  |
|  | Specification | Power consumption of 110VDC shall be specified by vendor for all switchgear. | From External | Closed. |  |  |  |
|  | Tests | Certificate or license, test reports and type test shall be submitted based on latest revision of related standard such as IP, short circuit level, temperature rise and etc by vendor after PO. | After Contract | Not Acceptable Vendor shall be followed client requirement. | Please refer to Attach 3. | Certificate or license, test reports and type test shall be submitted in this stage. | Confirmed Please refer to Attach 3. |
|  | Arrangement | Vendor shall prepare preliminary substation arrangement drawing in this stage. | After Contract | Not Acceptable Vendor shall prepare preliminary substation arrangement drawing in this stage | Please refer to Attach 4. | The DWG file is damaged and is not opened pl. send correct file with PDF format too. | Please refer to Attach 4. |
|  | Part List | Exact part list of the Switchgear including equipment name, brand, model and origin shall be submitted by vendor. Vendor is responsible for exact part list of the SWG | Please Refer to Technical Proposal. | Closed. |  | List of equipment for LV switchgears, Capacitor bank and MCC shall be specified separately. It's not clear in technical offer. Meanwhile every row that is not used in panels shall be deleted in table of equipment list. | Confirmed |
|  | I/O List | All required signals and mapping shall be submitted and considered From/To DCS base on "Electrical I/O Signal List BK-GCS-PEDCO-120-EL-LI-0005". Manufacture shall consider suitable relays / auxiliary contacts for this reason. Vendor shall confirm necessary facilities. Please follow Electrical I/O Signal List. | Confirmed | Closed. |  |  |  |
|  | Calculation | Burden of CT’ & PT’s will be finalized after purchase order based on the related calculation that will be submitted by Vendor and shall be approved by Purchaser. | Confirmed | Closed. |  |  |  |
|  | Software | The software of the protection relay shall be provided with original license. | Confirmed | Closed. |  |  |  |
|  | Protection Relay | All protection relays are equipped with key pan and LCD display, and 7 Numbers Digital input /7 Numbers Dry Output Contacts as minimum which is should be re-checked with schematic diagram. | Confirmed | Closed. |  |  |  |
|  | Protection Relay | All relays supplied with LV switchgear shall be microprocessor based, which will facilitate a connection to DCS. Please confirm. | Confirmed | Closed. |  |  |  |
|  | Protection Relay | Vendor shall perform programming of the relays based on requirements of typical & logic diagram. Related documents shall be submitted. | Is out of scope of work | Not Acceptable Vendor shall be followed client requirement | The values should be provided by the client and the initial settings of the relays are done in the factory. |  |  |
|  | Protection Relay | Vendor shall perform relay setting and relay coordination based on project relay coordination and setting study. | Is out of scope of work | Not Acceptable Vendor shall be followed client requirement | Confirmed | 6-Relay setting and coordination table study should be added to Scope of work and supply. | Confirmed |
|  | Relay Connection | All digital multi meters and protection relays shall have Mod Bus (RS 485) communication protocol. | Confirmed |  | Closed. |  |  |
|  | PT | Control circuit voltage for outgoing is 230 VAC which will be supplied for each LV cubicle. In other words for each LV cubicle one isolated dry type transformer shall be considered by vendor. | Confirmed |  | Closed. |  |  |
|  | Notes | All notes in the page 2 of document “BK-GCS-PEDCO-120-EL-SL-0002” shall be considered by vendor. | Confirmed |  | Closed. |  |  |
|  | Notes | Vendor shall consider "Control Logic Diagram for LV Incomers and Bus Tie" (BK-GCS-PEDCO-120-EL-LD-0001)" & "LV Switchgear/MCC Single Line Diagram (BK-GCS-PEDCO-120-EL-sl-0002)" as references for metering & schematic diagram of incomings. | Confirmed |  | Closed. |  |  |
|  | Notes | All notes in the page 3 of document “BK-GCS-PEDCO-120-EL-DG-0002” shall be considered by vendor. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Design temperature shall be considered 52⁰C and so item 7 of deviation list is not accepted. | Confirmed |  |  | All equipment like ACB ,MCCB, MPCB, Contractor ,...rating shall be sized at site condition and mentioned the true size in this offer as below example : 2000A ACB @ site condition Derated about 1650A so vendor shall offer 2500A ACB to Meet the project condition. | Confirmed It was considered for equipment except ACB according to catalog (ATTACH. 5) |
|  | PEDCO Comments | Switchgear arrangement layout in switchgear building shall be submitted at this stage by vendor to check free space, because of space limit in switchgear building. | Please refer to Attach 4. |  |  | The file is damaged please resend it. Please be informed offer that two alternative in arrangement layout for Rear and Font access should be submitted. | Please refer to Attach 4. |
|  | PEDCO Comments | Due to space limitation in switchgear building, proposal shall be submitted in two options: - Option one with Front access switchgears. - Option Two with Rear access switchgears. | According to data sheet and Attach 4 It is considered Front access. |  |  | The explanations provided in this TCL has priority over all other documents and vendor shall follow them. | Confirmed |
|  | PEDCO Comments | Type test, test report and certificate has not been submitted. These documents shall be submitted at the Bid stage. | Please refer to Attach 3. |  | Closed. |  |  |
|  | PEDCO Comments | Country of origin shall be mentioned in sub vendor list for each item. | Please refer to clause 3&4 of technical proposal. |  |  | Repeated comment : Country of origin do not mentioned in sub vendor list for each item. | Confirmed |
|  | PEDCO Comments | 2 years and Pre-Comm. & Commissioning Spare part shall be submitted based on project spare part instruction for below items separately: -LV switchgear -LV capacitor bank -MCC (2101A/2101B/2101C) | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | LV switchgear and Capacitor bank data sheet shall be filled completely and then submitted in next revision. | Please refer to Attach 2. |  | Closed. |  |  |
|  | PEDCO Comments | All catalogues of electrical equipment such as ACB, MCCB, switch fuse, protection relay, capacitor bank, Measuring center, alarm window, etc. shall be submitted by vendor. | Please refer to Attach 5. |  | Closed. |  |  |
|  | PEDCO Comments | List of equipment for LV switchgears, Capacitor bank and MCC shall be specified separately. It’s not clear in technical offer. Meanwhile every row that is not used in panels shall be deleted in table of equipment list. | It is considered according to RUNNIN SANAT format. |  |  | Not Acceptable The equipment list must be presented in such a way that the equipment for each panel is specified. So that it can be quickly tracked in case of discrepancies. | Confirmed |
|  | PEDCO Comments | Transducer for P,Q and V are required as per SLD, but these items have not been mentioned in the technical offer. | Transducer was not considered according to SLD. If it is not acceptable please Clarification for us. |  |  | 4-20m signal from MultiMate to DCS is shown in SLD please follow the comment and correct the tech. offer. | Confirmed |
|  | PEDCO Comments | Function 25 shall be considered separately. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | All sub vendors shall be selected from Ministry of Petroleum (MOP) approved vendor list. | Confirmed. Please refer to clause 5 of technical proposal. |  | Closed. |  |  |
|  | PEDCO Comments | Proposed panel width for each MCC (3000mm) is too big and it is not possible to installation in the considered space. Manufacturer to be proposed solution to reduce panel width. | Confirmed. It is modify in new version |  | Closed. |  |  |
|  | PEDCO Comments | Rating voltage of capacitor bank shall be considered 440V. | Confirmed |  | Closed. |  |  |
|  | PEDCO Comments | Technical justifications for deviations Item No's of 4 and 9 of deviation list shall be issued. | Confirmed |  | Closed. |  |  |
|  | NISOC Comments | براساس نوع مصارف و ملاحضات استانداردی Inrush Reactor در صورت نیاز باید در نظر گرفته شود | Inrush Reactor در تابلوهای بانک خازنی فشار متوسط کاربرد دارد. در صورت نیاز به راکتور برای بانک خازنی فشار ضعیف باید درصد هارمونیک مشخص گردد. |  |  | سازنده میبایست به صورت بدبینانه و با توجه به تجربیات گذشته اقدام به اضافه نمودن راکتور در پیشنهاد فنی خود نماید. | مورد تایید میباشد راکتور 7% لحاظ شد |
|  | NISOC Comments | درخصوص انحراف مطرح شده توسط سازنده مبنی بر عدم وجود کنتاکتهای fail safe جهت رلهای حفاظتی شفاف سازی گردد مشخص گردد که منظور سازنده مربوط کدام رله ها و جهت چه فانکشن هایی باشد. پس از شفاف سازی در این خصوص اظهار نظر خواهد شد. | لطفا به پیوست 4 مراجعه فرمایید |  |  | رله های حفاظتی میبایست حتما دارای کنتاکت fail safe باشند. | مورد تایید می باشد |
|  | NISOC Comments | رله Anti-pumping جهت ایمنی و جلوگیری از تداخل و وصل مجدد کلیدها مدنظر قرار گیرد. | مورد تایید می باشد |  | Closed. |  |  |
|  | NISOC Comments | علت مطرح نمودن انحرافات در خصوص MCCB/3P/LI was considered for capacitor Bank feeders و همچنین MCCB/3P/LI was considered for incoming circuit breaker in capacitor bank مشخص گردد، در هر صورت کلیدهای بانک خازنی می بایست مطابق با اسناد پیمان و الزامات استاندارد IPS در نظر گرفته شود. | بانک خازنی نول ندارد لذا نیازی به کلید 4P نمی باشد . مطابق با DATA SHEET حفاظتهای 49,50,51 برای کلید ورودی در نظر گرفته شد. |  | Closed. |  |  |
|  | NISOC Comments | سایز وایرینگ جهت کاربرد سیگنالینگ ۱٫۵ و سایز سیم سیستم کنترل و حفاظت ۲٫۵ ، سایز سیم خروجی CT چهار میلیمتر مربع لحاظ گردد. | مورد تایید می باشد |  | Closed. |  |  |
|  | NISOC Comments | دمای طراحی در این پیشنهاد بر اساس ۴۰ درجه مغایر با نیازمندیهای پروژه و مورد تایید نیست لذا اصلاحات لازم انجام گردد. | مورد تایید می باشد |  |  | کلیه تجهیزات تابلو میبایست بر اساس دمای طراحی 52 درجه دیریت گردد. | مورد تایید می باشد |
|  | NISOC Comments | لامپ تست براساس الزامات 143-IPS-M-ELجهت تابلوها مدنظر قرار گیرد | مورد تایید می باشد |  | Closed. |  |  |
|  | NISOC Comments | بدلیل محدودیتهای فضای نصب ، OPENINGهای موجود سوئیچگیر فشار ضعیف ( ارتباط با گالری کابل ( مقتضی است اطلاعات ابعاد تابلوهای سازندگان براین اساس اصلاح و باجزئیات مکفی مستندات ارائه گردد ( نیاز به Dummy Panel و ...) | لطفا به پیوست 4 مراجعه فرمایید |  |  | فایل خراب است و باز نمیشودلطفا مجددا فاییل اصلی و PDF ارسال گردد. | لطفا به پیوست 4 مراجعه فرمایید |
|  | NISOC Comments | مطابق با استاندارد 100-IPS-E-EL حفاظتهای کلیدهای ACB کلیدها میبایست از طریق رله های حفاظتی مجزا تامین گردد . | مورد تایید می باشد |  |  | در پیشنهاد فنی این مورد میبایست لحاظ گردد. | مورد تایید می باشد |
|  | NISOC Comments | جهت جلوگیری از وصل مکانیکی کلیدهای اصلی و ایجاد تداخل ، کلیدهای ACB مجهز به رله UNDR VOLTAGE RELEASE باشند | مورد تایید می باشد |  | Closed. |  |  |
|  | NISOC Comments | ظرفیت و مشخصات فنی تجهیزات درون تابلوها باید براساس شرایط حداکثر دمایی طراحی و تامین گردد. | مورد تایید می باشد |  |  | کلیه تجهیزات تابلو میبایست بر اساس دمای طراحی 52 درجه دیریت گردد. | مورد تایید می باشد |
|  | NISOC Comments | جهت درک ابعاد دقیق تابلوهای پیشنهاد شده لازم است که ابعاد تابلوهای MCC و بانک خازنی پروژه بصورت یک نقشه منسجم ترسیم و ارائه شود و آیتم TBE-1-11 خلاصه پیشنهاد دهندگان جهت کلیه سازندگان ابعاد تابلوها قید شود لذا عبارت Acc The Offer مورد پذیرش نیست . | لطفا به بند 5 دفترچه فنی ، قسمت Primary Outline and Opening Diagram مراجعه فرمایید |  | Closed. |  |  |
|  | NISOC Comments | استفاده از کلیدهای MPCB به جای ترکیب Disconnector Switch و رله Over Load جهت کلیه فیدرهای موتوری در صورتیکه برای فیدرهای با توان ۳۰ کیلووات و بالاتر (در صورت وجود) ، MPR در نظر گرفته شود مورد پذیرش می باشد | مورد تایید می باشد |  | Closed. |  |  |