# ATTACHMENT 3

## DEVIATIONS / EXCEPTIONS TO JOB SPECIFICATION

Requisition No.:

Description:

Equipment No.:

| Item No. | Description of proposed exception |  |  | Recommended revision to job specification | Reason for proposed exception | Effect on base proposal if CONTRACTOR rejects exception |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Specification for LV Switchgear -IPS-M-EL-143 | - | All wires shall have cable lugs and shall be terminated in clamp type terminals. | The screw type terminals were considered |  | closed |
| 2 | SLD | - | MCCB/4P/LSIG has been specified for incoming circuit breaker in capacitor bank. | MCCB/3P/LS0I was considered for incoming circuit breaker in capacitor bank. | MCCB 4P/LSIG is not required for the CAP. bank. Because it does not have a neutral. | Vendor shall consider 4P MCCB in this stage.it will finalized at detail design stage. |
| 3 | SLD | - | Type F3 has been specified for cap. Bank feeders. | MCCB/3P/LI was considered for cap. Bank feeders. | MCCB 4P is not required for the CAP. bank. Because it does not have a neutral. | Vendor shall consider 4P MCCB in this stage.it will finalized at detail design stage. |
| 4 | SLD | - | Switch fuse & load breaker switch has been specified for motor feeders. | MPCB was considered for motor feeders instead of Switch fuse & load breaker switch. | According to clause 69 of TCL. | closed |
| 5 | Data sheet for LV Switchgear | 3.24 | average thickness for painting has been specified 60-80 micron | average thickness for painting was considered 80-120 micron | According to IEC standard 100 (+/- 20) micron was considered | closed |
| 6 | Data sheet for LV Switchgear | 12.12 & 12.15 | Ammeter & Voltmeter has been specified class 1 and multi-meter has been specified class 0.5 | Ammeter & Voltmeter was considered class 1.5 and multi-meter was considered class class 1 |  | Ammeter & Voltmeter has been specified class 1 and multi-meter has been specified class 0.5 and vendor shall be confirmed this item at this stage. |
| 7 | Data sheet for LV Switchgear | 13.15 | Cable gland delivery has been specified | Only gland plate was considered for each panel and cable gland was omitted. |  | closed |
| 8 | Data sheet FOR LV CAPACITOR BANK | 12.1 | Inrush Reactor Required has been specified | Capacitor bank was considered according to SLD AND Inrush Reactor was not considered. |  | Vendor shall be followed the result of item 56 of TCL. |

Notes:

- The packing shall be thermofoil that is suitable for Land Freight in enclosed truck and indoor storage. In case wooden packing is required same can be provided at additional cost.

- For information of general data (thickness, RAL, degree of protection, accessibility, temperature, Altitude, ….) please refer to clause 5 of technical proposal.

- For manufacturers of proposed equipment (vendor list) please refer to Clause 3 of technical proposal.

- For the received documents please refer to clause 2 of this technical proposal.

- Busbar was considered copper with Silver plated only joints and heat-shrinkable tubing and tapes insulation.

- The rated of equipment in each feeder were considered according to SLD.

- The name plate and labels were considered laminated plastic and sticky type with white letter on black background.

- The screw type terminals were considered.

- Test box was considered only for protection relays.

- The rating current of busbar was considered according to SLD.