| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| TBE FOR LV SWITCHGEAR, MCC & LV CAPACITOR BANK نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |
| D00 | Oct. 2023 | IFI | H.Shakiba | M.Fakharian | M.Sadeghian |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | Client Approval |
| Class:3 |  | Client Doc. Number: F0Z-709330 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for Client Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  |  |  |  | 51 |  |  |  |  |  |
| 2 | X |  |  |  |  |  | 52 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 53 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 54 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 55 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 56 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 57 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 58 |  |  |  |  |  |
| 9 | X |  |  |  |  |  | 59 |  |  |  |  |  |
| 10 | X |  |  |  |  |  | 60 |  |  |  |  |  |
| 11 | X |  |  |  |  |  | 61 |  |  |  |  |  |
| 12 | X |  |  |  |  |  | 62 |  |  |  |  |  |
| 13 | X |  |  |  |  |  | 63 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 64 |  |  |  |  |  |
| 15 | X |  |  |  |  |  | 65 |  |  |  |  |  |
| 16 | X |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 | X |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 | X |  |  |  |  |  | 68 |  |  |  |  |  |
| 19 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

| # TBE for LV Switchgear |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MR | PMR For LV Switchgear, MCC & LV Capacitor Bank (BK-GCS-PEDCO-120-EL-MR-0002) | Purchaser Requirement | Vendor 1 | Status | Vendor 2 | Status | Vendor 3 | Status |
| Item | Description |  |  |  |  |  |  |  |
| - General |  |  |  |  |  |  |  |  |
|  | Name of Project / Plant | Binak Oilfield in Bushehr Province | A |  |  |  |  |  |
|  | Reference Doc. | - IPS-M-EL-143(3) - LV Switchgear/MCC Single Line Diagram (BK-GCS-PEDCO-120-EL-SL-0002) - Specification For LV Switchgear & Motor Control Centers (BK-GNRAL-PEDCO-000-EL-SP-0001) - Electrical Typical Schematic Diagrams For LV Panel (BK-GCS-PEDCO-120-EL-DG-0002) - Electrical System Design Criteria (BK-GNRAL-PEDCO-000-EL-DC-0001) Process Basis of Design (BK-GNRAL-PEDCO-000-PR-DB-0001) | A |  |  |  |  |  |
|  | Manufacturer of Cubicles | By Vendor | Taban Tablo Co. |  |  |  |  |  |
|  | Manufacturer Type No./Country Origin | By Vendor | SIVACON 8PT |  |  |  |  |  |
|  | Standard | IEC60439, IEC60947, IPS-M-EL-143(3) | A |  |  |  |  |  |
|  | Type Of Cubicle - Fixed/ With draw able | With Draw Able | A |  |  |  |  |  |
|  | Rated Voltage & Variation | 400 VAC & ± 10% | A |  |  |  |  |  |
|  | Rated Frequency & Variation | 50 HZ & ± 5% | A |  |  |  |  |  |
|  | Service Voltage | 400 VAC | A |  |  |  |  |  |
|  | Number Of Phases | 3PH + PE + N | A |  |  |  |  |  |
|  | Number of Cubicles (With Spare) | By Vendor | Pls refer to our technical offer |  |  |  |  |  |
|  | Number of Bus Sections | 3 | A |  |  |  |  |  |
|  | Power Frequency (One Min) | 1.89 KV (ACC to Table 8 of IEC 61439-1) | A |  |  |  |  |  |
|  | Impulse Withstand | 6 KV (ACC to Table G.1 of IEC 61439-1) | A |  |  |  |  |  |
|  | Rated Normal Current of Bus bars | 2000 A | A |  |  |  |  |  |
|  | Rated Short Current of Bus bars | 50 KA | A |  |  |  |  |  |
|  | Rated Peak Withstand Current | 125 KA | A |  |  |  |  |  |
|  | Rated Short Time Duration | 1 SEC. | A |  |  |  |  |  |
|  | System Earthing | Solidly Earthed At Transformer Neutral Point | A |  |  |  |  |  |
|  | Voltage of Control Circuit | Incoming/Tie: 110 VDC Outgoing: 230 VAC (by Isolation Transformer for each Cubicle, According to BK-GCS-PEDCO-120-EL-SL-0002 | A |  |  |  |  |  |
|  | Incoming Feeder Signaling Circuit | 110 VDC | A |  |  |  |  |  |
|  | Motor & Heater Outgoing Feeder Signaling Circuit | 230 VAC | A |  |  |  |  |  |
|  | Distribution Outgoing Feeder Signaling Circuit | 230 VAC | A |  |  |  |  |  |
|  | Panel Light Auto. Door Micro Switch Operated | 230 VAC | A |  |  |  |  |  |
|  | Internal Safety Interlocks | Yes | A |  |  |  |  |  |
| - Environmental Conditions (Process Basis Design, BK-GNRAL-PEDCO-000-PR-DB-0001) |  |  |  |  |  |  |  |  |
|  | Installation | Indoor, Safe Area | A |  |  |  |  |  |
|  | Max. Ambient Temperature | 52 °C | A |  |  |  |  |  |
|  | Min. Ambient Temperature | 5 °C | A |  |  |  |  |  |
|  | Relative Humidity (Max.) | 100% | A |  |  |  |  |  |
|  | Climate | Corrosive, Hot Atmosphere | A |  |  |  |  |  |
|  | Altitude Above Sea Level | 12.5 m | A |  |  |  |  |  |
| - Cubicle Construction |  |  |  |  |  |  |  |  |
|  | Enclosure | Metal Clad | A |  |  |  |  |  |
|  | Indoor / Outdoor | Indoor | A |  |  |  |  |  |
|  | Type of Installation | Floor Standing | A |  |  |  |  |  |
|  | Bus Bar Material | Hard Drown, High Conductivity Copper | A |  |  |  |  |  |
|  | Main Bus Bar Insulation Material | Flame Retardant, Non Hygroscopic Insulation Material | A |  |  |  |  |  |
|  | Bus Bar color | L1: Red , L2: Yellow , L3: Blue , N: Black | A |  |  |  |  |  |
|  | Shape of Main Bus Bars | By Vendor | 2*80*10 Per phase |  |  |  |  |  |
|  | Neutral Bus Bar Cross Section | By Vendor | 1*80*10 |  |  |  |  |  |
|  | Type / Material of Main Bus Bar Supporting Insulators | By Vendor | 1*40*10 |  |  |  |  |  |
|  | Bus Bar Joints | Silver Plated | Tin plated (Main busbar, not only joint) |  |  |  |  |  |
|  | Bus Bar Identification | By Vendor | Lable |  |  |  |  |  |
|  | Bus Bar Arrangement (Single / Duplicate) | By Vendor | Duplicate |  |  |  |  |  |
|  | Phase Bus Bar Cross Section | By Vendor | 2*80*10 Per phase |  |  |  |  |  |
|  | Earth Bus Bar Cross Section | By Vendor | 1*40*10 |  |  |  |  |  |
|  | Bus bar Cooling Method | Air Natural | A |  |  |  |  |  |
|  | Rear / Front Access | Front Access | A |  |  |  |  |  |
|  | Incomings / Outgoings To/From The Switchgear (Bus-Duct/Cable) | Incomings: Cable Outgoings: Cable | A |  |  |  |  |  |
|  | Top / Bottom Entry | Cable: Bottom | A |  |  |  |  |  |
|  | Degree of Protection | IP42 | A |  |  |  |  |  |
|  | Min. Cubicle Sheet & Door Thickness For Enclosure | 2 mm | 2 mm for body enclosure |  |  |  |  |  |
|  | Tropic Design | Yes | A |  |  |  |  |  |
|  | Provision For Extension at Each End of Switchgear | Yes | A |  |  |  |  |  |
|  | Paint Color Shade | Ral 7032 (Light Grey) | A |  |  |  |  |  |
|  | Thickness of Paint Coating | 60 – 80 Micron | A |  |  |  |  |  |
| - Circuit Breaker (ACB) |  |  |  |  |  |  |  |  |
|  | Manufacturer / Country | By Vendor | ABB |  |  |  |  |  |
|  | Manufacturer Type No. | By Vendor | EMAX |  |  |  |  |  |
|  | Type Of Main CB (Air / Vacuum / Others) | Air | A |  |  |  |  |  |
|  | No. of Poles in Main ACB | 4 Pole | A |  |  |  |  |  |
|  | Rated Insulation Voltage | 1000 VAC | A |  |  |  |  |  |
|  | Rated Operating Voltage | 400 VAC | A |  |  |  |  |  |
|  | Rated Current | By Vendor, Based on Load List (BK-GCS-PEDCO-120-EL-LI-0001) | A |  |  |  |  |  |
|  | Rated Breaking Current * | 50 KA | A |  |  |  |  |  |
|  | Rated Making Current * | 125 KA | A |  |  |  |  |  |
|  | S/C Withstanding Time | 1 SEC. | A |  |  |  |  |  |
|  | Closing Time | By Vendor | 5-10mS |  |  |  |  |  |
|  | Tripping Time | By Vendor | 3mS |  |  |  |  |  |
|  | Rated Electrical Life | By Vendor | 10000 |  |  |  |  |  |
|  | Rated Short Circuit Life | By Vendor | - |  |  |  |  |  |
|  | Power Consumption of Closing Coil | By Vendor | 5~10W |  |  |  |  |  |
|  | Power Consumption of Tripping Coil | By Vendor | 5~10W |  |  |  |  |  |
|  | Power Consumption of Spring Charging Motor | By Vendor | 60~90W |  |  |  |  |  |
|  | Spring Charge Motor Voltage Supply | 110 VDC | A |  |  |  |  |  |
|  | No. of Circuit Breaker Operating With Charged Spring | 5 | A |  |  |  |  |  |
|  | Anti-Pumping Feature | Yes | A |  |  |  |  |  |
|  | Shutters | Yes | A |  |  |  |  |  |
|  | Additional Auxiliary Contacts | By Vendor | By Aux Relay |  |  |  |  |  |
|  | Mechanical Operations Counter | By Vendor | Will be considered |  |  |  |  |  |
|  | Manual Mechanical Trip Facility | By Vendor | Will be considered |  |  |  |  |  |
|  | Closed/Open Position Indication | Yes | A |  |  |  |  |  |
|  | Charged/Discharged Spring Indication | Yes | A |  |  |  |  |  |
|  | No. of Make Contacts | By Vendor | - |  |  |  |  |  |
|  | No. of Break Contacts | By Vendor | - |  |  |  |  |  |
|  | Rated Current at Voltage (By Vendor) | By Vendor | 5 |  |  |  |  |  |
|  | Weight of One Unit | By Vendor | 80 |  |  |  |  |  |
| - MCCB |  |  |  |  |  |  |  |  |
|  | Manufacturer of MCCB | By Vendor | ABB/TMAX |  |  |  |  |  |
|  | Rated Insulation Voltage | 1000 VAC | A |  |  |  |  |  |
|  | Rated Operating Voltage | 400 VAC | A |  |  |  |  |  |
|  | Rated Current | According to “BK-GCS-PEDCO-120-EL-SL-0002” | A |  |  |  |  |  |
|  | NO. of Poles | According to “BK-GCS-PEDCO-120-EL-SL-0002” | A |  |  |  |  |  |
| - Switch-Fuse |  |  |  |  |  |  |  |  |
|  | Manufacturer of Switch-Fuse | By Vendor | ABB or ETI |  |  |  |  |  |
|  | Rated Insulation Voltage | 1000 VAC | A |  |  |  |  |  |
|  | Rated Operating Voltage | 400 VAC | A |  |  |  |  |  |
|  | Rated Current | According to “BK-GCS-PEDCO-120-EL-SL-0002” | A |  |  |  |  |  |
|  | NO. of Poles | 3 Pole | A |  |  |  |  |  |
| - Contactor |  |  |  |  |  |  |  |  |
|  | Manufacturer Country | By Vendor | ABB/AC3 |  |  |  |  |  |
|  | Manufacturer Type No. | By Vendor | AC3 |  |  |  |  |  |
|  | Type of Contactor (Air / Vacuum) | Air/AC3 | A |  |  |  |  |  |
|  | Rated Insulation Voltage | 1000 VAC | A |  |  |  |  |  |
|  | Rated Operating Voltage | 400 VAC | A |  |  |  |  |  |
|  | Rated Current | By Vendor, Based On SLD | A |  |  |  |  |  |
|  | Closing Time | By Vendor | 4~7mS |  |  |  |  |  |
|  | Tripping Time | By Vendor | 3~5 mS |  |  |  |  |  |
|  | Power Consumption of Elec. Bobbin | By Vendor | 2W |  |  |  |  |  |
|  | Rated Electrical Life | By Vendor | 15000 |  |  |  |  |  |
|  | Rated Short Circuit Life | By Vendor | 20000 |  |  |  |  |  |
|  | Elect. Bobbin Voltage Supply | 230 VAC | A |  |  |  |  |  |
|  | Utilization Category | By Vendor | AC3 |  |  |  |  |  |
|  | RC Element | Where Is Applicable | A |  |  |  |  |  |
|  | Weight of One Unit | By Vendor | 450g |  |  |  |  |  |
|  | NO. of Poles | 3 Pole | A |  |  |  |  |  |
| - Thermal Relays |  |  |  |  |  |  |  |  |
|  | Manufacturer Country | By Vendor | ABB |  |  |  |  |  |
|  | Manufacturer Type No. | By Vendor | Thermal |  |  |  |  |  |
|  | Rated Operating Voltage | 400 VAC | A |  |  |  |  |  |
|  | Single Phasing Protection | Yes | A |  |  |  |  |  |
|  | Thermal Relay Adjustable Range | By Vendor ( ACC to Coordination type 2 ) , According to “BK-GCS-PEDCO-120-EL-SL-0002” | A |  |  |  |  |  |
|  | Thermal Relay Reset Feature | Yes Via a Door Mounted Push-Button | A |  |  |  |  |  |
| - APT'S-FIXED TYPE |  |  |  |  |  |  |  |  |
|  | Manufacturer Country | By Vendor | AZMOON TRANS |  |  |  |  |  |
|  | Manufacturer Type No. | By Vendor | Window |  |  |  |  |  |
|  | Rated Operating Voltage | 400/3 VAC | A |  |  |  |  |  |
|  | Rated Secondary Voltage | 110/3 VAC , 230/3 VAC | A |  |  |  |  |  |
|  | Accuracy Class | Measuring : 1 Protection : 3P | A |  |  |  |  |  |
|  | Burden | By Vendor | 15VA (After P.O by PT Calculation) |  |  |  |  |  |
|  | Single-Phase / Three-Phase | 3 Phase | A |  |  |  |  |  |
|  | Type of Construction | By Vendor | - |  |  |  |  |  |
|  | Rated Voltage Factor | By Vendor | 230 |  |  |  |  |  |
|  | Dimension (L x W x H) | By Vendor | After construction |  |  |  |  |  |
|  | Weight | By Vendor | 2200g |  |  |  |  |  |
| - CTs |  |  |  |  |  |  |  |  |
|  | Manufacturer Country | By Vendor | Mag |  |  |  |  |  |
|  | Manufacturer Type No. | By Vendor | Window type |  |  |  |  |  |
|  | Rated Operating Voltage | 400 VAC | A |  |  |  |  |  |
|  | Rated Primary Current | By Vendor, Based on SLD | A |  |  |  |  |  |
|  | Rated Secondary Current | 1 A | A |  |  |  |  |  |
|  | Insulation Class | By Vendor | F |  |  |  |  |  |
|  | Accuracy Class | Measuring: 1 Protection: 5P10 | A |  |  |  |  |  |
|  | Max. Thermal Withstand Current | By Vendor | 1.2 |  |  |  |  |  |
|  | Burden | By Vendor | After CT Calculation |  |  |  |  |  |
|  | Type of Construction | Cast Resin | A |  |  |  |  |  |
|  | Type of Installation | FIX | A |  |  |  |  |  |
|  | Dimension (L X W X H) | By Vendor | - |  |  |  |  |  |
|  | Weight | By Vendor | - |  |  |  |  |  |
| - Protection |  |  |  |  |  |  |  |  |
|  | Manufacturer Country | By Vendor | Schneider |  |  |  |  |  |
|  | Manufacturer Designation No. | By Vendor | EASSERGY |  |  |  |  |  |
|  | Type of Protection Relays For Incomers/Tie | Multi-Function, Microprocessor Based | P3 |  |  |  |  |  |
|  | No. of Contacts | MIN. 4 | A |  |  |  |  |  |
|  | Contact Rating Current | 5 A | A |  |  |  |  |  |
|  | Auto Diagnostic & Self Supervision | Yes | A |  |  |  |  |  |
|  | Serial Link Communication Port | Yes | A |  |  |  |  |  |
| - Measuring & Control System |  |  |  |  |  |  |  |  |
|  | Manufacturer of Indicators / Country | By Vendor | A |  |  |  |  |  |
|  | Accuracy Class Of Indicators | CL.1 | A |  |  |  |  |  |
|  | Manufacturer of Selector Switch | By Vendor | TRS / RAAD |  |  |  |  |  |
|  | Manufacturer of Push Buttons | By Vendor | RAAD |  |  |  |  |  |
|  | Manufacturer of Indication Lamps | By Vendor | RAAD |  |  |  |  |  |
|  | Manufacturer of Terminals | By Vendor | RAAD |  |  |  |  |  |
|  | Manufacturer of AUX. Relays | By Vendor | Omron |  |  |  |  |  |
|  | Remote Control Indication / Alarm / Intertrip / ETC. | Yes | A |  |  |  |  |  |
|  | Mimic Diagram | Not Applicable | A |  |  |  |  |  |
|  | Size of Control Wiring | 2.5 mm2 for CT'S 1.5 mm2 for Other | A |  |  |  |  |  |
|  | Ammeter / Voltmeter Manufacture | By Vendor | BEW |  |  |  |  |  |
|  | Ammeter / Voltmeter Class | CL.1 | A |  |  |  |  |  |
|  | Ammeter / Voltmeter range | According to “BK-GCS-PEDCO-120-EL-SL-0002” | A |  |  |  |  |  |
|  | Multi Meters Manufacture | By Vendor | DM6200 Schneider |  |  |  |  |  |
|  | Multi Meters Class | CL.0.5 | A |  |  |  |  |  |
|  | Transducer Model & Manufacturer | By Vendor | Multi transducer |  |  |  |  |  |
| - Miscellaneous |  |  |  |  |  |  |  |  |
|  | Routine Tests Foreseen | Yes | A |  |  |  |  |  |
|  | Type Tests Foreseen | No, If Certified | A |  |  |  |  |  |
|  | Two Years Op. & Comis. Spare Parts Proposed | Yes | A |  |  |  |  |  |
|  | Special Tools | Yes, If Required | A |  |  |  |  |  |
|  | Accessories | Yes | A |  |  |  |  |  |
|  | Mimic Diagram for Each Cubicle | Yes for Incoming | A |  |  |  |  |  |
|  | Dimension of One Cubicle (H X W X D) | By Vendor | 2200*800*600/800 mm |  |  |  |  |  |
|  | Overall Dimension (H X W X D) | By Vendor | After detail design |  |  |  |  |  |
|  | Weight of One Cubicle | By Vendor | 250~320 Kg per cell |  |  |  |  |  |
|  | Total Weight of Cubicles | By Vendor | After detail design & Construction |  |  |  |  |  |
|  | Dynamic Load of One Cubicle | By Vendor | - |  |  |  |  |  |
|  | Time Schedule Prepared | By Vendor | After P.O |  |  |  |  |  |
|  | Delivery Time | By Vendor | 3months |  |  |  |  |  |
|  | Any Deviations From Spec. | By Vendor | As attached |  |  |  |  |  |
|  | Cable Gland Delivery | Yes | A |  |  |  |  |  |
| - Accessories |  |  |  |  |  |  |  |  |
|  | Illumination (Y/N) | Yes | A |  |  |  |  |  |
|  | Lifting Lugs (Y/N) | Yes | A |  |  |  |  |  |
|  | Space Heater With Thermostat (Y/N) | Yes | A |  |  |  |  |  |
|  | Humidity Control System (Y/N) | Yes | A |  |  |  |  |  |
|  | Mimic Diagram (Y/N) | Yes | A |  |  |  |  |  |
|  | C.B. Position Indicator | Yes | A |  |  |  |  |  |
|  | Door Key (Y/N) | Yes | A |  |  |  |  |  |
|  | C.B. Charging / Retracting (Y/N) | Yes | A |  |  |  |  |  |
|  | Installation Kit (Y/N) | Yes | A |  |  |  |  |  |
|  | Voltage and Current Test Block for Protection Relays (Y/N) | Yes | A |  |  |  |  |  |
|  | Lamp Test Facility (Y/N) | Yes | A |  |  |  |  |  |
|  | Automatic Shutter (Y/N) | Yes | A |  |  |  |  |  |
|  | Floor Frame (Y/N) | Yes | A |  |  |  |  |  |
|  | C.B. Transfer Trolley (Y/N) | Yes | A |  |  |  |  |  |
|  | Name Plate & Front Tag & Rear Side Tag (Y/N) | Yes | A |  |  |  |  |  |
|  | Telescopic Rotary Handle for MCCB(Y/N) | Yes | A |  |  |  |  |  |
| - Mechanical Interlock |  |  |  |  |  |  |  |  |
|  | Door Shall Not Able To Open When C.B. Is Closed | Yes | A |  |  |  |  |  |
|  | Impossibility of C.B. Rack-In / Rack-Out When C.B. Is Closed | Yes | A |  |  |  |  |  |
|  | Padlock for C.B. | Yes | A |  |  |  |  |  |
|  | MCCB Open / Close From Closed Door Through Lockable Telescopic Rotary Handle | Yes | A |  |  |  |  |  |
| - Panel Space Heater Technical Data |  |  |  |  |  |  |  |  |
|  | Type No. | By Vendor | LOCAL |  |  |  |  |  |
|  | Control Type | By Vendor | MCB |  |  |  |  |  |
|  | Protection Type | By Vendor | MCB |  |  |  |  |  |
|  | Voltage | 230 VAC | A |  |  |  |  |  |
|  | Power Consumption | By Vendor | 100W |  |  |  |  |  |
| - Panel Light Technical Data |  |  |  |  |  |  |  |  |
|  | Type No. | By Vendor | LOCAL |  |  |  |  |  |
|  | Control Type | By Vendor | MCB |  |  |  |  |  |
|  | Protection Type | By Vendor | MCB |  |  |  |  |  |
|  | Voltage | 230 VAC | A |  |  |  |  |  |
|  | Power Consumption | By Vendor | 60 |  |  |  |  |  |

| # TBE for LV Capacitor Bank |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MR | PMR For LV Switchgear, MCC & LV Capacitor Bank (BK-GCS-PEDCO-120-EL-MR-0002) | Purchaser Requirement | Vendor 1 | Status | Vendor 2 | Status | Vendor 3 | Status |
| Item | Description |  |  |  |  |  |  |  |
| - General Information |  |  |  |  |  |  |  |  |
|  | Quantity | 1 Set for Each LV Switchgear (Note 2) | A |  |  |  |  |  |
|  | Tag Numbers | CB01 & CB02 | A |  |  |  |  |  |
|  | Applicable Standards | IEC 60831 IPS-M-EL-181(2) IPS-M-EL-143(3) | A |  |  |  |  |  |
|  | Applicable Document | BK-GNRAL-PEDCO-000-EL-SP-0012 BK-GCS-PEDCO-120-EL-CN-0011 BK-GNRAL-PEDCO-000-EL-SP-0001 | A |  |  |  |  |  |
|  | Manufacturer's Name | By Vendor | TABAN TABLO |  |  |  |  |  |
| - Environmental Conditions (Process Basis Design, BK-GNRAL-PEDCO-000-PR-DB-0001) |  |  |  |  |  |  |  |  |
|  | Location | Binak Oilfield in Bushehr Province | A |  |  |  |  |  |
|  | Hazardous Area Classification | Safe | A |  |  |  |  |  |
|  | Max. Outdoor Ambient Temperature | 55C | A |  |  |  |  |  |
|  | Minimum Indoor Ambient Temp. | -5°C | A |  |  |  |  |  |
|  | Maximum Indoor Relative Humidity | 100% | A |  |  |  |  |  |
|  | Altitude (Above Sea Level) | 12.5 m | A |  |  |  |  |  |
|  | Seismic Factor | Zone 3 | A |  |  |  |  |  |
|  | Installation | Indoor | A |  |  |  |  |  |
| - Electrical Data |  |  |  |  |  |  |  |  |
|  | System Voltage | 400V AC ±10% | A |  |  |  |  |  |
|  | System Frequency | 50 Hz ±5% | A |  |  |  |  |  |
|  | No. of Phases | 3 | A |  |  |  |  |  |
|  | Control Voltage | 230 VAC | A |  |  |  |  |  |
|  | Space Heater Voltage | 230 VAC | A |  |  |  |  |  |
|  | Bus-Bar Rated Current | 315A | A |  |  |  |  |  |
|  | Short Time Withstand Current | 50 kA, 1 Sec. | A |  |  |  |  |  |
|  | Bus-Bars Material | Heat Shrink Copper | COLOR |  |  |  |  |  |
|  | Bus-Bars Joints | Silver Plated | Tin plated (Main busbar, not only joint) |  |  |  |  |  |
| - Enclosure Data |  |  |  |  |  |  |  |  |
|  | Enclosure Type | Free Standing/Fixed Type / Front Access | A |  |  |  |  |  |
|  | Degree of Protection | IP 42 | A |  |  |  |  |  |
|  | Cable Entry | Bottom (by Cable Gland) | A |  |  |  |  |  |
|  | Type & Size of Power Cable | According to “BK-GCS-PEDCO-120-EL-CN-0003” ( 4C×120 mm2 CU/XLPE/SWA/PVC ) | A |  |  |  |  |  |
|  | Control Cable | 2×(5C× 4 mm2) for Current & Voltage Sample | A |  |  |  |  |  |
|  | Material | Painted Sheet Steel | A |  |  |  |  |  |
|  | Color | RAL 7032 | A |  |  |  |  |  |
|  | Dimensions (HxWxD) | By Vendor | 2200*800*800 |  |  |  |  |  |
|  | Sheet Steel Thickness (Body/Frame) | 2mm/2.5mm | A |  |  |  |  |  |
|  | Weight | By Vendor | 300~350kg |  |  |  |  |  |
| - Capacitors |  |  |  |  |  |  |  |  |
|  | Capacitor Manufacturer/Model No./Year | By Vendor | FARAKOH/; IFASA/ SABAKHAZEN |  |  |  |  |  |
|  | Rating of each Capacitor Bank | 140Kvar = 1x20Kvar Fix + 6x20Kvar | A |  |  |  |  |  |
|  | Capacitor Bank Rated Current | By Vendor | 202 A |  |  |  |  |  |
|  | Capacitor Bank Rated Voltage | 440V | A |  |  |  |  |  |
|  | Capacitor Bank Connection Type | Delta | A |  |  |  |  |  |
|  | Capacitor Bank Rated Capacitance (µF) | By Vendor | Based on technical specification |  |  |  |  |  |
|  | Capacitance Variation (µF/ºC) | By Vendor | Based on technical specification |  |  |  |  |  |
|  | Capacitor Unit Rated Voltage | By Vendor | Based on technical specification |  |  |  |  |  |
|  | Capacitor Unit Temp. Category | -5/D | A |  |  |  |  |  |
|  | Capacitor Unit Insulating medium | By Vendor | Based on technical specification |  |  |  |  |  |
|  | Capacitor Unit Electrode Material | By Vendor | Based on technical specification |  |  |  |  |  |
|  | Capacitor Unit Dielectric Material | By Vendor | Based on technical specification |  |  |  |  |  |
|  | Capacitor Unit Case Material | Aluminum | A |  |  |  |  |  |
|  | Capacitor Unit Discharge Resistor (Ω) | By Vendor | 2 |  |  |  |  |  |
|  | Capacitor Unit Discharge time (to 75V) | <3 Minutes | A |  |  |  |  |  |
| - Control Unit (Regulator) |  |  |  |  |  |  |  |  |
|  | Manufacturer / Type | By Vendor | BKM06 |  |  |  |  |  |
|  | Mode of Operation | Automatic & Manual | A |  |  |  |  |  |
|  | Number of Steps | 5 Steps | 6Step |  |  |  |  |  |
|  | Selector Switch | Auto/Off/Manual Selector Switch For Each Step | A |  |  |  |  |  |
| - Fuses |  |  |  |  |  |  |  |  |
|  | Manufacturer / Type | By Vendor | Pichaz |  |  |  |  |  |
|  | Rated Current | 1.5 times of Capacitor Rated Current | A |  |  |  |  |  |
|  | Inrush Current | 100 times of Capacitor Rated Current | A |  |  |  |  |  |
|  | Rated Voltage | 500V | A |  |  |  |  |  |
|  | Service Voltage | 400V±10% | A |  |  |  |  |  |
|  | Rated Frequency | 50Hz±5% | A |  |  |  |  |  |
| - Contactors |  |  |  |  |  |  |  |  |
|  | Manufacturer / Type | By Vendor | RK/LIFASA |  |  |  |  |  |
|  | Rated Voltage | 690V AC | A |  |  |  |  |  |
|  | Service Voltage | 400V AC | A |  |  |  |  |  |
|  | Coil Voltage | 230 VAC (Note 2) | A |  |  |  |  |  |
|  | Duty | AC6-b | A |  |  |  |  |  |
| - Incoming Circuit Breaker |  |  |  |  |  |  |  |  |
|  | Manufacturer / Type | By Vendor | ABB |  |  |  |  |  |
|  | Type | MCCB, 4Pole, Fixed Type | A |  |  |  |  |  |
|  | Rated Current | 315A | A |  |  |  |  |  |
|  | Rated Short Circuit Breaking Current | 50 kA | A |  |  |  |  |  |
|  | Rated Insulation Voltage | 1000 VAC | A |  |  |  |  |  |
|  | Service Voltage | 400V | A |  |  |  |  |  |
|  | Internal Protections | 49, 50, 51 | 49&50 |  |  |  |  |  |
|  | Voltage Protection | 230 VAC | A |  |  |  |  |  |
|  | Trip and Status aux. switches | Yes | A |  |  |  |  |  |
| - Voltmeter with Selector Switch |  |  |  |  |  |  |  |  |
|  | Manufacturer / Type | By Vendor | VOLTMETER: BEW SELECTOE: TRS |  |  |  |  |  |
|  | Operating Range | 0 -500V | A |  |  |  |  |  |
|  | Accuracy Class | 1.5 | A |  |  |  |  |  |
| - Accessories |  |  |  |  |  |  |  |  |
|  | Panel Lighting & Space Heater with Thermostat/Hygrostat | Yes | A |  |  |  |  |  |
|  | Door Key | Yes | A |  |  |  |  |  |
|  | Gland Plate | Yes | A |  |  |  |  |  |
|  | Terminal Lugs | Yes | A |  |  |  |  |  |
|  | Commissioning Spare Parts | Yes | A |  |  |  |  |  |
|  | Two Year Operation Spare Parts | Yes | A |  |  |  |  |  |
|  | Routine Test | Witnessed and Report | A |  |  |  |  |  |
|  | Type Test CERTIFICATE | Certificat | A |  |  |  |  |  |
| - Inrush Reactor |  |  |  |  |  |  |  |  |
|  | Inrush Reactor Requied (Y/N) | By Vendor | FARAKOH |  |  |  |  |  |
|  | Inductance (mH) | By Vendor | - |  |  |  |  |  |
|  | Type | By Vendor | IRON |  |  |  |  |  |

Conclusion Table:

| Item | Equipment | Vendor 1 | Vendor 2 | Vendor 3 |
| --- | --- | --- | --- | --- |
| 1 | LV Switchgear |  |  |  |
| 2 | LV Capacitor Bank |  |  |  |

Conclusion Note:

Vendor 1

- X

- X

- X

Vendor 2

- X

- X

- X

Vendor 3

- X

- X

- X