## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-EL-MT-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2826 |  |  | Transmital Date: 10/Nov/2024
Document Title: MTO For Cathodic Protection System for Siahmakan Gas Injection |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0308-EL-TR-2826 |  |  | Transmital Date: 10/Nov/2024
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-EL-MT-0003_D00 |  |  | CRS Status: | C3
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Compacted coke breeze has not been considered in MTO. It shall be rechedked and modified. (Based on IPS-D-TP-705 and cathodic calculation document) |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | According to calculation note and design report for cathodic protection system the impressed current anodes have been considered in canistered MMO tubular anode that fabricated in factory included coke. So, this comment is not exerted.
2 | Earthing system material shall be added as per IPS-D-TP-717 such as earth pit, earth rod, earth cable/wire, etc. It seems item 3 of MTO has been considered generally. |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Will be followed up as respect to details and configuration materlas will be included. Description of mentioned item is corrected in next revision.
3 | Installation detail NO. (IPS NO.) shall be added based on "Typical Installation Details & Notes For Cathodic Protection Systems" document for PBB, NBB, ground bed marker and test point for more information at bid stage. |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Added
4 | Following items shall be added as per "specification for cathodic protection" basic document: -Cable warning tape -14.17. Datalogger for recording the data of coating efficiency test. |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Cable warning tape will be covered in item 22 as bulk materials. According to scope of work for cathodic protection, for verifying the cathodic protection effectiveness shall be checked as acceptance criteria " polarization and potentail IR-free , and equivalent criteria " the coating efficiency is not in scope of work by cathodic protection system.
5 | Item 1 of MTO (Transformer/Rectifier):
5.1 | Following note shall be added: Generally in accordance with: IPS-M-EL-155 |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Followed
5.2 | Following note shall be added as per "specification for cathodic protection" basic document as general featurers: Oil immersed type, continuous duty.Transformer/Rectifier equipped with step less voltage regulating system and thyristor control |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Covered
6 | Item 2 of MTO (AC Box):
6.1 | Technical characteristics such as IP, Voltage, frequency, rated current, short circuit level, number of phase, type/size/and number of pole for incoming and outgoings feeder CB, etc shall be added. |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Exerted
7 | Item 5 of MTO (Splicing kit):
7.1 | Generally in accordance with: IPS-M-EL-155Following note shall be added: Generally In Accordance With: IPS-M-TP-750 , Part 11. |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Done
8 | Items 6,9,10 and 14 of MTO (Cable):
8.1 | Minimum conductor sizes shall be as follows based on "specification for cathodic protection" basic document : Negative cables 50 mm2 , Armoured cable Positive cable 50 mm2 , Armoured cable Header cable 50 mm2, Armoured cable Potential monitoring 16 mm2 Spark gap 25 mm2 current testing and bonding 25 mm2 Equipotential bonding 16 mm2. |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Main cable positive and negative are considered 50 mm and with armored , header cable size is 35 mm 2 and without armored due to suitable for executive. And other size are mentioned will be covered in next revision.
8.2 | Following note shall be added: Generally In Accordance With: IPS-M-TP-750 , Part 7 |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Done
8.3 | All cables shall be armored type based on "specification for cathodic protection" basic document |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | will be followed , for main cables
8.4 | All the AC & DC cables (anode cable, positive and negative cable and lead/monitoring cable) shall be used of chlorine resistant type based on "specification for cathodic protection" basic document. (Shall be rechecked and considered if required) |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | According to IPS-M-TP-750 the anode cable tail shall be considered as HMWPE/PVDF type for resistanting of chloride contamination that considered in MTO for anode cable.
9 | Items 11 and 12 of MTO (Test Point):
9.1 | There is conflict between this document and "Plan & Profile Drawings For Gas Pipeline (to Siahmakan)" document form point of test point and combined box No's view. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | followed
10 | Items 7 and 8 of MTO (Bond Box:
10.1 | General featurers such as material and IP shall be added.. |  | BK-SUR-ENG-ELE-03-09718 | 2024-11-23 | Done
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozaffari | Signature |  |  |  | Clarified By: | Signature
| Date: 23/11/2024 |  |  |  |  | Date: