## Sheet1
N.I.S.O.C |  | Mansour Abad Project | [5 empty] | P.E.D.C.O
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-TE-PY-0008 |  |  |  |  | EPC Contractor Tr. No.: BK-PEDCO-NISOC-0311-TE-TR-2933 |  |  | Transmital Date: 01-Feb-2025
Document Title: Telecommunication Equipment Layout For CGS Warehause |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0311-TE-TR-2933 |  |  | Transmital Date: 01-Feb-2025
[5 empty] | CRS No: CRS-BK-GCS-PEDCO-120-TE-PY-0008_D01 |  |  | CRS Status:
Item | Comments (NISOC) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نظرات عمومی: Layout مربوط به سیستمهای پیجینگ و تلفن و رادیو ساختمانهای (سویچگیر و CCTV ) همزمان با مدرک مربوطه ارسال گردد |  | 1403-2294-493974 | 1403/12/08 | به استحضار می رساند که برای هر ساختمان و هر فضا مدرک مجزایی تعریف شده است . مدارک ساختمان Electrical Buiding , CCB قبلا ارسال شده است ساختمان CCTV نیز بعد از نهایی شدن معماری ارسال میگردد . لذا بررسی مدرک لطفا به صورت مجزا طبق رویه پروژه انجام و نتیجه به این پیمانکار ارسال گردد
2 | لازم است تهیه و کنترل مدارک بر اساس اصول نقشه کشی تهیه گردد |  | 1403-2294-493974 | 1403/12/08 | موارد مربوط به نقشه کشی اصلاح گردید
3 |  |  | 1403-2294-493974 | 1403/12/08 | یکی از بلندگوهای اتاق WORKSHOP حذف گردید
4 |  |  | 1403-2294-493974 | 1403/12/08 | مدارک تلفن و پیجینگ به بخش مراجع اضافه گردید
5 |  |  | 1403-2294-493974 | 1403/12/08 | ولوم کنترلر به درخواست آن کارفرمای محترم اضافه گردید . اما مجددا به استحضار می رساند کاربرد ولوم کنترلر جهت محیط اداری و کاربرد آفیس میباشد و با توجه به صنعتی بودن ساختمان ، کارایی و قابلیت نصب و اجرای آن متناسب فضا نخواهد بود
6 |  |  | 1403-2294-493974 | 1403/12/08 | دستگاه تلفن اتاق 101 جابه جا گردید . اما به استحضار می رساند تلفن صنعتی دیواری در فضاهای مشابه معمولا در مجاورت درب ورودی و محیط جنرال نصب میگردد و در فضای داخل Workshop با نویز بالا و انباشتگی تجهیزات توصیه نمیگردد
|  |  | 1403-2294-493974 | 1403/12/08 | کلیه کابلهای تعریف شده در لجند متناسب گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: AP.Golrang | Signature
| Date: |  |  |  |  | Date: 03-Feb-2025