## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-PY-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2833 |  |  | Transmital Date: 13 Nov 2024
Document Title: F&G Location Layout For Buildings |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0308-IN-TR-2833 |  |  | Transmital Date: 13 Nov 2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-PY-0006_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در راهرو اصلی جلوی اتاق کنترل، یک شستی اعلان حریق و آلارم دیداری و شنیداری اضافه شود. |  | 03/2294/392584 | 1403/10/01 | مدرک مطابق نظر کارفرمای محترم اصلاح گردید
2 | در بیرون ساختمان کنترل درب ورودی (در نزدیکی اتاق باطری) یک شستی اعلان حریق و آلارم دیداری و شنیداری اضافه شود. |  | 03/2294/392584 | 1403/10/01 | مدرک مطابق نظر کارفرمای محترم اصلاح گردید
3 | در بیرون ساختمان کنترل درب ورودی (در نزدیکی آلارم 1101) یک شستی اعلان حریق اضافه شود. |  | 03/2294/392584 | 1403/10/01 | مدرک مطابق نظر کارفرمای محترم اصلاح گردید
4 | در ساختمان CCTV آلارم دیداری و شنیداری 1301 به نزدیک درب ورودی ساختمان جابجا شود. |  | 03/2294/392584 | 1403/10/01 | مدرک مطابق نظر کارفرمای محترم اصلاح گردید
5 | یک آلارم دیداری و شنیداری داخل راهرو در ساختمان CCTV اضافه شود. |  | 03/2294/392584 | 1403/10/01 | مدرک مطابق نظر کارفرمای محترم اصلاح گردید
6 | محل قرارگیری FACP مشخص گردد. |  | 03/2294/392584 | 1403/10/01 | مدرک مطابق نظر کارفرمای محترم اصلاح گردید
7 | وضعیت اتاق های موجود از لحاظ دارا بودن سیستم اعلان بررسی و نتیجه اعلام گردد. |  | 03/2294/392584 | 1403/10/01 | اتاق های موجود دارای تجهیزات اعلان و سیستم F&G مربوطه هستند که در مدار کاری خود در حال بهره بردای می باشندو تنها ارتباط سیستم F&G جدید با سیستم F&G موجود در طراحی جدید در نظر گرفته شده است .
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: