## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-PY-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2833 |  |  | Transmital Date: 13 Nov 2024
Document Title: F&G Location Layout For Buildings |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0308-IN-TR-2833 |  |  | Transmital Date: 13 Nov 2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-PY-0006_D03 |  |  | CRS Status: | C1
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بازگشت به كامنت قبل مدرك پيشين، فاصله بين ديتكتورها بر اساس ميزان پوشش دهي مشخص شود. |  | BK-SUR-ENG-INS-01-05931 | 2022-10-19 | اصلاح گردید
2 | در خصوص Mac هايي كه در آيتم هاي شماره 1، 14 و 15 بصورت متمايز ارائه شده است در مدرك نيز نشان داده شود. اين مورد براي تمامي آيتم ها بررسي و در مدرك اعمال گردد. |  | BK-SUR-ENG-INS-01-05931 | 2022-10-19 | اصلاح گردید
3 | تگ ها بصورت Duplicate مي باشد مانند HN-1101. موارد مجددا بررسي و اصلاح گردد |  | BK-SUR-ENG-INS-01-05931 | 2022-10-19 | اصلاح گردید
4 | جداول ارائه شده در هر صفحه با محتواي آن تناقض دارد موارد مجددا بررسي و اصلاح گردد. براي مثال صفحه 2 |  | BK-SUR-ENG-INS-01-05931 | 2022-10-19 | اصلاح گردید
D02
1 | نقطه نظرات ذینفع اصلی بر روی این مدرک در نظر گرفته شود. |  | BK-SUR-ENG-INS-02-08732 | 2023-11-08 | ملاحظه گردید. |  |  | بسته شد
2 | F&G برای انبارهای ابزاردقیق،‌تعمیرات ابزاردقیق و مواد شیمیایی که به پلات اضافه شده است در نظر گرفته شود. |  | BK-SUR-ENG-INS-02-08732 | 2023-11-08 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید. |  |  | بسته شد.
D03
1 | با توجه به تایید بخش ایمنی ذینفع اصلی مورد خاصی مطرح نمی باشد. لازم به ذکر است که مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-03-09755 | 2024-11-30 | ملاحظه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: