## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از10
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0007 | D07
طرح نگهداشت و افزایش تولید 27 مخزن
I&C POWER CONSUMPTION SUMMARY نگهداشت و افزایش تولید میدان نفتی بینک
D07 |  | MAR.2025 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D06 |  | FEB.2025 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D05 |  | AUG.2024 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Sadeghian
D04 |  | JAN.2024 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D03 |  | AUG.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D02 |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708973
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 10
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0007 |  | D07
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D05 |  | D06 |  | D07 | D08 | D09
1 | X | X | X |  | X |  | X |  | 1 |  | X |  | X |  | X
2 | X | X | X |  | X |  | X |  | 2 |  | X |  | X |  | X
3 | X | X | [6 empty] | 3 |  |  |  | X
4 | X | X | X |  | X |  | X |  | 4 |  | X |  | X |  | X
5 | X | X | X |  | X |  | X |  | 5 |  |  |  | X
6 |  | X | X |  | X |  |  |  | 6 |  | X |  | X
7 |  |  |  |  | X |  | X |  | 7 |  | X |  | X |  | X
8 |  |  |  |  | X |  | X |  | 8 |  | X |  | X |  | X
9 | [8 empty] | 9 |  |  |  | X |  | X
10 | [8 empty] | 10 | [5 empty] | X
11 | [8 empty] | 11
12 | [8 empty] | 12
13 | [8 empty] | 13
14 | [8 empty] | 14
15 | [8 empty] | 15
16 | [8 empty] | 16
17 | [8 empty] | 17
18 | [8 empty] | 18
19 | [8 empty] | 19
20 | [8 empty] | 20
21 | [8 empty] | 21
22 | [8 empty] | 22
23 | [8 empty] | 23
24 | [8 empty] | 24
25 | [8 empty] | 25
26 | [8 empty] | 26
27 | [8 empty] | 27
28 | [8 empty] | 28
29 | [8 empty] | 29
30 | [8 empty] | 30
31 | [8 empty] | 31
32 | [8 empty] | 32
33 | [8 empty] | 33
34 | [8 empty] | 34
35 | [8 empty] | 35
36 | [8 empty] | 36
37 | [8 empty] | 37
38 | [8 empty] | 38
39 | [8 empty] | 39
40 | [8 empty] | 40
41 | [8 empty] | 41
42 | [8 empty] | 42
43 | [8 empty] | 43
44 | [8 empty] | 44
45 | [8 empty] | 45
46 | [8 empty] | 46
47 | [8 empty] | 47
48 | [8 empty] | 48
49 | [8 empty] | 49
50 | [8 empty] | 50
51 | [8 empty] | 51
52 | [8 empty] | 52
53 | [8 empty] | 53
54 | [8 empty] | 54
55 | [8 empty] | 55
56 | [8 empty] | 56
57 | [8 empty] | 57
58 | [8 empty] | 58
59 | [8 empty] | 59
60 | [8 empty] | 60
61 | [8 empty] | 61
62 | [8 empty] | 62
63 | [8 empty] | 63
64 | [8 empty] | 64

## REFERENCES
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 10
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D07
REFERENCE DOCUMENTS:
| I/O LIST FOR CONTROL SYSTM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0002
| I/OLIST FOR ESD SYSTEM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0003
| I/O LIST FOR F&G SYSTEM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0004
| SPECIFICATION FOR INSTRUMENTATION | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| SPECIFICATION FOR CONTROL SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0002
| SPECIFICATION FOR ESD SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0003
| SPECIFICATION FOR ESD SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0012
| SPECIFICATION FOR INSTRUMENT AND CONTROL OF PACKAGE UNIT SYSTEM(PU | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0004
| ELECTRICAL/UPS CONSUMPTION LOAD LIST ( HAVAYAR) | [7 empty] | BK-GCS-HY-120-EL-LI-0001
| UCP AND BMS SYSTEM POWER CONSUMPTION LIST | [7 empty] | BK-GCS-MF-120-IN-LI-0004
| VENDOR PROPOSAL FOR DCS/ESD/F&G/AIR COMPRESSOR PACKAGES/NITROGEN PACKAGE | [7 empty] | -

## UPS 110 VAC
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 4 از10
9184 – 073 - 053 |  |  |  |  | BK | GCS |  | PEDCO |  | 120 |  | IN | LI |  | 0007 |  | D07
INST./CONTROL UPS 110 VAC POWER CONSUMPTION TABLE
- Table (1) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 3) |  |  | POWER CONSUMPTION (W) (Note 1)( AS PER APPENDIX A,B) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION (W)
| 1 | DCS SYSTEM PANEL (AS PER APPENDEX "A") |  | Power Supply for CPUs ( 2 No. redundant) |  | 1 | 2 hr. | 400 |  |  | 130 |  |  | 2 Nos. (Redundant) |  | 900
|  |  |  | 110/24 VDC Power Supply |  |  | 2 hr. |  |  |  | 770 |  |  | 2 Nos. (Redundant)
| 2 | DCS MARSHALING PANEL (AS PER APPENDEX "A") |  | 110/24 VDC Power Supply ( 2 No. redundant) |  | 3 | 2 hr. | - |  |  | 40 |  |  | 2 Nos. (Redundant) |  | 120
| 3 | SERVER/ NETWORK |  | 110/24 VDC Power Supply ( 2 No. redundant) |  | 2 | 2 hr. | - |  |  | 885 |  |  | 2 Nos. (Redundant) |  | 1770
| 4 | ESD SYSTEM PANEL (AS PER APPENDEX "A") |  | Power Supply for CPUs (2 No. redundant) |  | 1 | 2 hr. | 200 |  |  | 130 |  |  | 2 Nos. (Redundant) |  | 900
|  |  |  | 110/24 VDC Power Supply |  |  | 2 hr. |  |  |  | 750 |  |  | 2 Nos. (Redundant)
| 5 | ESD MARSHALING PANEL (AS PER APPENDEX "A") |  | 110/24 VDC Power Supply |  | 2 | 2 hr. | - |  |  | 40 |  |  | 2 Nos. (Redundant) |  | 80
| 6 | SERVER/ NETWORK |  | 110/24 VDC Power Supply ( 2 No. redundant) |  | 2 | 2 hr. | - |  |  | 15 |  |  | 2 Nos. (Redundant) |  | 30
| ITEM | DESCRIPTION |  |  |  | SYSTEM QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 3) |  |  | UNIT POWER CONSUMPTION (W) (Note 1) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION (W)
| 7 | ELECRO GAS COMPRESSOR UCP A/B/C SYSTEM AND MARSHALING CABINET (AS PER APPENDEX "B") |  |  |  | 3 | 2 hr. | 3x250 |  |  | 1500 |  |  | 2 Nos. (Redundant) |  | 4500
| 8 | DEHYDRATION PACKAGE(UCP/BMS) (AS PER APPENDEX "C") |  |  |  | 2 | 2 hr. | (2x56) +(2x32) |  |  | 2000 |  |  | 2 Nos. (Redundant) | 1 | 4000
| 9 | PAGING SYSTEM |  |  |  | 1 | 2 hr. | - |  |  | 1000 |  |  | 2 Nos. (Redundant) | 1 | 1000
| 10 | AIR COMPRESSOR UCP A/B (AS PER APPENDEX "D") |  |  |  | 2 | 2 hr. | 2x100 |  |  | 1000 |  |  | 2 Nos. (Redundant) | 2 | 2000
| 11 | AIR DRAYER LOCAL LCP (AS PER APPENDEX "D") |  |  |  | 2 | 2 hr. | - |  |  | 500 |  |  | 2 Nos. (Redundant) | 2 | 1000
| 12 | NITROGEN PACKAGE UCP (AS PER APPENDEX "D") |  |  |  | 1 | 2 hr. | 100 |  |  | 1500 |  |  | 2 Nos. (Redundant) | 2 | 1500
| 13 | OPERATOR WORKSTATION (DUALL MONITOR )(AS PER APPENDEX "A") |  |  |  | 2 | 2 hr. | - |  |  | 610 |  |  | 1 No. ( Socket) | 4 | 1220
| 14 | OPERATOR WORKSTATION (SINGLE MONITOR )(AS PER APPENDEX "A") |  |  |  | 2 | 2 hr. | - |  |  | 530 |  |  | 1 No. ( Socket) | 4 | 1060
| 15 | DCS ENGINEERING WORKSTATION (SINGLE MONITOR ) (AS PER APPENDEX "A") |  |  |  | 1 | 2 hr. | - |  |  | 530 |  |  | 1 No. ( Socket) | 4 | 530
| 16 | ESD OPERATOR/ ENGINEERING WORKSTATION (SINGLE MONITOR )(AS PER APPENDEX "A") |  |  |  | 1 | 2 hr. | - |  |  | 530 |  |  | 1 No. ( Socket) | 4 | 530
| 17 | F&G OPERATOR/ ENGINEERING WORKSTATION (SINGLE MONITOR ) (AS PER APPENDEX "A") |  |  |  | 1 | 2 hr. | - |  |  | 530 |  |  | 1 No. ( Socket) | 4 | 530
TABLE 1
|  |  | TOTAL POWER CONSUMPTION (W) | [12 empty] | 21670
|  |  | TOTAL POWER CONSUMPTION CONSIDERING 20% SPARE CAPACITY (W) | [12 empty] | 26004
|  |  | TOTAL POWER CONSUMPTION CONSIDERING 15% CONTINGENCY FACTOR(W) | [12 empty] | 29904.6
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Power supply modules QTY, Voltage/Amp Range, Spare capacity… will be specified by vendor considering project documents.
Note 3: UPS power for HVAC Panel shall be supplied by vendor. Only 400VAC , 3 phase will be supplied by EPC contractor.
Note 3: Power Consumption of panels have been estimatted considering project I/O count. Refer to '' I/O List For Control System Doc.No.BK-GCS-PEDCO-120-IN-LI-0002 , I/O List For ESD System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003
D07
D07

## NON UPS 230 VAC
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 9
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN | LI | 0007 | D07
INST./CONTROL NON- UPS 230 VAC POWER CONSUMPTION TABLE
- Table (2) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room.
| ITEM | DESCRIPTION |  |  | UNIT POWER CONSUMPTION (W) (Note 1) | [5 empty] | QTY. (Note 1) | TOTAL POWER CONSUMPTION (W) + 500 W for 1 Socket per system
| 1 | Cabinet Utilities For DCS (Heater, Fan , Light, Socket) |  |  | 400 | [5 empty] | 4 | 2100
| 2 | Cabinet Utilities For ESD (Heater, Fan , Light, Socket) |  |  | 400 | [5 empty] | 3 | 1700
| 3 | Cabinet Utilities For F&G (Heater, Fan , Light, Socket) |  |  | 400 | [5 empty] | 3 | 1700
| 4 | Cabinet Utilities For Gas Compressor UCP(Heater, Fan , Light ,Socket) |  |  | 400 | [5 empty] | 6 | 2900
| 5 | Cabinet Utilities For Dehydration BMS( if any) (Heater, Socket, Fan , Light, Socket) |  |  | 400 | [5 empty] | 4 | 2100
| 6 | Cabinet Utilities For Total Flooding UCP(Heater, Socket, Fan , Light, Socket) |  |  | 400 | [5 empty] | 1 | 900
| 7 | Cabinet Utilities For Paging Cabinet (Heater, Socket, Fan , Light, Socket) |  |  | 400 | [5 empty] | 1 | 900
| 8 | Cabinet Utilities For Air Compressor UCP(Heater, Socket, Fan , Light, Socket) |  |  | 400 | [5 empty] | 2 | 1300
| 9 | Cabinet Utilities For Nitrogen package UCP(Heater, Socket, Fan , Ligh, Sockett) |  |  | 400 | [5 empty] | 1 | 900
| 10 | Control Desk Sockets |  |  | 500 | [5 empty] | 7 | 3500
| TOTAL POWER CONSUMPTION | [10 empty] | 18000
TABLE 2
|  |  | TOTAL POWER CONSUMPTION (W) | [8 empty] | 18000
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (W) | [8 empty] | 21600
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents.

## 24 VDC CHARGER
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 6 از10
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 |  | IN | LI |  | 0007 |  | D07
INST./CONTROL UPS 24 VDC POWER CONSUMPTION TABLE
- Table (3) is represents 24V DC UPS power consumption for F&G system. The estimation is based on the design of F&G systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 4) |  | POWER CONSUMPTION (W) ( WILL BE FINALIZED AFTER RECIEVING VENDOR DETAILED DATA) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION FOR QUIESENCE MODE(W) (Note 3) |  |  | TOTAL POWER CONSUMPTION FOR ALARM MODE (W) (Note 3)
| 1 | F&G SYSTEM PANEL |  |  | 1 | 24hr. | 265 |  | 1000 |  |  | 2 Nos. (Redundant) |  | 1130 |  |  | 1826
( for Quiescence)
[6 empty] | 5 MIN |  |  | 1826
(for alarm mode-)
| 2 | F&G MARSHALLING PANEL |  |  | 2 | 24hr. |  |  | 130
( for Quiescence)
| 1 | FACP system |  |  | 1 | 24hr. | - |  | 250 ( for Quiescence) |  |  | 2 Nos. (Redundant) |  | 390 |  |  | -
| 2 | FACP Detectors |  |  |  | 24hr. |  |  | 140 (for Quiescence mode)
[6 empty] | 5 MIN |  |  | 404 |  |  |  |  | - |  |  | 404
| 3 | FIRE PROTECTION AND TOTAL FLOODING SYSTEM UCP |  |  | 1 | 5 MIN | 50 |  | 500 |  |  | 2 Nos. (Redundant) | 2 | - |  |  | 500
|  |  | TOTAL POWER CONSUMPTION FOR 5 MIN BACK UP TIME (W) (Note 3) | [10 empty] | 2730
|  |  | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME (W) (Note 3) | [10 empty] | 1520
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITYFOR 5 MIN BACK UP TIME (W) | [10 empty] | 3276
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY FOR 24 HOURS BACK UP TIME (W) | [10 empty] | 1824
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Note 2: Deleted Note 3: DC charger shall supply 2KW + Spare, for 24H back up time but also it shall be capable to prepare 4.3KW+ Spare, as a peak power consumption in alarming conditions for 5 Min back up time. it shall be considered during battery sizing in related documents. Note 4: Power Consumption of panels have been estimatted considering project I/O count. Refer to '' I/O List For Control System Doc.No.BK-GCS-PEDCO-120-IN-LI-0002 , I/O List For ESD System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003.

## (APPENDIX A)
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 10
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D07
(APPENDIX "A": VENDOR DATA FOR DCS/ESD/F&G SYSTEMS & ACCESSORIES POWER CONSUMPTION)
APPENDIX "A": VENDOR DATA FOR DCS/ESD/F&G SYSTEMS & ACCESSORIES POWER CONSUMPTION)
`

## (APPENDIX B)
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 10
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D07
(APPENDIX "B": VENDOR DATA FOR GAS COMPRESSOR PACKAGE'S UCPS(A/B/C) POWER CONSUMPTION)
APPENDIX "B": VENDOR DATA FOR GAS COMPRESSOR PACKAGE'S UCPS(A/B/C) POWER CONSUMPTION

## (APPENDIX C)
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 10
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D07
(APPENDIX "C": VENDOR DATA FOR DEHYDRATION PACKAGE'S UCPS POWER CONSUMPTION)
APPENDIX "C": VENDOR DATA FOR DEHYDRATION PACKAGE'S UCPS POWER CONSUMPTION

## (APPENDIX D)
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 10
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D07
(APPENDIX "D": VENDOR DATA FOR AIR COMPRESSOR / NITROGEN PACKAGE'S UCPS POWER CONSUMPTION)
APPENDIX "D": VENDOR DATA FOR AIR COMPRESSOR / NITROGEN PACKAGE'S UCPS POWER CONSUMPTION